## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Count of EVENT_COUNT | Count of DISTINCT_UNITS | Sum of MWLost | Sum of MWHrsLost
0010-Thaw shed failure or fire | 1 | 1 | 3.3 | 102.3
0020-Coal car dumpers; shakers; and unloaders | 4 | 4 | 622 | 12383.2331
0022-Unloading/receiving hopper (train/truck) | 6 | 6 | 146 | 241445.0333
0024-Rotary plow | 12 | 12 | 412 | 1276.1166
0028-Dust collection system | 12 | 12 | 2947.7 | 215989.604
0030-Coal conveyors and feeders | 265 | 265 | 61081.74 | 1144072.3272
0035-Metal detector/collector (including magnetic separator) | 2 | 2 | 422.4 | 5582.4999
0050-Coal storage fires | 4 | 4 | 640 | 4897.4163
0060-Coal crushers including motors | 26 | 26 | 4071.8 | 28348.2589
0075-Storage silos/hoppers | 14 | 14 | 2216 | 56918.7492
0080-Stackers/reclaimers | 28 | 28 | 3486.4 | 318520.2561
0084-Coal conveyor scales-storage coal pile | 3 | 3 | 1036 | 325764.7
0085-Bunker feeder coal scales | 1 | 1 | 30 | 418.5
0090-Bunker fires | 15 | 15 | 4335.39 | 139251.5036
0095-Bunker flow problems | 144 | 144 | 14129.16 | 384424.0912
0100-Bunker gates | 4 | 4 | 363.13 | 1666.3899
0105-Bunker structures | 2 | 2 | 175 | 54861.25
0107-Screen (prior to bunkers) | 2 | 2 | 11 | 16.5667
0110-Other coal fuel supply problems up through bunkers | 35 | 35 | 4923.42 | 38993.9887
0111-Solid fuel feeder conveyors | 89 | 89 | 1583.72 | 24325.9338
0112-Solid fuel feed tanks/hoppers | 9 | 9 | 468 | 1318.1998
0114-Solid fuel volumetric feeder | 10 | 10 | 147.6 | 1415.55
0115-Solid fuel gravimetric feeder | 25 | 25 | 675.5 | 5283.9749
0116-Solid fuel feeder motors | 1 | 1 | 2.8 | 30.8
0121-Other solid fuel feed problems | 77 | 77 | 957.19 | 14535.6618
0125-Coal crusher dryer hammers | 2 | 2 | 94 | 15157.8666
0129-Other coal processing system problems | 20 | 20 | 2987.43 | 248595.2362
0152-Sorbent feed volumetric feeder | 3 | 3 | 1085 | 1239.2496
0160-Bed material tanks/hoppers | 3 | 3 | 1324.4 | 956044.6462
0165-Bed material crushers | 6 | 6 | 1084.6 | 70140.4795
0174-Other bed material handling equipment | 1 | 1 | 124.8 | 1591.2
0200-Pulverizer exhauster fan (for indirect firing) | 3 | 3 | 247.2 | 22578.5633
0205-Pulverizer exhauster fan drive | 18 | 18 | 1141.4 | 71910.2381
0240-Pulverized coal bin | 13 | 13 | 2611.9 | 33512.5127
0250-Pulverizer feeders | 927 | 927 | 97076.82 | 991428.7727
0253-Pulverizer feeder motor | 40 | 40 | 3045.97 | 45690.6803
0255-Pulverizer feeder coal scales | 10 | 10 | 1017.29 | 3146.8375
0256-Seal air system (air to pulverizers) | 36 | 36 | 7963.5 | 133312.7973
0257-Coal Crusher/dryer between feeder and pulverizer | 13 | 13 | 1708.96 | 14871.7298
0260-Primary air fan | 135 | 135 | 19870.05 | 1576152.6021
0262-Primary air fan lube oil system | 3 | 3 | 1373 | 15119.2161
0263-Primary air fan drives | 43 | 43 | 4099.72 | 79306.2374
0264-Other primary air fan problems | 42 | 42 | 4929.69 | 88069.4652
0265-Primary air heater | 12 | 12 | 2400 | 236941.0731
0266-Primary air heater fouling | 8 | 8 | 58.64 | 18417.7216
0267-Primary air flow instrumentation | 39 | 39 | 5415.44 | 53587.1436
0270-Primary air duct and dampers | 100 | 100 | 14668.5 | 791663.5174
0280-Pulverizer fires | 35 | 35 | 7166.83 | 520272.7803
0290-Pulverizer reduced capacity due to wear | 4 | 4 | 556.85 | 37579.9332
0300-Pulverizer motors and drives | 126 | 126 | 12774.18 | 280794.0613
0310-Pulverizer mills | 859 | 859 | 86382.75 | 1996510.1139
0312-Pulverizer mill classifiers | 15 | 15 | 1605.3 | 43952.143
0313-Pulverizer mill trunnion seals | 4 | 4 | 572 | 35862.5164
0314-Pulverizer mill ball charger hopper (ball mills only) | 1 | 1 | 50 | 46.6666
0315-Pulverizer mill coal level controls | 3 | 3 | 186 | 610.85
0320-Foreign object in Pulverizers mill | 82 | 82 | 3273.04 | 22207.2987
0325-Pulverizer skidding | 7 | 7 | 640.1 | 25924.4385
0330-Pulverizer coal leak (pulverizers only) | 104 | 104 | 10926.19 | 76025.9406
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 49 | 49 | 3795.03 | 36551.0556
0335-Pulverizer lube oil system | 80 | 80 | 7084.31 | 80236.3144
0338-Pulverizer control systems (temperature and pressure) | 41 | 41 | 3804.66 | 16683.8548
0339-Pulverizer System Puff | 15 | 15 | 3474.53 | 468904.6619
0340-Other pulverizer problems | 270 | 270 | 34784.8 | 428830.8186
0341-Pulverizer deluge system | 2 | 2 | 164 | 4368.6666
0342-Pulverizer inert system | 12 | 12 | 2390 | 30449.683
0344-Pulverizer inspection | 26 | 26 | 2028.44 | 22833.3088
0345-Pulverizer overhaul | 45 | 45 | 2447.54 | 182331.8026
0346-Pulverizer pyrite removal system | 92 | 92 | 10139.01 | 56171.1494
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 66 | 66 | 8968.54 | 70569.3022
0358-Oil burner piping and valves | 10 | 10 | 1913.1 | 27111.8944
0359-Gas burner piping and valves | 173 | 173 | 23423.41 | 441681.3027
0360-Burners | 201 | 201 | 18745.72 | 527978.491
0362-Burner tilts | 1 | 1 | 15 | 68.5
0370-Burner instruments and controls (except light-off) | 105 | 105 | 13172.32 | 367166.6588
0380-Light-off (igniter) systems (including fuel supply) | 53 | 53 | 12934.91 | 197312.7292
0385-Igniters | 71 | 71 | 18434.93 | 113680.1877
0390-Burner wind boxes and dampers | 7 | 7 | 952.17 | 19179.4818
0400-Burner wind box fires | 4 | 4 | 1377 | 202630.4828
0410-Other burner problems | 59 | 59 | 5737.02 | 60480.1741
0415-Cyclone feeders | 98 | 98 | 3670.44 | 75349.269
0420-Cyclone crusher | 8 | 8 | 168 | 4141.8333
0425-Cyclone dampers | 5 | 5 | 229.18 | 5580.1967
0426-Cyclone air ducts | 6 | 6 | 95 | 904.95
0430-Cyclone furnace | 9 | 9 | 443 | 101442.1832
0435-Other cyclone problems | 59 | 59 | 5047.74 | 218464.2329
0440-Fuel oil pumps (general) | 10 | 10 | 2678.1 | 26882.2928
0441-Fuel oil pumps (burner supply) | 9 | 9 | 2266 | 3877.1654
0442-Fuel oil pumps (forwarding/transfer) | 1 | 1 | 300.1 | 1485.495
0450-Fuel oil heaters | 1 | 1 | 184 | 1220.5333
0460-Fuel oil atomizers | 4 | 4 | 609 | 1769.3831
0470-Oil and gas fires | 11 | 11 | 1552.5 | 106649.6928
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 101 | 101 | 17475.04 | 481418.2276
0500-Main steam piping up to turbine stop valves | 39 | 39 | 14765.78 | 1456978.692
0510-Main steam relief/safety valves off superheater | 70 | 70 | 14679 | 388877.6219
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 56 | 56 | 16132.13 | 751398.7749
0530-Other main steam system problems | 92 | 92 | 12145.94 | 481928.87
0540-Hot reheat steam piping up to turbine stop valves | 26 | 26 | 5699.1 | 534745.3363
0541-Cold reheat steam piping up to boiler | 19 | 19 | 3791.4 | 381510.0372
0550-Reheat steam relief/safety valves | 59 | 59 | 7189.36 | 341488.3121
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 49 | 49 | 11940.6 | 371941.8183
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 45 | 45 | 10146.82 | 179608.7634
0570-Other reheat steam problems | 43 | 43 | 4728.5 | 108407.2895
0580-Desuperheater/attemperator piping | 4 | 4 | 756 | 58919.5496
0590-Desuperheater/attemperator valves | 47 | 47 | 14045.27 | 506035.3933
0600-Desuperheater/attemperator spray nozzles | 5 | 5 | 511.8 | 10804.7666
0610-Desuperheater/attemperator drums | 3 | 3 | 228.94 | 916.6456
0620-Other desuperheater/attemperator problems | 8 | 8 | 860.1 | 13640.8581
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 1 | 1 | 455 | 6021.1665
0640-Startup bypass system valves | 25 | 25 | 13021.38 | 768807.4214
0650-Startup bypass tanks or flash tanks | 1 | 1 | 814.7 | 27876.3178
0655-Steam by-pass system instrumentation and controls | 3 | 3 | 829 | 5408.1831
0660-Other startup bypass system problems | 3 | 3 | 2079 | 43029.9989
0670-Feedwater piping downstream of feedwater regulating valve | 18 | 18 | 2824.43 | 50520.5702
0680-Feedwater valves (not feedwater regulating valve) | 63 | 63 | 13289.3 | 239323.1182
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 23 | 23 | 3479 | 115710.4657
0700-Blowdown system valves A | 16 | 16 | 3628 | 198185.4507
0710-Blowdown system piping B | 22 | 22 | 5222.46 | 187995.7606
0730-Other blowdown system problems | 4 | 4 | 1896.67 | 200850.1026
0740-Boiler recirculation pumps | 78 | 78 | 15157.76 | 2314631.9448
0741-Boiler recirculation pumps - motors | 26 | 26 | 4453.3 | 1206315.9256
0742-Boiler recirculation pumps - motors - cooling system | 8 | 8 | 2558 | 28971.0825
0750-Boiler recirculation piping including downcomers | 2 | 2 | 488 | 33667.9333
0760-Boiler recirculation valves | 19 | 19 | 7166.51 | 201386.8079
0770-Other boiler recirculation problems | 35 | 35 | 3689 | 188553.1325
0775-Economizer piping | 33 | 33 | 7271.38 | 473148.946
0780-Headers between tube bundles | 1 | 1 | 63.77 | 14.8796
0782-Headers and caps | 2 | 2 | 359.7 | 7194.5281
0790-Pipe hangers; brackets; supports (general) | 5 | 5 | 1932 | 591052.799
0799-Other miscellaneous piping system problems | 29 | 29 | 6864.96 | 1174401.4443
0800-Drums and drum internals (single drum only) | 41 | 41 | 9841.37 | 128115.494
0801-HP Drum (including drum level trips not attributable to other causes) | 138 | 138 | 23216.59 | 223188.2564
0802-IP Drum (including drum level trips not attributable to other causes) | 68 | 68 | 11456.28 | 93911.7963
0803-LP Drum (including drum level trips not attributable to other causes) | 32 | 32 | 6527.01 | 57446.4634
0810-Boiler supports and structures (use code 1320 for tube supports) | 9 | 9 | 502.77 | 264923.4019
0820-Casing | 33 | 33 | 5754.92 | 495755.1311
0830-Doors | 18 | 18 | 3970.9 | 231171.2638
0840-Refractory and insulation | 111 | 111 | 3664.27 | 195732.4771
0845-Windbox expansion joints | 5 | 5 | 1329.16 | 55147.7375
0847-Other expansion joints | 6 | 6 | 661.94 | 35288.5896
0850-Other internal or structural problems | 15 | 15 | 2053 | 94014.473
0855-Drum relief/safety valves (Single drum only) | 37 | 37 | 5256.5 | 106252.3648
0856-HP Drum relief/safety valves | 9 | 9 | 1103.8 | 63700.273
0857-IP Drum relief/safety valves | 4 | 4 | 756.2 | 17270.9496
0859-Tube external fins/membranes A | 3 | 3 | 876 | 15145.0665
0860-Soot blowers - air (see code 3844 for air delivery system) | 4 | 4 | 1094 | 18631.1498
0870-Soot blowers - steam | 36 | 36 | 7814.05 | 127970.1066
0872-Soot blowers - water | 3 | 3 | 638.4 | 10129.6298
0873-Soot blower drives | 5 | 5 | 897 | 11267.1998
0876-Soot blower controls | 14 | 14 | 1236.7 | 12865.6662
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 63 | 63 | 9501.94 | 515469.0901
0885-Fly ash Removal System - wet transport | 5 | 5 | 1075.1 | 15927.5833
0890-Bottom ash systems (wet or dry) | 153 | 153 | 20222.18 | 1278979.7814
0891-Bottom ash hoppers (including gates) | 14 | 14 | 4753.15 | 155891.2248
0892-Bottom ash clinker grinders | 16 | 16 | 3886.5 | 123842.6486
0893-Bottom ash water pumps and motors | 5 | 5 | 1773.73 | 14904.6094
0894-Bottom ash piping and valves | 11 | 11 | 2446 | 75410.8727
0895-Ashpit trouble | 10 | 10 | 200 | 7795.8999
0897-Bottom ash rotary (drag chain type) conveyor and motor | 87 | 87 | 23290.67 | 662939.8909
0898-Bottom ash pyrite hopper (pulverizer reject) system | 6 | 6 | 442.85 | 2517.8637
0899-Bottom ash controls and instrumentation | 4 | 4 | 664.77 | 5093.2266
0900-Slag-tap (cyclone furnace) | 8 | 8 | 810 | 92783.9666
0920-Other slag and ash removal problems A | 88 | 88 | 13037.06 | 322366.0618
0930-Bed material coolers | 13 | 13 | 246.5 | 19971.7332
0931-Bed material transport piping/valves | 1 | 1 | 225 | 1267.4999
0936-Bed material conveyors B | 2 | 2 | 101 | 744.5
0937-Bed material mechanical separators and baghouse | 1 | 1 | 34 | 223.8333
0950-Other bed material system problems | 3 | 3 | 15.9 | 156.2017
0959-Other char reinjection equipment problems | 1 | 1 | 4 | 3.6667
0970-Flue gas-solids separator | 1 | 1 | 344 | 516
0980-High pressure loop seal recirculation fans/blowers | 1 | 1 | 32.5 | 127.2916
0989-Other bed solids recirculation problems | 23 | 23 | 2475.81 | 318825.4505
0991-Tube leaks | 22 | 22 | 851.12 | 78082.1213
0999-Other heat exchanger problems | 17 | 17 | 284.9 | 45722.5833
1000-Waterwall (Furnace wall) | 608 | 608 | 198551.1 | 19212075.6212
1003-Steam generating tubes between steam drum and mud drum | 18 | 18 | 4982.7 | 401670.5618
1005-Generating tubes | 25 | 25 | 4419.74 | 357806.5988
1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | 1 | 1 | 155 | 16683.1666
1010-Cyclone furnace (in cyclone area only) | 34 | 34 | 7491.66 | 560251.1208
1020-Convection pass wall (water tubes only) | 14 | 14 | 6164.13 | 407427.4696
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 48 | 48 | 12119.9 | 804364.6802
1035-Platen superheater | 59 | 59 | 22125.16 | 2047058.5392
1040-First superheater | 100 | 100 | 25163.37 | 2303068.6651
1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | 3 | 3 | 805 | 91177.4998
1050-Second superheater | 97 | 97 | 39294.48 | 3927150.1849
1055-External superheater link tubing | 5 | 5 | 1988 | 111892.6996
1060-First reheater | 138 | 138 | 55018.44 | 5237251.1939
1070-Second reheater | 25 | 25 | 10958.1 | 1672701.2172
1075-External reheater link tubing | 1 | 1 | 199 | 13986.3833
1080-Economizer | 128 | 128 | 39170.28 | 2723443.6081
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 17 | 17 | 3710 | 492642.8316
1090-Other boiler tube leaks | 147 | 147 | 50290.55 | 7426743.6336
1100-Waterwall (Furnace wall) | 46 | 46 | 8420.81 | 368548.731
1103-Steam generating tubes between steam drum and mud drum | 5 | 5 | 100 | 363.3333
1105-Generating tubes | 9 | 9 | 471 | 22605.6
1110-Cyclone furnace (in cyclone area only) | 3 | 3 | 37 | 693.3
1120-Convection pass wall | 2 | 2 | 830 | 31388.1666
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 6 | 6 | 1332.84 | 128071.6781
1140-First superheater | 25 | 25 | 1671.62 | 66140.9632
1150-Second superheater | 78 | 78 | 15307.75 | 1014908.265
1160-First reheater | 20 | 20 | 1507.55 | 127080.9567
1170-Second reheater | 28 | 28 | 4384 | 159409.1649
1180-Economizer | 34 | 34 | 3363.5 | 72334.9821
1190-Other tube slagging or fouling | 158 | 158 | 8502.86 | 185323.4042
1191-Bed agglomeration (FBC only) | 1 | 1 | 37.5 | 1616.875
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 59 | 59 | 8311 | 376334.7739
1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | 5 | 5 | 847.1 | 25569.5942
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 4 | 4 | 733 | 23065.9833
1340-Tube modifications (including addition and removal of tubes) | 10 | 10 | 1170.8 | 421128.783
1350-Other miscellaneous boiler tube problems | 42 | 42 | 4356.3 | 98094.6464
1360-Boiler drains system | 27 | 27 | 6312.41 | 144616.6728
1400-Forced draft fans | 238 | 238 | 22363.98 | 2917252.2496
1401-Forced draft fan dampers | 54 | 54 | 8068.22 | 93259.6002
1407-Forced draft fan lubrication system | 8 | 8 | 2032.3 | 45769.0014
1410-Forced draft fan motors | 74 | 74 | 14129.55 | 2155426.0842
1411-Forced draft fan motors - variable speed | 20 | 20 | 4911.66 | 230449.6251
1412-Forced draft fan drives (other than motor) | 24 | 24 | 6954.58 | 287246.9714
1413-Forced draft fan couplings | 3 | 3 | 1555 | 98410.833
1415-Forced draft fan controls | 33 | 33 | 7770.03 | 66612.5169
1420-Other forced draft fan problems | 46 | 46 | 6260.41 | 209724.4723
1421-Secondary air fans/blowers | 14 | 14 | 1481.24 | 27617.6298
1422-Secondary air fan/blower motors - single speed | 5 | 5 | 418.42 | 40587.6939
1423-Secondary air fan/blower motors - variable speed | 5 | 5 | 181 | 3519.5
1424-Secondary air fan/blower controls | 5 | 5 | 291.82 | 5874.6716
1430-Air supply ducts from FD fan | 10 | 10 | 1906.13 | 564092.2786
1431-Air supply dampers from FD fan | 2 | 2 | 235 | 1811.7666
1432-Air supply duct expansion joints | 8 | 8 | 2111.4 | 55268.4562
1440-Air supply dampers | 11 | 11 | 1528.69 | 33862.5385
1450-Other air supply problems | 104 | 104 | 6133.26 | 963237.0388
1455-Induced draft fans | 829 | 829 | 60654.88 | 2988386.5571
1456-Induced draft fan dampers | 68 | 68 | 16819.5 | 339404.2209
1457-Induced draft fan lubrication systems | 16 | 16 | 4930.61 | 158694.0823
1460-Induced draft fan fouling | 11 | 11 | 804 | 40240.6332
1470-Induced draft fan motors and drives | 191 | 191 | 27916.73 | 2308141.166
1471-Induced draft fan motors - variable speed | 49 | 49 | 10401.85 | 475393.896
1472-Inducted draft fan coupling | 6 | 6 | 1296.5 | 146484.7828
1475-Induced draft fan controls | 108 | 108 | 16688.08 | 277622.8444
1476-Induced draft fan speed changer | 14 | 14 | 1942.2 | 83477.1544
1480-Other induced draft fan problems | 230 | 230 | 20656.55 | 1115006.246
1487-Air heater (tubular) | 13 | 13 | 2573.5 | 268451.9658
1488-Air heater (regenerative) | 146 | 146 | 25189.57 | 1023695.7356
1489-Air heater (heat pipe; plate-type) | 19 | 19 | 3986 | 264524.0319
1492-Air heater fouling (tubular) | 9 | 9 | 158.5 | 8516.6916
1493-Air heater fouling (regenerative) | 38 | 38 | 1286.99 | 350561.9572
1495-Other air heater fouling (heat pipe; plate-type) | 4 | 4 | 1222 | 95714.1328
1500-Air heater soot blowers | 11 | 11 | 2049.35 | 94403.1409
1510-Flue gas ducts (except recirculation) | 16 | 16 | 2310 | 2428105.3661
1512-Flue gas expansion joints | 5 | 5 | 1130.07 | 24298.009
1520-Flue gas dampers (except recirculation) | 8 | 8 | 1115 | 46641.1161
1530-Other flue gas problems | 42 | 42 | 4026.93 | 573560.8473
1535-Flue gas recirculating fan | 5 | 5 | 1418.5 | 26643.9999
1536-Flue gas recirculating fan dampers | 1 | 1 | 455 | 2297.75
1550-Flue gas recirculation fan motors | 2 | 2 | 117 | 247264.1
1560-Other flue gas recirculation fan problems | 1 | 1 | 747 | 1954.6495
1570-Flue gas recirculation ducts | 2 | 2 | 440.87 | 14508.4733
1572-Flue gas recirculation duct expansion joints | 1 | 1 | 214.27 | 492.821
1580-Flue gas recirculation dampers | 2 | 2 | 117 | 554.05
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 7 | 7 | 884.52 | 761.6189
1591-Stack damper and linkage | 13 | 13 | 2033.84 | 14577.5522
1592-Stack damper linkage motors | 1 | 1 | 32 | 72.5333
1599-Other miscellaneous boiler air and gas system problems | 263 | 263 | 10647.72 | 341461.8265
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 251 | 251 | 56153.15 | 932328.404
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 156 | 156 | 14639.98 | 569063.4851
1720-Desuperheater/attemperator controls | 73 | 73 | 11355.98 | 294606.621
1740-Boiler drum gage glasses/level indicator | 77 | 77 | 20400.1 | 112725.4729
1750-Burner management system | 131 | 131 | 21671.1 | 289368.5005
1760-Feedwater instrumentation (not local controls) | 43 | 43 | 11029.24 | 90839.1254
1761-Combustion /Steam condition instrumentation (not local controls) | 14 | 14 | 5509 | 17138.5988
1762-Desuperheater/attemperator instrumentation (not local controls) | 18 | 18 | 3125.99 | 33819.5468
1799-Other boiler instrumentation and control problems | 240 | 240 | 53380.47 | 1654949.6499
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 1381 | 229225.5329
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 40 | 40 | 2001.84 | 133966.0339
1810-Other boiler inspections | 1 | 1 | 300 | 744.9999
1811-Boiler Inspections - problem identification/investigative | 5 | 5 | 726 | 5625.9998
1812-Boiler Inspections - scheduled or routine | 7 | 7 | 771.27 | 105987.6727
1850-Boiler water condition (not feedwater water quality) | 228 | 228 | 40577.12 | 1126468.5268
1900-Improper balance between tube sections not due to fouling or plugging | 1 | 1 | 64 | 951.4666
1910-Inadequate air not due to equipment problems | 35 | 35 | 516.6 | 916404.6727
1980-Boiler safety valve test | 11 | 11 | 1716.28 | 5091.0393
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 53 | 53 | 6325.37 | 82974.5633
1999-Boiler; miscellaneous | 825 | 825 | 34723.04 | 1991396.0642
2010-Fuel failure including high activity in Reactor Coolant System (RCS) or off-gas system | 2 | 2 | 264.87 | 929.9488
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 24 | 24 | 1876.57 | 55930.3627
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 3 | 3 | 231.64 | 7506.8383
2031-Fuel preconditioning | 2 | 2 | 1086 | 24446.9995
2035-Core xenon restrictions | 6 | 6 | 444.72 | 12982.298
2036-End-of-life scram reactivity/rod worth restrictions | 1 | 1 | 171.3 | 38913.6499
2040-Core physics tests | 2 | 2 | 351.97 | 6537.3545
2060-Excore nuclear instrumentation | 1 | 1 | 28.72 | 377.1893
2061-Incore nuclear instrumentation | 1 | 1 | 118.75 | 2810.4166
2062-Other fuel/core related instrumentation problems | 1 | 1 | 40.13 | 200.65
2070-Normal refueling | 4 | 4 | 3476.38 | 1551970.6132
2110-Control rod drive motors | 1 | 1 | 328 | 2695.0664
2111-Control rod magnetic jack drives | 2 | 2 | 1320.79 | 309355.136
2140-Control rod drive cooling | 1 | 1 | 37 | 74
2151-Control rod drive controls | 4 | 4 | 2003.58 | 149059.8633
2152-Control rod drive power supplies | 2 | 2 | 1934 | 91240.8997
2155-Control rod testing | 3 | 3 | 1050.7 | 40102.0053
2200-Reactor coolant/recirculating pumps | 11 | 11 | 3687.44 | 358890.9568
2210-Reactor coolant/recirculating pump motors | 2 | 2 | 1596 | 188770.3998
2220-Reactor coolant/recirculating pump MG sets | 2 | 2 | 2194.28 | 460667.138
2270-Power operated relief and safety/relief valves | 4 | 4 | 4112.17 | 185730.5345
2300-Recirculation loop flow control valves | 3 | 3 | 346.12 | 18342.5571
2350-BWR feedwater controls | 2 | 2 | 745.01 | 52228.5575
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 1 | 1 | 1166 | 96292.1663
2380-Reactor control system/integrated control system problems | 2 | 2 | 1349 | 59617.4665
2390-Other reactor coolant system instruments and controls | 2 | 2 | 827.57 | 31900.2343
2422-Other steam generator internals problems | 1 | 1 | 1.9 | 8346.6367
2440-Steam generator chemistry (excluding feedwater chemistry) | 1 | 1 | 9.65 | 548.2808
2450-Blowdown system piping A | 1 | 1 | 1122 | 100475.1
2480-Other blowdown | 4 | 4 | 46.8 | 471.6466
2510-Main steam isolation valves (BWR and PWR) | 2 | 2 | 1494.78 | 116607.202
2520-Main steam safety/relief valves (except BWR) | 1 | 1 | 18 | 2752.2
2550-Steam generator instruments (including piping and valves) (no RPS or SAS inputs) | 7 | 7 | 3985.7 | 53479.4619
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 3 | 3 | 70 | 103
2630-Safeguard actuation system (including sensors; logic; activators; and sequencers) | 1 | 1 | 1242 | 106749.9
2799-Other containment system problems | 4 | 4 | 2845.34 | 100295.638
2815-Heat exchangers | 1 | 1 | 267.49 | 6357.3455
2817-Instruments and controls | 3 | 3 | 13.8 | 34.5833
2819-Other CVCS and RWC problems | 2 | 2 | 5 | 43
2820-Nuclear closed cooling water pumps | 1 | 1 | 671.43 | 114870.4823
2821-Nuclear closed cooling water piping | 1 | 1 | 877.7 | 102690.9
2999-Other miscellaneous nuclear reactor problems | 1 | 1 | 22 | 484
3110-Condenser tube leaks | 140 | 140 | 37226.11 | 2145776.8705
3111-Condenser tube fouling shell side | 25 | 25 | 1937.5 | 210786.8876
3112-Condenser tube fouling tube side | 261 | 261 | 16337.65 | 671293.949
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 94 | 94 | 15888.09 | 122417.8714
3114-Air-cooled condenser tubes | 2 | 2 | 289 | 7769.2832
3115-Air-cooled condenser pumps | 11 | 11 | 1969.28 | 19357.8394
3116-Air-cooled condenser fans | 27 | 27 | 964.18 | 2961.1531
3117-Air-cooled condenser fan motors | 14 | 14 | 342.5 | 1331.6666
3118-Other Air-cooled condenser problems | 1143 | 1143 | 45993.5 | 104954.9679
3119-Other condenser tube casing or shell and internal problems | 40 | 40 | 4128.02 | 900281.0722
3120-Tube sheets | 1 | 1 | 26.57 | 371.98
3121-Expansion joint | 8 | 8 | 1338.9 | 101494.133
3122-Gaskets and seals | 5 | 5 | 2236.5 | 193217.4496
3123-Hot well | 16 | 16 | 1461.85 | 2696.9587
3124-Tube sheet fouling | 43 | 43 | 744 | 121330.9997
3129-Other condenser casing or shell and internal problems | 15 | 15 | 3395 | 347026.1824
3130-Air ejectors | 13 | 13 | 2081 | 198754.4825
3131-Air ejector piping and valves | 17 | 17 | 2732.67 | 27628.1372
3132-Inter and after condensers | 1 | 1 | 27 | 321.75
3133-Vacuum pumps | 54 | 54 | 9498.87 | 220386.6076
3134-Vacuum pump piping and valves | 11 | 11 | 3219.11 | 17142.9943
3135-Vacuum pump motor and auxiliaries | 7 | 7 | 1855.03 | 22877.8136
3139-Other air extraction system problems - general | 21 | 21 | 3495.51 | 54473.1229
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 319 | 319 | 42402.68 | 1404868.7861
3150-Hot well level controls | 28 | 28 | 5159.41 | 45182.1409
3151-Vacuum pump and air ejector controls | 11 | 11 | 1657 | 9176.0248
3152-Air-cooled condenser controls | 5 | 5 | 1508 | 1621.8997
3159-Other condensing system controls and instruments | 12 | 12 | 2971 | 28966.862
3186-Auxiliary Condenser and Associated Equipment | 21 | 21 | 2145.99 | 167921.0117
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 19 | 19 | 2099.92 | 111911.6415
3199-Other miscellaneous condensing system problems | 133 | 133 | 12758.86 | 553223.9891
3210-Circulating water pumps | 244 | 244 | 31856.18 | 2994989.5191
3211-Circulating water pump motors | 115 | 115 | 13682.45 | 1237651.5459
3220-Circulating water piping | 27 | 27 | 5236.6 | 488793.7823
3221-Circulating water piping fouling | 3 | 3 | 570 | 2419.5331
3230-Circulating water valves | 26 | 26 | 6354.16 | 771395.7082
3231-Waterbox | 29 | 29 | 8132.2 | 117389.1145
3232-Condenser tube cleaning system including debris filter | 41 | 41 | 4082.4 | 62210.7353
3233-Circulating water priming system | 3 | 3 | 715 | 30639.6665
3235-Cooling tower booster pump | 7 | 7 | 556.08 | 65666.0609
3236-Cooling tower booster motor | 4 | 4 | 58.79 | 16844.97
3238-Cooling tower fan motors | 23 | 23 | 1918.53 | 26991.6073
3239-Cooling tower fan motors - variable speed | 2 | 2 | 102.4 | 476.9
3240-Cooling tower fans | 71 | 71 | 3668.81 | 253572.1887
3241-Cooling tower efficiency below design | 61 | 61 | 1707.17 | 40071.8397
3242-Cooling tower fill damage | 4 | 4 | 514 | 395052.333
3243-Cooling tower icing | 1 | 1 | 340 | 1603.6664
3245-Other cooling tower problems | 78 | 78 | 7995.16 | 493279.0235
3246-Cooling tower fouling | 2 | 2 | 30.4 | 6208.6
3247-Cooling tower instrumentation | 2 | 2 | 104 | 177.8666
3250-Circulating water system instruments and controls | 26 | 26 | 6500.41 | 169926.8692
3260-Traveling screens | 45 | 45 | 5318.9 | 297123.8883
3261-Traveling screen fouling | 13 | 13 | 3383.01 | 387223.3078
3269-Circulating water biological conditions (ie; zebra mussels) | 28 | 28 | 3116.35 | 19980.1065
3270-Intake system problems other than traveling screens | 26 | 26 | 4066 | 111221.038
3271-Intake grating fouling | 4 | 4 | 394.35 | 6947.7808
3272-Circulating water screenwash system | 5 | 5 | 679.44 | 6963.0909
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 80 | 80 | 14199 | 151611.7617
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 10 | 10 | 2205.1 | 24616.6988
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 67 | 67 | 7122.6 | 451706.3845
3281-Circulating water tempering system | 4 | 4 | 461.64 | 1519.3599
3282-Circulating water cooling ponds | 11 | 11 | 574 | 7434.0331
3285-Circulating water chemistry | 7 | 7 | 2254.5 | 28498.7656
3290-Waste water (zero discharge) tanks; pumps and motors | 2 | 2 | 456.5 | 11458.15
3292-Waste water (zero discharge) piping | 3 | 3 | 548 | 19336.033
3295-Other Waste water (zero discharge) problems | 1 | 1 | 250 | 6070.8332
3299-Other circulating water system problems | 48 | 48 | 8769.04 | 311872.252
3300-Condensate water pre-treatment | 19 | 19 | 3729.88 | 142796.0628
3310-Condensate/hotwell pumps | 102 | 102 | 15630.53 | 1867934.37
3311-Condensate/hotwell pump motor | 82 | 82 | 14513.86 | 553306.4912
3312-Condensate booster pump | 22 | 22 | 4629.35 | 78346.2103
3313-Condensate booster pump motor | 13 | 13 | 4410.5 | 832386.199
3314-Condensate booster pump motor - variable speed | 1 | 1 | 205 | 662.8333
3315-Condensate booster pump drive (other than 3313 and 3314) | 2 | 2 | 554 | 34864.2164
3320-Condensate piping | 22 | 22 | 7014.9 | 299776.5499
3330-Condensate valves | 60 | 60 | 11336.98 | 341982.8556
3339-LP heater head leaks | 1 | 1 | 158 | 4450.3332
3340-LP heater tube leaks | 19 | 19 | 2223.31 | 176372.3054
3341-Other LP heater - general | 27 | 27 | 1876.68 | 25798.9249
3342-IP heater tube leaks | 9 | 9 | 512.5 | 70848.1082
3343-Other IP heater - general | 8 | 8 | 731.58 | 16243.8841
3344-Deaerator (including level control) | 106 | 106 | 20742.42 | 980080.6927
3350-Condensate polishing and filtering systems | 30 | 30 | 6297.45 | 63697.3044
3351-Chemical addition systems | 7 | 7 | 1224.01 | 49156.5871
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 74 | 74 | 15736.03 | 201319.0615
3360-Condensate makeup and return (including storage tanks) | 35 | 35 | 7238.76 | 105967.4811
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 21 | 21 | 4464.67 | 60032.539
3380-Condensate coolers | 1 | 1 | 168.8 | 183848.52
3399-Other miscellaneous condensate system problems | 40 | 40 | 9335.27 | 644075.6349
3401-Startup feedwater pump | 9 | 9 | 3501 | 34918.3323
3402-Startup feedwater pump drives - all types | 1 | 1 | 324.32 | 62723.488
3407-Feedwater pump suction screens | 11 | 11 | 2501.4 | 25623.7325
3408-Feedwater pump drive - local controls | 39 | 39 | 10782.62 | 184073.5353
3409-Feedwater pump drive motor - variable speed | 25 | 25 | 3233.6 | 56935.0942
3410-Feedwater pump | 391 | 391 | 75191.28 | 5891371.294
3411-Feedwater pump drive - motor | 59 | 59 | 8327.36 | 282820.0486
3412-Feedwater pump drive - steam turbine | 125 | 125 | 41243.51 | 3158726.2386
3413-Feedwater pump coupling and drive shaft | 18 | 18 | 2731.1 | 160483.2743
3414-Feedwater pump local controls | 41 | 41 | 13218.43 | 168852.4402
3415-Feedwater pump/drive lube oil system | 76 | 76 | 22330.61 | 402195.8568
3416-Other feedwater pump problems | 122 | 122 | 28058.74 | 659451.7677
3417-Feedwater pump drive - main shaft | 3 | 3 | 1522.4 | 105930.3943
3418-Feedwater pump drive - other | 12 | 12 | 1994.4 | 55847.6312
3420-Feedwater piping and supports | 43 | 43 | 6332.54 | 261670.4101
3430-Feedwater regulating (boiler level control) valve | 162 | 162 | 39059.22 | 1211998.0443
3431-Other feedwater valves | 180 | 180 | 41872.21 | 1397805.2202
3439-HP heater head leaks | 10 | 10 | 1468.73 | 92384.574
3440-High pressure heater tube leaks | 150 | 150 | 17811.81 | 1507025.2953
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 64 | 64 | 9366.7 | 353129.0604
3454-Feedwater Booster Pump | 27 | 27 | 7436.6 | 145645.2583
3455-Feedwater Booster Pump Drive - Motor | 10 | 10 | 2182.59 | 80923.4103
3458-Feedwater Booster Pump Local Controls | 1 | 1 | 92 | 1225.1333
3459-Feedwater Booster Pump/Drive Lube Oil System | 1 | 1 | 315 | 482.9999
3460-Other Feedwater Booster Pump Problems | 1 | 1 | 48 | 288
3461-Feedwater Booster Pump Drive - Main Shaft | 1 | 1 | 233.33 | 139.998
3499-Other feedwater system problems | 166 | 166 | 24009.75 | 862024.722
3501-Heater drain pumps | 30 | 30 | 2327.28 | 120258.1605
3502-Heater level control | 49 | 49 | 6432.87 | 307252.383
3503-Heater drain piping | 9 | 9 | 3535.31 | 474568.4196
3504-Heater drain valves | 47 | 47 | 6668.2 | 358420.9439
3505-Heater drain pump drive | 2 | 2 | 520.01 | 32730.1955
3509-Other heater drain system problems | 1 | 1 | 8.4 | 130.2
3520-HP Extraction steam piping | 3 | 3 | 1098 | 201267.4327
3521-HP Extraction steam valves | 14 | 14 | 3531.2 | 185643.7891
3522-HP Extraction steam instruments and controls | 7 | 7 | 783.34 | 166520.3497
3529-Other HP extraction steam system problems | 10 | 10 | 2310.5 | 51135.9524
3530-IP Extraction steam piping | 2 | 2 | 326 | 93249.5831
3531-IP Extraction steam valves | 4 | 4 | 546.34 | 117933.903
3532-IP Extraction steam instruments and controls | 3 | 3 | 1070 | 15846.6661
3539-Other IP extraction steam system problems | 7 | 7 | 508 | 11038.5332
3540-LP Extraction steam piping | 12 | 12 | 734.83 | 159808.3693
3541-LP Extraction steam valves | 4 | 4 | 209 | 4287.35
3549-Other LP extraction steam system problems | 11 | 11 | 324.25 | 49537.05
3600-Switchyard transformers and associated cooling systems - external | 21 | 21 | 2092.79 | 308800.5443
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 9 | 9 | 2396.24 | 207266.9769
3610-Switchyard circuit breakers - (not outside management control) | 75 | 75 | 11702.83 | 2700762.5645
3611-Switchyard circuit breakers - external | 87 | 87 | 17804.77 | 427545.9251
3612-Switchyard system protection devices - external | 95 | 95 | 17934.27 | 396797.5839
3613-Switchyard system protection devices - (not outside management control) | 43 | 43 | 6970.35 | 208208.2376
3618-Other switchyard equipment ? (not outside management control) | 17 | 17 | 4427.91 | 174651.6517
3619-Other switchyard equipment - external | 71 | 71 | 11146.18 | 629447.9026
3620-Main transformer | 373 | 373 | 49207.03 | 11376422.6839
3621-Unit auxiliaries transformer | 115 | 115 | 25465.25 | 2967352.0098
3622-Station service startup transformer | 27 | 27 | 5751.76 | 467087.3625
3623-Auxiliary generators | 2 | 2 | 101 | 1956.5833
3624-Generator Voltage Supply System | 18 | 18 | 2287.72 | 59383.5621
3629-Other switchyard or high voltage system problems - external | 70 | 70 | 15316.14 | 425075.5293
3630-480-volt transformers | 12 | 12 | 3261.23 | 70436.3672
3631-480-volt circuit breakers | 77 | 77 | 14285.35 | 231092.8325
3632-480-volt conductors and buses | 16 | 16 | 3315 | 194644.9656
3634-480-volt protection devices | 11 | 11 | 2004.98 | 17596.1821
3639-Other 480-volt problems | 14 | 14 | 2325.86 | 23183.2658
3640-AC instrument power transformers | 29 | 29 | 2621.5 | 57675.2827
3641-AC Circuit breakers | 84 | 84 | 10826.84 | 395952.6848
3642-AC Conductors and buses | 24 | 24 | 6909.54 | 304180.2087
3643-AC Inverters | 25 | 25 | 5841.27 | 205656.2289
3644-AC Protection devices | 96 | 96 | 11145.6 | 175687.0494
3649-Other AC instrument power problems | 14 | 14 | 1508.99 | 28353.289
3650-DC instrument power battery chargers | 24 | 24 | 1727.24 | 83515.2816
3651-DC circuit breakers | 8 | 8 | 1682 | 28128.1664
3652-DC conductors and buses | 6 | 6 | 526 | 264630.4165
3653-DC protection devices | 30 | 30 | 4035.16 | 139699.2825
3659-Other DC power problems | 38 | 38 | 4925.18 | 1847234.2705
3660-4160-volt transformers | 12 | 12 | 1768.48 | 196484.2284
3661-4160-volt circuit breakers | 116 | 116 | 21192.57 | 1492986.6518
3662-4160-volt conductors and buses | 26 | 26 | 10374.9 | 508456.0415
3664-4160-volt protection devices | 36 | 36 | 8660.05 | 441229.6505
3669-Other 4160-volt problems | 19 | 19 | 2449.5 | 64309.9823
3670-12kV transformers | 29 | 29 | 5141.68 | 206324.1572
3671-12kV circuit breakers | 70 | 70 | 9070.62 | 1913482.602
3672-12kV conductors and buses | 43 | 43 | 6184.56 | 1075625.3347
3673-12kV insulators | 22 | 22 | 2192.36 | 151693.5447
3674-12kV protection devices | 36 | 36 | 3279.88 | 157569.1022
3679-Other 12kV problems | 6 | 6 | 314 | 31540.3999
3680-Other voltage system transformers | 28 | 28 | 4543.76 | 1782717.472
3681-Other voltage system breakers | 41 | 41 | 3807.51 | 140861.8338
3682-Other voltage system conductors and buses | 27 | 27 | 7137.09 | 443557.4615
3683-Other voltage system insulators | 8 | 8 | 1743.39 | 62549.0712
3684-Other voltage system protection devices | 33 | 33 | 4286.06 | 100314.1867
3689-Other Other voltage system problems | 45 | 45 | 7894.33 | 457894.6639
3690-Station Service Power Distribution System; General | 132 | 132 | 13099.46 | 128448.205
3700-Power Station switchyard (non generating unit equipment) | 63 | 63 | 8531.69 | 519726.7348
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 84 | 84 | 9261.45 | 717482.1956
3720-Transmission equipment at the 1st substation) | 40 | 40 | 4624.51 | 145895.5549
3730-Transmission equipment beyond the 1st substation | 62 | 62 | 6313.58 | 220160.7011
3800-Open cooling water pumps and motors | 1 | 1 | 5 | 5.6667
3801-Open cooling water piping | 5 | 5 | 1405.4 | 96203.9497
3803-Open cooling water heat exchangers | 2 | 2 | 47 | 325.6833
3805-Open cooling water system instrumentation | 3 | 3 | 233 | 983.1666
3806-Open cooling water strainer | 1 | 1 | 293 | 102.55
3809-Other open cooling water problems | 5 | 5 | 719 | 3410.0497
3810-Service water pumps and motors | 35 | 35 | 2576.45 | 158123.5431
3811-Service water piping | 62 | 62 | 7706.77 | 430145.5568
3812-Service water valves | 6 | 6 | 1260.8 | 25812.5429
3813-Service water heat exchangers | 2 | 2 | 48.5 | 1200.3333
3814-Service water system fouling | 3 | 3 | 122.5 | 3376.8583
3819-Other service water problems A | 29 | 29 | 5940.1 | 69626.8081
3820-Closed cooling water pumps | 31 | 31 | 4834 | 107986.9397
3821-Closed cooling water piping | 8 | 8 | 2094.38 | 123217.5396
3822-Closed cooling water valves | 10 | 10 | 1257.38 | 1249.0128
3823-Closed cooling water heat exchangers | 20 | 20 | 3567.87 | 86208.0778
3824-Closed cooling water system fouling | 5 | 5 | 121 | 4861.0833
3825-Closed cooling water instrumentation | 3 | 3 | 960 | 1950.6662
3829-Other closed cooling water system problems A | 51 | 51 | 4778.22 | 92144.4854
3830-Auxiliary boiler | 40 | 40 | 15068.38 | 990326.0135
3831-Auxiliary steam piping | 6 | 6 | 845.4 | 19285.1562
3832-Auxiliary steam valves | 15 | 15 | 3148.7 | 95625.7488
3833-Auxiliary steam controls and instruments | 35 | 35 | 8140.51 | 88538.3115
3834-Auxiliary boiler tube leaks | 26 | 26 | 7776.9 | 339654.1237
3835-Auxiliary boiler burner management system | 4 | 4 | 1671 | 14061.9996
3836-Steam Transfer to Other Unit | 97 | 97 | 9872.82 | 168856.7427
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 34 | 34 | 8543.12 | 293932.438
3840-Service air compressors | 27 | 27 | 3521.28 | 30529.2768
3841-Service air piping | 8 | 8 | 232.35 | 3305.9824
3842-Service air valves | 4 | 4 | 1034.5 | 5011.9914
3843-Service air dryers | 6 | 6 | 863.4 | 1779.3766
3844-Soot blowing air compressor and system | 16 | 16 | 2959.8 | 100599.4125
3849-Other service air problems | 9 | 9 | 596.8 | 6869.9565
3850-Instrument air compressors | 81 | 81 | 17108.45 | 183497.2951
3851-Instrument air piping | 11 | 11 | 2670.1 | 16947.2944
3852-Instrument air valves | 13 | 13 | 2177.45 | 27582.687
3853-Instrument air dryers | 8 | 8 | 2144.52 | 19759.2407
3859-Other instrument air problems | 36 | 36 | 7607.9 | 278933.2696
3860-Fire protection system pumps | 1 | 1 | 112 | 29.8666
3861-Fire protection system piping | 5 | 5 | 857.85 | 22016.989
3862-Fire protection system valves | 4 | 4 | 279.3 | 16544.2665
3863-Fire protection system fouling | 1 | 1 | 32.93 | 422.0528
3864-Fire protection system instrumentation and controls | 76 | 76 | 7731.01 | 337146.8198
3869-Other fire protection system problems | 52 | 52 | 4310.24 | 224533.3054
3870-Fuel Gas Compressor and Motors | 48 | 48 | 4800.69 | 63094.9618
3871-Fuel Gas Compressor Piping | 10 | 10 | 474.24 | 8121.8712
3872-Fuel Gas Compressor Valves | 40 | 40 | 5359.9 | 77042.4254
3873-Fuel Gas Compressor Heat Exchangers | 2 | 2 | 88 | 1256
3874-Fuel Gas Compressor Controls and Instrumentation | 58 | 58 | 4955.55 | 12791.8301
3875-Fuel Gas Compressor Filters | 3 | 3 | 245.8 | 2146.2933
3876-Fuel Gas Compressor Fire System | 2 | 2 | 84 | 512.4333
3879-Fuel Gas Compressor - other | 41 | 41 | 2908.2 | 36531.774
3880-Seal air fan | 4 | 4 | 896 | 68466.9164
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 97 | 97 | 9607.55 | 1402017.2774
3899-Other miscellaneous auxiliary system problems | 94 | 94 | 8667.3 | 178873.7367
3950-Process computer | 40 | 40 | 3175.63 | 328131.6535
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 210 | 210 | 5569.48 | 471518.2411
3970-Distributive Control System (DCS) - process computer | 53 | 53 | 7718.85 | 128934.0709
3971-DCS - data highway | 30 | 30 | 3744.09 | 81655.58
3972-DCS - hardware problems (including card failure) | 152 | 152 | 27482.63 | 435210.3115
3973-DCS - internal and termination wiring | 2 | 2 | 561 | 3790.5998
3974-DCS - logic problems | 80 | 80 | 14187.69 | 103917.3767
3975-DCS - upgrades | 36 | 36 | 3767.95 | 30487.0054
3979-Other DCS problems | 55 | 55 | 9318.28 | 341926.3306
3980-Programmable Logic Controller (PLC) | 32 | 32 | 1885.49 | 10040.9028
3981-PLC - data highway | 13 | 13 | 1094.76 | 25435.748
3982-PLC - hardware problems (including card failure) | 28 | 28 | 2787.35 | 66733.9889
3983-PLC - internal and termination wiring | 3 | 3 | 82.48 | 816.2013
3984-PLC - logic problems | 23 | 23 | 1486.13 | 3292.4334
3985-PLC - upgrades | 18 | 18 | 1086 | 1300.5996
3989-Other PLC problems | 28 | 28 | 2161.55 | 24297.4502
3995-Powerhouse heating and ventilating systems | 5 | 5 | 274.4 | 27938.0399
3996-Air conditioning systems - rooms and areas | 25 | 25 | 3164.51 | 13119.3365
3998-Balance of plant overhaul/outage | 12 | 12 | 1624.75 | 44060.7306
3999-Other miscellaneous balance of plant problems | 561 | 561 | 58244.81 | 2016525.8515
4000-Outer casing A | 3 | 3 | 1052.74 | 14110.8492
4001-Inner casing C | 6 | 6 | 555 | 573.6666
4010-Nozzles and nozzle blocks C | 8 | 8 | 190 | 112151.9166
4012-Buckets or blades A | 3 | 3 | 423.86 | 73886.2705
4014-Bucket or blade fouling C | 49 | 49 | 629 | 115656.1998
4020-Shaft seals B | 5 | 5 | 1059.2 | 69455.9897
4030-Rotor shaft C | 8 | 8 | 1754 | 11966.6828
4040-Bearings C | 192 | 192 | 27002.88 | 2617063.2966
4041-HP steam turbine thrust bearings | 40 | 40 | 4515 | 341249.6147
4099-Other high pressure turbine problems | 55 | 55 | 12710.76 | 2986514.1932
4100-Outer casing B | 2 | 2 | 346 | 34455.8332
4112-Buckets or blades B | 1 | 1 | 485 | 453919.583
4130-Rotor shaft B | 5 | 5 | 1054.25 | 613931.5288
4140-Bearings D | 21 | 21 | 5683.05 | 236257.8379
4141-IP steam turbine thrust bearings | 6 | 6 | 1632 | 105080.5831
4199-Other intermediate pressure turbine problems | 24 | 24 | 8468.13 | 443403.5953
4201-Inner casing A | 3 | 3 | 425.62 | 2342.2641
4211-Diaphragms C | 5 | 5 | 1510.7 | 10063.9649
4212-Buckets or blades C | 72 | 72 | 9260.9 | 1101424.1377
4220-Shaft seals D | 3 | 3 | 443.45 | 451.3958
4230-Rotor shaft A | 3 | 3 | 1510.7 | 190727.6275
4240-Bearings E | 36 | 36 | 9261.66 | 605994.247
4241-LP steam turbine thrust bearings | 4 | 4 | 1735.7 | 180633.2711
4250-Other low pressure turbine problems | 42 | 42 | 8504.5 | 301220.3116
4260-Main stop valves | 103 | 103 | 23773.42 | 1962017.4282
4261-Control valves | 301 | 301 | 61223.97 | 3536089.5096
4262-Intercept valves | 72 | 72 | 21123.96 | 419132.6525
4263-Reheat stop valves | 38 | 38 | 11016.12 | 620396.425
4264-Combined intercept valves | 15 | 15 | 3204.9 | 206830.3259
4265-Miscellaneous drain and vent valves | 18 | 18 | 5427.61 | 284169.9031
4266-Main stop valve testing | 8 | 8 | 1585.9 | 5664.5392
4267-Control valve testing | 36 | 36 | 8187.14 | 254496.825
4268-Reheat/intercept valve testing | 14 | 14 | 4596.52 | 42132.6691
4269-Other turbine valves (including LP steam admission valves) | 89 | 89 | 15463.52 | 825115.1709
4270-Crossover or under piping | 10 | 10 | 4294 | 18761.2319
4279-Miscellaneous turbine piping | 33 | 33 | 12412.25 | 371293.3344
4280-Lube oil pumps A | 37 | 37 | 7855.77 | 414109.8947
4281-Lube oil coolers A | 12 | 12 | 2573.54 | 203890.6035
4283-Lube oil system valves and piping | 16 | 16 | 1701.15 | 71329.4369
4284-Lube oil pump drive | 1 | 1 | 82 | 1015.4333
4289-Other lube oil system problems | 72 | 72 | 14860.43 | 792837.2364
4290-Hydraulic system pumps | 54 | 54 | 9195.87 | 237636.7185
4291-Hydraulic system coolers | 1 | 1 | 235 | 4120.3333
4292-Hydraulic system filters | 2 | 2 | 657 | 5142.5996
4293-Hydraulic system pipes and valves | 76 | 76 | 22002.99 | 707622.271
4299-Other hydraulic system problems | 86 | 86 | 20201.11 | 627072.1843
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 23 | 23 | 7351.83 | 139551.3805
4301-Turbine governing system | 60 | 60 | 11806.89 | 265310.4388
4302-Turbine trip devices (including instruments) | 130 | 130 | 24878.09 | 505151.0682
4303-Exhaust hood and spray controls | 15 | 15 | 4371 | 7908.9153
4304-Automatic turbine control systems - mechanical | 7 | 7 | 360.5 | 147875.6167
4305-Automatic turbine control systems - mechanical - hydraulic | 10 | 10 | 4215.8 | 27720.4754
4306-Automatic turbine control systems - electro-hydraulic - analog | 18 | 18 | 3584.9 | 132078.0707
4307-Automatic turbine control systems - electro-hydraulic - digital | 8 | 8 | 2366.8 | 9152.2973
4308-Automatic turbine control systems - digital control and monitoring | 59 | 59 | 13867.76 | 322389.1239
4309-Other turbine instrument and control problems | 131 | 131 | 30338.07 | 701298.9418
4310-Steam Turbine Control System - data highway | 13 | 13 | 2635.8 | 85285.6574
4311-Steam Turbine Control System - hardware problems (including card failure) | 72 | 72 | 12420.66 | 252103.5109
4312-Steam Turbine Control System - internal and termination wiring | 10 | 10 | 3052.06 | 49308.8174
4313-Steam Turbine Control System - logic problems | 51 | 51 | 10305.87 | 51803.1541
4314-Steam Turbine Control System - upgrades | 8 | 8 | 1410.75 | 31399.5454
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 5 | 5 | 1156.47 | 2229671.2009
4401-Inspection F | 8 | 8 | 2015.7 | 265184.3163
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 210.5 | 216742.3916
4410-Turning gear and motor A | 40 | 40 | 9583.48 | 1378032.8566
4412-Steam turbine clutch (single shaft configuration) | 1 | 1 | 150.22 | 225.33
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 177 | 177 | 37989.41 | 2576945.594
4430-Gland seal system | 79 | 79 | 14182.76 | 551959.5293
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 7 | 7 | 186.28 | 11337.4774
4445-Steam reheater | 2 | 2 | 162 | 450.6666
4450-Water induction | 3 | 3 | 533 | 1599310.7331
4460-Turbine overspeed trip test | 14 | 14 | 1655.4 | 36606.1695
4470-Differential expansion | 69 | 69 | 18442.32 | 387997.4502
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 5 | 5 | 1408.8 | 12816.8761
4499-Other miscellaneous steam turbine problems | 441 | 441 | 55388.97 | 3021642.2615
4500-Rotor windings (including damper windings and fan blades on hydro units) | 112 | 112 | 10078.32 | 4046739.6281
4510-Rotor collector rings | 20 | 20 | 3121.44 | 350494.6881
4511-Rotor; General | 32 | 32 | 3796.04 | 2711504.6788
4512-Retaining Rings | 1 | 1 | 172 | 1588.1333
4520-Stator windings; bushings; and terminals | 43 | 43 | 5919.27 | 4758505.7356
4530-Stator core iron | 6 | 6 | 1916 | 1467448.6999
4535-Stator; General | 83 | 83 | 9250.92 | 3117218.6558
4540-Brushes and brush rigging | 29 | 29 | 6463.1 | 716165.4151
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 107 | 107 | 7417.2 | 637532.8143
4551-Generator bearings | 59 | 59 | 6284.36 | 1013702.4934
4552-Generator lube oil system | 120 | 120 | 8170.52 | 373870.7405
4555-Bearing cooling system A | 42 | 42 | 3183.55 | 50455.797
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 146 | 146 | 18682.89 | 707653.2132
4570-Generator casing | 3 | 3 | 780.7 | 155489.4729
4580-Generator end bells and bolting | 1 | 1 | 164.4 | 90954.3
4590-Generator brakes | 35 | 35 | 4161.86 | 38963.0553
4600-Exciter drive - motor | 19 | 19 | 2454.19 | 49246.5268
4601-Exciter field rheostat | 7 | 7 | 676.27 | 9760.2905
4602-Exciter commutator and brushes | 45 | 45 | 10788.46 | 1791509.558
4603-Solid state exciter element | 58 | 58 | 7517.04 | 284253.3287
4604-Exciter drive - shaft | 6 | 6 | 2808 | 992244.4664
4605-Exciter transformer | 33 | 33 | 6881.18 | 908947.5384
4609-Other exciter problems | 655 | 655 | 95511.63 | 5443144.9708
4610-Hydrogen cooling system piping and valves | 17 | 17 | 4732.2 | 271222.0228
4611-Hydrogen coolers | 52 | 52 | 5966.72 | 1229162.9287
4612-Hydrogen storage system | 1 | 1 | 306 | 3519
4613-Hydrogen seals | 10 | 10 | 3609.46 | 854582.4176
4619-Other hydrogen system problems | 38 | 38 | 9513.92 | 490673.639
4620-Air cooling system | 31 | 31 | 2261.17 | 66405.3663
4630-Liquid cooling system | 55 | 55 | 10824.27 | 789147.9166
4640-Seal oil system and seals A | 48 | 48 | 9048.34 | 3228446.9225
4650-Other cooling system problems | 43 | 43 | 6312.89 | 122878.804
4700-Generator voltage control | 212 | 212 | 32149.96 | 845265.3458
4710-Generator metering devices | 49 | 49 | 6654.63 | 285981.081
4720-Generator synchronization equipment | 171 | 171 | 16639.28 | 512242.6182
4730-Generator current and potential transformers | 88 | 88 | 15822.31 | 548582.4893
4740-Emergency generator trip devices | 259 | 259 | 36952.4 | 1217444.9851
4750-Other generator controls and metering problems | 259 | 259 | 31578.12 | 753477.351
4800-Generator main leads | 43 | 43 | 7953.82 | 1290030.9294
4805-Generator Bus Duct Cooling System | 7 | 7 | 1108.11 | 57295.3932
4810-Generator output breaker | 489 | 489 | 51778.19 | 3067416.1669
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 1 | 1 | 30 | 215.5
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 8 | 8 | 219 | 99657.1499
4840-Inspection E | 34 | 34 | 1799.34 | 43769.8218
4842-Reactive and capability testing | 10 | 10 | 656.89 | 14238.5501
4850-Core monitor alarm | 4 | 4 | 149 | 569.2332
4860-Generator Neutral Grounding Equipment | 24 | 24 | 3684.08 | 1058900.1604
4899-Other miscellaneous generator problems | 251 | 251 | 31334.22 | 8754370.4209
5000-Inlet air ducts A | 9 | 9 | 630.8 | 116968.1998
5001-Inlet air vanes / nozzles | 133 | 133 | 17825.94 | 392063.5103
5002-Inlet air filters A | 199 | 199 | 14080.75 | 139792.139
5003-Inlet cone | 2 | 2 | 5 | 3600
5004-Inlet air chillers B | 126 | 126 | 3168.97 | 133124.2919
5005-Inlet air evaporative coolers B | 38 | 38 | 452.65 | 18197.9579
5006-Inlet air foggers B | 35 | 35 | 1378.8 | 32645.3862
5009-Other inlet air problems A | 48 | 48 | 5038.88 | 84229.6921
5010-High pressure shaft D | 1 | 1 | 25 | 10043.75
5011-High pressure bearings C | 2 | 2 | 205 | 1560.5833
5012-High pressure blades/buckets B | 35 | 35 | 3983.5 | 1983895.1006
5013-Compressor casing and bolts | 2 | 2 | 152.5 | 818.9999
5014-Compressor diaphragms | 9 | 9 | 1575 | 154091.216
5015-Compressor seals | 3 | 3 | 124 | 56191.3167
5016-High pressure compressor bleed valves | 222 | 222 | 23901.62 | 121021.8196
5017-Low pressure compressor bleed valves | 89 | 89 | 12210.81 | 74451.5448
5019-Other high pressure problems A | 16 | 16 | 811.19 | 349098.4319
5021-Low pressure bearings D | 3 | 3 | 149 | 27246.2333
5022-Low pressure blades/buckets A | 4 | 4 | 241.28 | 760173.7333
5029-Other low pressure problems E | 4 | 4 | 428.71 | 2451.1979
5035-Compressor Washing | 1 | 1 | 47 | 245.9667
5036-Compressor shaft & bearings two sft machines | 2 | 2 | 186.5 | 49.7332
5037-Inlet bleed heat valve | 92 | 92 | 11916 | 103678.5442
5039-Other compressor problems | 211 | 211 | 14383.22 | 2019335.458
5040-Fuel tanks B | 23 | 23 | 2882.4 | 8269.8441
5041-Fuel piping and valves A | 776 | 776 | 111780.92 | 2388877.3636
5042-Fuel nozzles/vanes B | 66 | 66 | 7733.28 | 357474.3256
5043-Fuel filters A | 56 | 56 | 6257.56 | 112572.2502
5044-Liquid fuel oil pump A | 27 | 27 | 2830.4 | 42178.5642
5046-Liquid fuel oil transfer/forwarding pump B | 30 | 30 | 2613.27 | 9405.6908
5047-Liquid fuel purge system A | 39 | 39 | 5527.74 | 66605.359
5048-Gas fuel system B | 722 | 722 | 92755.9 | 1092829.1417
5049-Other fuel system problems B | 385 | 385 | 46431.11 | 581605.759
5050-Ignition system A | 353 | 353 | 49900.23 | 320568.3528
5051-Pilot fuel piping and valves A | 91 | 91 | 12246.89 | 166313.4465
5052-Pilot fuel nozzles/vanes B | 11 | 11 | 1907 | 8852.366
5053-Pilot fuel filters A | 2 | 2 | 300 | 336.6498
5054-Water Injection System (Gas Turbine) | 185 | 185 | 17558.63 | 187553.0742
5060-Atomizing air system B | 65 | 65 | 6826 | 303181.5079
5065-NOx water injection system including pumps | 136 | 136 | 11233.92 | 67883.425
5066-NOx Steam Injection System | 24 | 24 | 1771.61 | 39627.3788
5070-Combustor casing A | 25 | 25 | 3957.05 | 415745.1969
5071-Combustor liner B | 11 | 11 | 1168 | 168768.2828
5072-Combustor caps B | 8 | 8 | 1548.99 | 117406.0281
5073-Flame scanners B | 92 | 92 | 11823.46 | 77590.8287
5074-Flashback including instruments | 109 | 109 | 12541.31 | 242081.9274
5075-Blade Path Temperature Spread A | 293 | 293 | 45831.79 | 1025877.1715
5079-Other combustor problems B | 452 | 452 | 54743.39 | 781314.6812
5080-High pressure shaft C | 5 | 5 | 521.65 | 8022.724
5081-High pressure bearings D | 19 | 19 | 1498.53 | 177644.9999
5082-High pressure blades/buckets A | 27 | 27 | 3033.35 | 2460359.7258
5083-High pressure nozzles/vanes A | 19 | 19 | 2588.84 | 184652.8632
5084-High pressure casing/expansion joints | 9 | 9 | 1315.5 | 38044.8663
5085-Interstage gas passages - HP | 1 | 1 | 275 | 165
5086-High pressure shaft seals A | 6 | 6 | 407 | 45657.4499
5087-Thrust Bearing | 18 | 18 | 1712.41 | 1187693.2641
5088-Gas turbine cooling steam | 60 | 60 | 11058.04 | 373620.3099
5089-Other high pressure problems B | 19 | 19 | 2840.82 | 62909.7048
5090-Low pressure shaft A | 3 | 3 | 291.38 | 153.4945
5091-Low pressure bearings A | 11 | 11 | 1034 | 135927.3663
5092-Low pressure blades/buckets D | 6 | 6 | 921.1 | 708844.2297
5093-Low pressure nozzles/vanes B | 6 | 6 | 928.2 | 189575.153
5094-Low pressure casing/expansion joints A | 2 | 2 | 65.6 | 656.9
5095-Interstage gas passages ? LP | 2 | 2 | 316.5 | 1288.8583
5096-Low pressure shaft seals | 2 | 2 | 299.4 | 431.635
5097-Other low pressure problems B | 19 | 19 | 1894.64 | 52573.7986
5098-Expansion joints A | 13 | 13 | 1824.91 | 225108.7609
5099-HP to LP coupling | 1 | 1 | 55 | 792.9166
5100-Chamber A | 9 | 9 | 841 | 105194.7999
5102-Vanes/nozzles A | 1 | 1 | 55 | 137.5
5103-Silencer B | 6 | 6 | 328 | 3688.7933
5105-Diverter Dampers B | 19 | 19 | 825.4 | 41774.0514
5106-Exhaust Stack | 27 | 27 | 2315.09 | 36776.3958
5108-High engine exhaust temperature A | 166 | 166 | 15532.46 | 544777.5524
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 216 | 216 | 24004.18 | 981307.9498
5110-Lube oil system - general | 226 | 226 | 16281.06 | 596338.4987
5111-Lube oil pumps B | 90 | 90 | 10145.25 | 511402.2798
5112-Lube oil coolers B | 38 | 38 | 2338.2 | 39036.8842
5113-Lube oil valves/piping | 33 | 33 | 3120.39 | 56849.6463
5114-Lube oil filters | 18 | 18 | 936.03 | 8142.7676
5115-Oil vapor extractor | 18 | 18 | 1753.83 | 162403.5661
5116-Power Augmentation System Equipment B | 20 | 20 | 783.69 | 116682.6553
5117-Power augmentation piping | 9 | 9 | 468.3 | 2179.3965
5118-Power augmentation valves | 12 | 12 | 1124.5 | 12347.0416
5119-Power augmentation controls | 26 | 26 | 1323.1 | 14003.7931
5120-Hydraulic oil system A | 89 | 89 | 11434.52 | 159165.3308
5121-Hydraulic oil system pumps | 35 | 35 | 4292.12 | 72478.2408
5122-Hydraulic oil system piping/valves | 36 | 36 | 5075.25 | 259323.5327
5130-Starting system (including motor) A | 377 | 377 | 45821.05 | 833698.8849
5140-Battery and charger system B | 20 | 20 | 1378.02 | 218269.3724
5150-Turning gear and motor C | 99 | 99 | 11488.03 | 486278.7166
5151-Load gear compartment B | 13 | 13 | 337 | 21021.7332
5160-Cooling and seal air system B | 175 | 175 | 25836.39 | 323660.5342
5170-Cooling water system A | 43 | 43 | 4113.55 | 158748.0665
5180-Anti-icing system A | 13 | 13 | 2353.28 | 11595.7084
5190-Other auxiliary system problems A | 143 | 143 | 17163.46 | 309062.881
5200-Reduction gear B | 2 | 2 | 266 | 89009.0666
5201-Load shaft and bearings A | 34 | 34 | 5727.83 | 1358225.3211
5205-Main coupling between the turbine and generator A | 7 | 7 | 326 | 181938.0999
5206-Gas Turbine Clutch | 7 | 7 | 377.86 | 14249.2181
5210-Intercoolers A | 6 | 6 | 858 | 6156.9662
5240-Fire detection and extinguishing system B | 182 | 182 | 28253.62 | 459126.6501
5241-Fire in unit A | 20 | 20 | 2233.78 | 3041246.3893
5245-Gas Turbine Control System - data highway | 35 | 35 | 4276.26 | 26831.4069
5246-Gas Turbine Control System - hardware problems (including card failure) | 187 | 187 | 22295.76 | 460546.2763
5247-Gas Turbine Control System - internal and termination wiring | 31 | 31 | 4208.48 | 32073.481
5248-Gas Turbine Control System - logic problems | 142 | 142 | 14146.91 | 424197.9326
5249-Gas Turbine Control System - upgrades | 5 | 5 | 702.95 | 43801.6166
5250-Other Controls and instrumentation Problems A | 705 | 705 | 79652.78 | 952058.8783
5255-Computer | 6 | 6 | 572.5 | 3270.9414
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 29 | 29 | 2452.69 | 1049222.0321
5261-Gas turbine/compressor washing | 12 | 12 | 2130.67 | 28462.4003
5262-Gas turbine exchange | 1 | 1 | 49 | 4752.1833
5269-Combustion inspection (CI) | 9 | 9 | 1122.9 | 114894.3246
5270-Hot end inspection B | 7 | 7 | 1055 | 88230.0832
5272-Boroscope inspection A | 34 | 34 | 3472.79 | 198992.0381
5274-General unit inspection A | 15 | 15 | 1554.9 | 80634.1463
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 72 | 72 | 5909.65 | 357321.627
5285-Gas turbine vibration | 244 | 244 | 25139.03 | 1926293.1104
5286-Gas Turbine lockout cause by OEM specifications | 16 | 16 | 1289.34 | 33915.1376
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 81 | 81 | 5227.36 | 89126.0003
5292-Turbine Overspeed Trip Test - Gas Turbine | 5 | 5 | 223.5 | 2828.2582
5295-Synchronous condenser equipment A | 6 | 6 | 339 | 5673.3833
5298-Main gas filter | 5 | 5 | 3038 | 109239.0992
5299-Other miscellaneous gas turbine problems | 557 | 557 | 52124.27 | 3199194.6119
5400-Inlet air ducts B | 5 | 5 | 281.4 | 4869.4499
5401-Inlet air vanes/noozles | 9 | 9 | 456.22 | 3722.1578
5402-Inlet air filters B | 21 | 21 | 661 | 3570.7331
5404-Inlet air chillers A | 16 | 16 | 175.5 | 1477.8833
5405-Inlet air evaporative coolers A | 4 | 4 | 48 | 13481.9333
5406-Inlet air foggers A | 2 | 2 | 14 | 160.1833
5409-Other inlet air problems B | 29 | 29 | 1700.9 | 234907.7811
5410-High pressure shaft B | 1 | 1 | 102 | 824.5
5412-High pressure blades/buckets C | 9 | 9 | 409 | 374913.1498
5413-Other high pressure problems D | 11 | 11 | 684.83 | 6092.2101
5414-Compressor diaphragms/vanes | 12 | 12 | 932.3 | 48851.9214
5420-Low pressure shaft C | 2 | 2 | 228 | 4163.7998
5422-Low pressure blades/buckets C | 1 | 1 | 45 | 24007.5
5429-Other low pressure problems D | 10 | 10 | 564.45 | 320026.7207
5435-Jet Engine Compressor Washing | 2 | 2 | 89.5 | 2195.5
5439-Jet engine other compressor problems | 28 | 28 | 1441.42 | 206652.4215
5440-Fuel tanks A | 6 | 6 | 384 | 4806.5832
5441-Fuel piping and valves B | 118 | 118 | 5806.6 | 85936.7483
5442-Fuel nozzles/vanes A | 21 | 21 | 1039.8 | 21558.4145
5443-Fuel filters B | 12 | 12 | 385 | 9805.0282
5444-Liquid fuel oil pump B | 8 | 8 | 346.9 | 15526.3215
5445-Liquid fuel oil transfer/forwarding pump A | 24 | 24 | 965 | 8749.9164
5446-Liquid fuel purge system B | 6 | 6 | 243.8 | 474.5332
5447-Gas fuel system A | 125 | 125 | 7821.62 | 80866.9755
5449-Other fuel system problems A | 109 | 109 | 4670.83 | 100034.1119
5450-Ignition system B | 41 | 41 | 2269.54 | 15626.3
5451-Pilot fuel piping and valves B | 5 | 5 | 380 | 2497.1332
5452-Pilot fuel nozzles/vanes A | 1 | 1 | 194 | 33743.0666
5454-Water injection system (Jet Engine) | 92 | 92 | 4331.43 | 31147.6694
5455-Fuel nozzle/vane cooling air system | 2 | 2 | 84.5 | 1335.825
5460-Atomizing air system A | 12 | 12 | 948 | 26860.5997
5471-Combustor liner A | 1 | 1 | 48 | 11304
5472-Combustor caps A | 1 | 1 | 10 | 6
5473-Flame scanners A | 19 | 19 | 877.44 | 11137.7511
5475-Blade Path Temperature Spread B | 92 | 92 | 12334.54 | 40045.631
5479-Other combustor problems A | 46 | 46 | 2596.7 | 85881.614
5480-High pressure shaft A | 8 | 8 | 439.25 | 43268.704
5481-High pressure bearings A | 4 | 4 | 1110.2 | 51989.7404
5482-High pressure blades/buckets D | 2 | 2 | 32 | 69088.0167
5483-High pressure nozzles/vanes B | 4 | 4 | 515 | 152658.5665
5485-Interstage gas passages | 1 | 1 | 179 | 832.35
5487-Thrust Bearing/jet | 9 | 9 | 404.4 | 1452.2632
5489-Other high pressure problems C | 2 | 2 | 122 | 47713.1333
5490-Low pressure shaft B | 9 | 9 | 443.8 | 74.0566
5491-Low pressure bearings C | 8 | 8 | 655.6 | 17272.6231
5492-Low pressure blades/buckets B | 1 | 1 | 47 | 11025.4167
5493-Low pressure nozzles/vanes A | 1 | 1 | 18.25 | 423.4
5497-Other low pressure problems C | 3 | 3 | 211.7 | 208.06
5499-Shaft seals A | 5 | 5 | 232.8 | 42869.7999
5500-Chamber B | 1 | 1 | 37 | 5733.7666
5505-Diverter Dampers A | 1 | 1 | 57 | 816.05
5508-High engine exhaust temperature B | 30 | 30 | 1280.66 | 12203.5158
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 37 | 37 | 1989.54 | 19903.5071
5510-Lube oil system A | 210 | 210 | 10985.04 | 449646.7593
5516-Power Augmentation System Equipment A | 32 | 32 | 890.92 | 54782.1525
5520-Hydraulic oil system B | 41 | 41 | 2409.54 | 13831.5707
5530-Starting system (including motor) B | 63 | 63 | 3368.7 | 56660.8454
5540-Battery and charger system A | 6 | 6 | 294.22 | 3342.7745
5550-Turning gear and motor B | 12 | 12 | 1125.1 | 130879.5064
5551-Load gear compartment A | 1 | 1 | 21.63 | 306.425
5560-Cooling and seal air system A | 22 | 22 | 1040.57 | 59428.694
5570-Cooling water system B | 16 | 16 | 657.9 | 34473.8365
5580-Anti-icing system B | 22 | 22 | 1386.8 | 14373.4064
5590-Other auxiliary system problems B | 69 | 69 | 2868.04 | 404917.7991
5601-Load shaft and bearings B | 1 | 1 | 48 | 36
5605-Main coupling between the turbine and generator B | 3 | 3 | 89.8 | 17115.3133
5606-Jet Engine Clutch | 3 | 3 | 136.5 | 1530.3166
5610-Intercoolers B | 1 | 1 | 95 | 172.5833
5640-Fire detection and extinguishing system A | 49 | 49 | 2273.76 | 32354.1797
5645-Jet Engine Control System - data highway | 12 | 12 | 742.3 | 23135.1497
5646-Jet Engine Control System - hardware problems (including card failure) | 89 | 89 | 4207.2 | 80889.1333
5647-Jet Engine Control System - internal and termination wiring | 25 | 25 | 944.2 | 6678.3131
5648-Jet Engine Control System - logic problems | 23 | 23 | 1024.3 | 19452.2748
5649-Jet Engine Control System - upgrades | 14 | 14 | 1792.4 | 5486.7228
5650-Other Controls and instrumentation Problems B | 212 | 212 | 10295.68 | 194498.8141
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 3 | 3 | 158.22 | 28634.041
5661-Engine/compressor washing | 6 | 6 | 304 | 1742.4
5662-Engine exchange | 3 | 3 | 199 | 41153.5666
5665-Engine shafts and bearings | 1 | 1 | 52 | 15487.3333
5672-Boroscope inspection B | 12 | 12 | 834.21 | 6681.2831
5674-General unit inspection B | 29 | 29 | 1570.03 | 472889.0662
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 47 | 47 | 2022.1 | 17412.7944
5685-Engine vibration | 72 | 72 | 3341.73 | 1682303.4441
5686-Jet Engine lockout cause by OEM specifications | 12 | 12 | 765 | 5517.2997
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 21 | 21 | 394.7 | 90.6082
5695-Synchronous condenser equipment B | 1 | 1 | 100 | 486.6666
5699-Other miscellaneous jet engine problems | 79 | 79 | 3195.56 | 232317.096
5710-Cylinders | 29 | 29 | 401.36 | 15590.1589
5711-Cylinder heads | 19 | 19 | 326.2 | 3718.5712
5720-Pistons | 39 | 39 | 1449.56 | 16798.3521
5730-Intake valves | 4 | 4 | 58.6 | 3601.1217
5731-Exhaust valves | 14 | 14 | 123.5 | 3108.9
5734-exhaust gas bellow | 4 | 4 | 56.2 | 1716.975
5735-main starting air valve | 3 | 3 | 48.5 | 109.0833
5740-Turbo charger | 8 | 8 | 180.93 | 2698.628
5756-starting air distributer | 2 | 2 | 22.04 | 33.3533
5758-charge air cooler | 2 | 2 | 22.08 | 620.632
5759-waste gate | 3 | 3 | 34.12 | 723.2093
5799-Other engine problems | 117 | 117 | 2580.75 | 41933.4772
5800-Lube oil system C | 16 | 16 | 350.61 | 10683.0128
5805-Cooling system | 40 | 40 | 679.14 | 41203.5596
5815-Fuel system | 15 | 15 | 297.96 | 2856.7699
5820-Start system | 29 | 29 | 499.91 | 5136.0824
5830-Air filter system | 1 | 1 | 226 | 128.0665
5831-Exhaust gas rapture disc | 6 | 6 | 102 | 866.2167
5849-Other engine auxiliaries problems | 10 | 10 | 151.92 | 7084.952
5850-Governor | 1 | 1 | 17 | 5.3833
5855-Engine control system | 20 | 20 | 314.87 | 2884.8761
5865-Synchronization system | 1 | 1 | 18.72 | 16.848
5870-Other engine control problems | 40 | 40 | 816.75 | 8228.17
5873-Gas admission valve | 3 | 3 | 94.5 | 2020.75
5874-Exhaust gas temp sensor | 2 | 2 | 38 | 595.9667
5895-Inspection C | 1 | 1 | 11.04 | 57.592
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 14 | 14 | 291.08 | 8106.5672
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 19 | 19 | 2720.55 | 105990.3501
6005-HP Evaporator tubes | 30 | 30 | 5037.48 | 859692.0432
6006-IP Evaporator tubes | 5 | 5 | 577.6 | 31515.8999
6007-LP Evaporator tubes | 18 | 18 | 2539.99 | 209334.8948
6010-HP superheater | 31 | 31 | 5240.35 | 574638.5411
6011-HP reheater | 5 | 5 | 541.31 | 39126.2608
6012-HP economizer | 38 | 38 | 4063 | 217467.9871
6020-IP superheater | 11 | 11 | 1977.2 | 129925.2044
6021-IP reheater | 12 | 12 | 1957.9 | 289538.0475
6022-IP economizer | 6 | 6 | 860 | 29965.9997
6030-LP reheater | 2 | 2 | 258 | 19092
6032-LP economizer | 9 | 9 | 1391.4 | 54652.1596
6090-Other HRSG tube Problems | 52 | 52 | 4342.3 | 390874.0389
6100-Steam turbine to gas turbine coupling. For additional codes; use Fossil Steam Cause Codes 4000 to 4499. | 1 | 1 | 266 | 421.1666
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 7 | 7 | 2045.86 | 50874.0374
6111-HP steam relief/safety valves | 2 | 2 | 190 | 7472.6
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 30 | 30 | 5504.82 | 101444.8163
6113-Other HP steam system problems | 31 | 31 | 5938.16 | 31504.0344
6114-HP steam isolation/boundary valves | 33 | 33 | 7508.78 | 83133.1403
6121-IP steam relief/safety valves | 6 | 6 | 673.5 | 2621.7166
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 13 | 13 | 3791.78 | 14631.651
6123-Other IP steam system problems | 13 | 13 | 2054.5 | 7001.1489
6124-IP steam isolation/boundary valves | 9 | 9 | 1434.7 | 8514.3428
6131-LP steam relief/safety valves | 1 | 1 | 194.8 | 4986.88
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 7 | 7 | 706.04 | 15680.659
6133-Other LP steam system problems | 9 | 9 | 1297.58 | 5835.2536
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 7 | 7 | 1376.5 | 4446.7497
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 16 | 16 | 3863.33 | 60006.5355
6141-HP Desuperheater/attemperator valves | 46 | 46 | 8294.76 | 77033.4085
6142-HP Desuperheater/attemperator spray nozzles | 8 | 8 | 1867.38 | 18279.1664
6144-Other HP desuperheater/attemperator problems | 12 | 12 | 2446.5 | 31930.7241
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 5 | 5 | 710.9 | 67966.2765
6146-IP Desuperheater/attemperator valves | 10 | 10 | 1772 | 19365.6828
6147-IP Desuperheater/attemperator spray nozzles | 2 | 2 | 167 | 77.9332
6148-IP Desuperheater/attemperator drums | 1 | 1 | 133 | 39.9
6149-Other IP desuperheater/attemperator problems | 19 | 19 | 2912.78 | 50410.9133
6150-LP Desuperheater/attemperator piping - Less than 200 PSIG | 1 | 1 | 0 | 0
6152-LP Desuperheater/attemperator spray nozzles | 2 | 2 | 379 | 1654.9664
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 16 | 16 | 4740.63 | 139398.6261
6161-HP Startup bypass system valves | 66 | 66 | 15014.96 | 574496.9419
6163-Other HP startup bypass system problems | 6 | 6 | 1057 | 1703.9332
6164-HP Startup bypass instrumentation and controls | 21 | 21 | 3038.65 | 37943.8813
6171-IP Startup bypass system valves | 30 | 30 | 6266.88 | 128503.6341
6173-Other IP startup bypass system problems | 1 | 1 | 158 | 508.2332
6174-IP Startup bypass instrumentation and controls | 10 | 10 | 1965.9 | 178290.4781
6181-LP Startup bypass system valves | 3 | 3 | 574 | 18548.2831
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 68 | 68 | 10891.02 | 122359.0317
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 23 | 23 | 3261.81 | 30748.664
6399-Other coal gasification equipment problems | 204 | 204 | 25972.03 | 1057263.2426
6410-Steam wells/steam field piping problems | 50 | 50 | 597.1 | 15948.2831
6415-Low steam pressure | 1 | 1 | 39 | 13
6420-Condensate reinjection system | 4 | 4 | 25.5 | 229
6440-H2S abatement system problems ? general | 7 | 7 | 320 | 9072.3666
6460-Condenser problems due to H2S abatement system | 1 | 1 | 30 | 50
6499-Geothermal | 11 | 11 | 166.5 | 1019.9999
7000-Shaft B | 16 | 16 | 1401.85 | 1288511.4632
7001-Shaft packing | 27 | 27 | 2296.94 | 168383.1313
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 32 | 32 | 2902.12 | 357588.0596
7007-Bearings A | 31 | 31 | 4016.42 | 530998.9309
7008-Bearing cooling system B | 32 | 32 | 2176.41 | 116475.2262
7009-Bearing Oil System | 61 | 61 | 5298 | 368068.8496
7010-Runner cavitation damage | 3 | 3 | 4.7 | 4858.9067
7011-Other runner problems | 23 | 23 | 1729.26 | 576573.5956
7012-Casing; wear ring; or liner cavitation damage | 3 | 3 | 153 | 106629.4167
7020-Nozzle assembly | 12 | 12 | 396.19 | 6402.5709
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 42 | 42 | 3729.1 | 98097.7392
7040-Turbine overhaul | 2 | 2 | 217.4 | 58.03
7050-Turbine governor | 188 | 188 | 16449.47 | 576182.8902
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 43 | 43 | 5447.38 | 60371.6609
7053-Governor Oil System | 83 | 83 | 5907.11 | 441345.8779
7070-Speed Increaser | 5 | 5 | 114.07 | 1804.4368
7099-Other turbine problems | 59 | 59 | 6420.48 | 518963.4324
7100-Upper reservoir dams and dikes | 25 | 25 | 1829.4 | 34314.3959
7101-Lower reservoir dams and dikes | 35 | 35 | 3302.2 | 14377.0733
7110-Intake channel or flume (including trash racks) | 138 | 138 | 6708.66 | 451186.3624
7111-Intake tunnel | 11 | 11 | 669.77 | 15216.9859
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 3 | 3 | 41.95 | 8259.7958
7120-Headgates | 51 | 51 | 869.66 | 174567.7128
7121-Shutoff valves | 19 | 19 | 4007.66 | 520789.2609
7123-Shutoff valve bypass line and valve | 13 | 13 | 1234.21 | 29510.0968
7124-Penstock | 23 | 23 | 1514.44 | 15140.4
7130-Spiral case | 2 | 2 | 559.75 | 40254.2498
7140-Wicket gate assembly | 18 | 18 | 1298.04 | 181174.7275
7141-Wicket gate operating mechanism or positioner | 23 | 23 | 3624.85 | 106070.1359
7142-Wicket gate shear pin | 116 | 116 | 6213.27 | 126834.4997
7160-Pressure regulating valve | 13 | 13 | 561.3 | 214027.3271
7161-Pressure regulating valve operator or positioner | 1 | 1 | 45 | 210.75
7162-Relief valve and vacuum breakers | 7 | 7 | 624 | 17682.0082
7170-Draft tube | 6 | 6 | 445 | 4283.5249
7180-Tailrace | 11 | 11 | 319.2 | 6745.4699
7181-Tail water depressing equipment | 3 | 3 | 401 | 440.6831
7190-Dewatering and rewatering equipment | 10 | 10 | 799.66 | 4529.1575
7191-Equalizing line | 1 | 1 | 140 | 156.3332
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 112 | 112 | 4434.09 | 256754.4994
7201-Inspection A | 3 | 3 | 50.2 | 417.2333
7210-Canals (including siphons; radial gates; and spills) | 2 | 2 | 274.56 | 1438.2452
7220-Unit out of service due to common penstock with unit under repair | 2 | 2 | 55.34 | 70.0973
7230-Pony motor (pumped storage units only) | 3 | 3 | 512.43 | 2135.8362
7240-Powerhouse Substructure | 1 | 1 | 292 | 1070.6665
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 19 | 19 | 1764.98 | 57242.6603
7300-Routine Hydro Planned Outage (reoccuring schedule) | 4 | 4 | 152 | 67538.1333
7800-Couplings | 1 | 1 | 23 | 6154.4167
7810-Shaft A | 2 | 2 | 170 | 92760.4999
7820-Bearings B | 10 | 10 | 389.5 | 184408.1049
7830-Blades | 7 | 7 | 289.99 | 282498.4725
7860-Nozzles/vanes | 1 | 1 | 71 | 1260.25
7870-Heat shields B | 1 | 1 | 25 | 18.75
7880-Exhaust diffusers | 1 | 1 | 36 | 65587.2
7890-Seal oil system and seals B | 1 | 1 | 28 | 132941.6666
7920-Lube oil system B | 11 | 11 | 546.8 | 124986.3131
7930-Controls and instrumentation A | 22 | 22 | 1752.55 | 15962.0436
7960-Other expander turbine problems | 4 | 4 | 214 | 48780.5333
8000-Chemical feed storage; mill feeders; and conveyors | 1 | 1 | 234 | 3728.3999
8002-Screw conveyors | 2 | 2 | 101.77 | 201.5889
8010-Crushers/mills | 17 | 17 | 4203.99 | 32859.493
8020-Mill slurry tanks supply problems | 14 | 14 | 3473.3 | 11971.3424
8040-Slurry transfer pumps and motors | 6 | 6 | 1873 | 17136.366
8050-Chemical unavailability | 18 | 18 | 1599 | 26324.8495
8099-Other chemical supply problems | 12 | 12 | 1279.15 | 13555.3153
8100-Scrubber/absorber tower or module | 154 | 154 | 18742.11 | 625996.7603
8110-Spray nozzles | 11 | 11 | 2751 | 144161.2655
8120-Spray pumps and motors | 11 | 11 | 1222.81 | 23769.7838
8125-Scrubber recycle (liquid) pumps | 17 | 17 | 3552.25 | 129061.4497
8127-Scrubber recycle (liquid) pump motors | 6 | 6 | 1163.42 | 10827.8861
8130-Recirculation tanks including agitators | 2 | 2 | 254 | 59023.5833
8140-Reaction tanks including agitators | 1 | 1 | 213.24 | 4570.4439
8160-Mist eliminators/demisters and washdown | 39 | 39 | 4288.83 | 161607.2601
8199-Other scrubber problems | 65 | 65 | 10763.04 | 246043.3592
8200-Piping | 16 | 16 | 3909.12 | 240021.0347
8210-Valves | 7 | 7 | 759.79 | 14076.0514
8230-Ducting | 6 | 6 | 2976 | 652774.699
8235-Demister | 9 | 9 | 243 | 135.8999
8240-Bypass dampers | 2 | 2 | 1070 | 3008.2326
8250-Dampers other than bypass | 2 | 2 | 346 | 11093.4664
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 22 | 22 | 5090.37 | 706865.9352
8261-Scrubber booster I.D. fan drive | 1 | 1 | 31 | 502.7166
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 12 | 12 | 1683.9 | 13358.946
8264-Scrubber booster I.D. fan blades (fan specific to the scrubber) | 2 | 2 | 90.24 | 5501.83
8265-Scrubber ID fan dampers | 9 | 9 | 3107 | 48557.249
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 5 | 5 | 406.17 | 3236.0455
8271-Scrubber booster F.D. fan drive | 2 | 2 | 594 | 3837.1664
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 2 | 2 | 213 | 36331.2166
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 1 | 1 | 378 | 32029.1999
8275-Scrubber FD fan dampers | 1 | 1 | 427 | 960.75
8280-Reagent feed piping | 4 | 4 | 675.8 | 11405.2233
8290-Demister wash piping assembly | 1 | 1 | 207 | 2542.6499
8299-Other piping; ducting; damper; and fan problems | 6 | 6 | 793.1 | 7031.0332
8300-Waste disposal/recovery tanks | 12 | 12 | 5335 | 135984.9317
8310-Waste disposal/recovery pumps | 2 | 2 | 420 | 2859.7998
8330-Dewatering equipment (thickener; centrifuge; etc.) | 14 | 14 | 4910.94 | 529040.2034
8340-Centrifuge/vacuum filter | 1 | 1 | 107 | 756.1333
8349-Other waste disposal and recovery problems | 3 | 3 | 911 | 70140.3831
8399-Solids conveying and mixing system problems | 3 | 3 | 2081 | 66991.2498
8400-Scrubber gas discharge reheaters - general | 1 | 1 | 80.01 | 394.716
8404-Scrubber gas discharge reheaters - tube leaks | 2 | 2 | 390 | 2368.1666
8406-Scrubber gas discharge reheaters - ducts | 1 | 1 | 393 | 307.8499
8410-Scrubber instruments and controls | 9 | 9 | 1038 | 13852.0995
8415-Liquid level controls | 9 | 9 | 1212 | 53166.2024
8426-Miscellaneous electrical failures | 3 | 3 | 606 | 11008.5332
8430-Stack damage related to scrubber system | 1 | 1 | 595 | 474512.5
8450-Inspection | 1 | 1 | 280 | 1227.3332
8499-Other miscellaneous wet scrubber problems | 37 | 37 | 6515.2 | 123114.9518
8500-Slurry storage and feed tanks | 7 | 7 | 1524.4 | 15955.4663
8501-Reagent storage; feed bins; and conveyors | 8 | 8 | 1815 | 37474.1659
8502-Weigh feeders | 1 | 1 | 315 | 845.2499
8503-Screw conveyors | 9 | 9 | 654 | 1876.3999
8504-Mills/slakers | 1 | 1 | 75 | 62.5
8506-Slurry pipelines | 7 | 7 | 1012.36 | 18532.023
8507-Reagent uploading and transfer systems | 3 | 3 | 896 | 18861.8998
8508-Reagent unavailability | 7 | 7 | 1099 | 26492.5331
8510-Slurry mixers and agitators | 13 | 13 | 784 | 34538.9164
8520-Slurry transfer pumps and motors | 6 | 6 | 825.5 | 6047.7998
8521-Reagent/slurry problems | 19 | 19 | 3940 | 57799.2489
8522-Piping | 3 | 3 | 805 | 13255.3331
8523-Valves | 3 | 3 | 435.8 | 1177.3164
8525-Ducting | 4 | 4 | 773 | 26271.4163
8526-Dampers | 1 | 1 | 250 | 941.6665
8528-Dry scrubber instruments and controls | 7 | 7 | 1215 | 16368.7495
8529-Gas dispersers | 10 | 10 | 852 | 16159.4996
8530-Spray towers | 127 | 127 | 4666.9 | 143481.1003
8531-Spray machine/atomizer | 97 | 97 | 18579.06 | 241777.8406
8532-Spray machine/atomizer motors | 3 | 3 | 704.2 | 12187.0862
8533-Spray machine/atomizer lubrication systems | 8 | 8 | 1390.5 | 4703.4664
8534-Spray machine/atomizer vibration problems | 39 | 39 | 2368 | 28138.6327
8535-Fly ash conveyors | 14 | 14 | 656.49 | 29662.3148
8538-Recycle storage and feed tanks including agitators | 8 | 8 | 2036 | 37905.8993
8539-Recycle slurry transfer pumps | 1 | 1 | 406 | 5623.1
8540-Waste disposal | 1 | 1 | 220 | 5463.3333
8542-Recycle feed bins aeration systems | 1 | 1 | 254 | 1447.8
8544-Mechanical failures | 12 | 12 | 2880 | 13754.2825
8545-Electrical failures | 8 | 8 | 778.5 | 15418.6331
8547-Inspection | 3 | 3 | 377 | 3382.0499
8549-Other dry scrubber problems | 25 | 25 | 3010 | 142343.6327
8550-Electrostatic precipitator fouling | 43 | 43 | 2027.2 | 24836.1211
8551-Electrostatic precipitator field out of service | 47 | 47 | 7575.38 | 261977.9905
8560-Electrostatic precipitator problems | 68 | 68 | 6894.76 | 212549.1398
8570-Mechanical precipitator fouling | 4 | 4 | 370 | 40506
8580-Mechanical precipitator problems | 5 | 5 | 770 | 25264.9998
8590-Other precipitator problems | 49 | 49 | 4708.52 | 149580.1876
8600-Flue gas additives (furnace injection) | 1 | 1 | 403 | 839.5832
8601-SO3 mitigation | 10 | 10 | 2328.2 | 14474.7458
8620-Mercury Abatement | 33 | 33 | 5163 | 1385288.08
8650-Baghouse systems; general | 416 | 416 | 25215.04 | 1719597.9403
8651-Bag failures and rebagging | 183 | 183 | 9055.12 | 319156.3643
8652-Shakers and rappers | 1 | 1 | 48 | 121.6
8653-Inflation and deflation fans and motors | 91 | 91 | 2944 | 48108.1823
8654-Baghouse booster fans and motors | 53 | 53 | 5739 | 190264.9318
8655-Structural duct work and dampers | 4 | 4 | 292 | 36317.2165
8656-Controls and instrumentation B | 72 | 72 | 6214.42 | 110782.8035
8657-Ash handling system and hoppers | 77 | 77 | 8019.1 | 290934.7585
8658-Slurry system from precipitators | 2 | 2 | 778 | 16508.0664
8670-Emission monitors (other than CEMS) A | 3 | 3 | 510.1 | 117285.5264
8699-Other miscellaneous pollution control equipment problems | 60 | 60 | 8084.2 | 338585.679
8700-CEMS Certification and Recertification | 25 | 25 | 2012.04 | 5562.0951
8710-SO2 analyzer problems | 6 | 6 | 700 | 3749.6498
8720-NOx analyzer problems | 65 | 65 | 5420.15 | 64587.725
8730-CO analyzer problems | 24 | 24 | 2718.23 | 285178.0052
8740-CO2 analyzer problems | 2 | 2 | 144.2 | 583.4366
8750-O2 analyzer problems | 14 | 14 | 1379.7 | 12160.006
8760-Opacity monitor problems | 15 | 15 | 3208 | 17349.0493
8770-Flow monitor problems | 14 | 14 | 941.6 | 9112.5348
8780-Data acquisition system problems | 10 | 10 | 1132.7 | 65976.5299
8790-Miscellaneous CEMS problems | 173 | 173 | 13114.78 | 245338.7683
8800-SNCR NOx Reagent | 3 | 3 | 135 | 780.75
8801-SNCR NOx Carrier gas | 1 | 1 | 21 | 89.6
8802-SNCR NOx Control system | 20 | 20 | 1411.52 | 13817.4491
8803-Sncr Performance Testing | 1 | 1 | 36.1 | 21.66
8809-Other SNCR NOx problems | 22 | 22 | 1460.24 | 17032.8534
8810-SCR NOx Reactor | 1 | 1 | 22 | 528
8811-SCR NOx Reagent | 4 | 4 | 684.9 | 1388.0995
8812-SCR NOxCatalyst | 38 | 38 | 2209.56 | 495785.9982
8813-SCR NOx Injection grid piping/valves | 19 | 19 | 984.8 | 12692.7964
8814-SCR NOx Catalyst support material | 7 | 7 | 385 | 15904.8332
8815-SCR NOx Soot blowers | 5 | 5 | 2897.4 | 88426.2895
8816-SCR NOx Plugging | 182 | 182 | 34079.76 | 2023059.3608
8817-SCR NOx Control system | 58 | 58 | 6771.29 | 90377.3599
8820-SCR NOx Ammonia injection grid piping/valves | 52 | 52 | 6063.23 | 39606.3472
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 38 | 38 | 7757.46 | 68971.5224
8822-SCR NOx Ammonia air blowers | 40 | 40 | 4137.81 | 34146.9599
8823-SCR NOx Other ammonia system problems | 115 | 115 | 11625.37 | 189907.7735
8825-Other SCR NOx problems | 70 | 70 | 7888.21 | 69645.6242
8831-CAH NOx Support materials | 2 | 2 | 375 | 2090.2
8840-CO Active catalyst | 34 | 34 | 809.69 | 39657.0053
8841-CO Support materials | 2 | 2 | 303 | 2302.8
8842-CO Plugging | 39 | 39 | 3424.1 | 140114.184
8845-Other CO reduction problems | 126 | 126 | 10674.7 | 117007.6263
9000-Flood | 20 | 20 | 1823.15 | 36409.8784
9001-Drought | 4 | 4 | 1891.5 | 233078.9498
9010-Fire; not related to a specific component | 18 | 18 | 1432.26 | 527247.2076
9015-Pandemic | 2 | 2 | 831 | 26461.5
9020-Lightning | 147 | 147 | 25220.56 | 671549.0486
9030-Earthquake | 6 | 6 | 801 | 1945.2163
9031-Tornado | 5 | 5 | 816 | 52419.9832
9035-Hurricane | 28 | 28 | 4004.48 | 1016109.5651
9036-Storms (ice; snow; etc) | 233 | 233 | 21428.31 | 656365.853
9040-Other catastrophe | 13 | 13 | 3232.44 | 685091.1431
9110-Core coastdown (nuclear) | 6 | 6 | 458.29 | 125426.8297
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 665 | 665 | 89505.23 | 6333729.5277
9131-Lack of fuel: Contract or Tariff allows for interruption | 576 | 576 | 71591.63 | 2372246.5428
9132-Wet Fuel - Biomass | 250 | 250 | 1779.65 | 10409.8771
9134-Fuel conservation | 56 | 56 | 6706.5 | 205131.0979
9135-Lack of water (hydro) | 2494 | 2494 | 48385.74 | 2349701.5794
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 4 | 4 | 258.1 | 4458.4766
9137-Ground water or other water supply problems | 82 | 82 | 11035.3 | 78402.1681
9138-High Water Level in Tailrace (too much water) | 120 | 120 | 1247.81 | 75305.6603
9140-Plant modifications to burn different fuel (not regulatory mandated) | 17 | 17 | 1008 | 39267.2996
9160-Other economic problems | 14 | 14 | 1718 | 477891.326
9180-Economic (for internal use at plants only) | 2 | 2 | 75.47 | 12383.8355
9181-Economic (for internal use at plants only) | 6 | 6 | 2556 | 7076.9323
9182-Economic (for internal use at plants only) | 32 | 32 | 13536 | 26407.129
9191-Economic (for internal use at plants only) | 1 | 1 | 162 | 3817.7999
9200-High ash content | 238 | 238 | 6337.28 | 141437.0641
9201-High ash content ? (not outside management control) | 2 | 2 | 12 | 364.2
9205-Poor quality natural gas fuel; low heat content | 59 | 59 | 1176.97 | 16836.7219
9210-Low grindability | 13 | 13 | 390 | 13929.4999
9211-Low grindability (not outside management control) | 1 | 1 | 135 | 278.9999
9220-High sulfur content | 36 | 36 | 11522.34 | 249985.8441
9221-High sulfur content ? (not outside management control) | 33 | 33 | 9811.5 | 387578.4723
9240-High sodium content | 1 | 1 | 50 | 208.3333
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 369 | 369 | 10852.55 | 284198.3023
9251-Low Btu Coal From Contract For Low Btu Coal | 149 | 149 | 5480.16 | 255909.8682
9270-Wet coal | 446 | 446 | 55884.65 | 1612102.3839
9271-Wet coal (not outside management control) | 642 | 642 | 53211.87 | 1020483.1251
9272-Wet Fuel (other than coal) | 1 | 1 | 76.8 | 1186.56
9280-Frozen coal | 30 | 30 | 7090.51 | 181681.6388
9281-Frozen coal (not outside management control) | 4 | 4 | 375.9 | 1689.0319
9290-Other fuel quality problems | 599 | 599 | 38382.06 | 762912.4808
9291-Other fuel quality problems (not outside management control) | 133 | 133 | 6515.76 | 68634.2943
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 901 | 901 | 94216.99 | 5765570.6555
9305-Ash disposal problem | 4 | 4 | 525.3 | 4898.7998
9320-Other miscellaneous external problems | 592 | 592 | 51258.53 | 2961346.1279
9340-Synchronous Condenser Operation | 1 | 1 | 28 | 448
9350-Public Safety/River Rescue | 13 | 13 | 795.75 | 13506.933
9506-Regulatory (environmental) proceedings and hearings - intervenor initiated | 21 | 21 | 1848 | 453438.1659
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 8 | 8 | 5380.2 | 222083.2179
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 30 | 30 | 2504.23 | 111266.8641
9600-SO2 stack emissions (fossil) | 292 | 292 | 50667.6 | 559113.2693
9610-NOx stack emissions (fossil) | 35 | 35 | 5670.34 | 174875.2569
9613-NOx stack emissions (gas turbine) | 245 | 245 | 14586.62 | 469958.8805
9614-NOx stack emissions (jet engines) | 14 | 14 | 633.5 | 595.6915
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 5 | 5 | 72.7 | 2973.7366
9616-CO stack emissions | 123 | 123 | 7889.06 | 130529.4786
9620-Particulate stack emissions (fossil) | 73 | 73 | 9062.1 | 596402.933
9623-Particulate stack emissions (gas turbine) | 3 | 3 | 252 | 4295.6999
9630-Opacity (fossil) | 814 | 814 | 91798.43 | 4375212.3491
9650-Other stack or exhaust emissions (fossil) | 41 | 41 | 3750.8 | 276622.2848
9653-Other stack or exhaust emissions (gas turbine) | 19 | 19 | 2490.76 | 39748.3062
9654-Other stack or exhaust emissions (jet engines) | 4 | 4 | 134 | 260.8999
9656-Other stack or exhaust emissions testing - fossil | 16 | 16 | 1949.35 | 226381.223
9657-Other stack or exhaust emissions testing - gas turbine | 7 | 7 | 904.59 | 20803.994
9658-Other stack or exhaust emissions testing - jet engines | 1 | 1 | 10 | 70
9660-Thermal discharge limits (fossil and nuclear) | 87 | 87 | 7111.73 | 275455.7194
9663-Thermal discharge limits (gas turbine) | 9 | 9 | 261.41 | 21303.8332
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 76 | 76 | 3740.16 | 287047.7757
9693-Other miscellaneous operational environmental limits (gas turbines) | 38 | 38 | 2513.46 | 586616.0986
9694-Other miscellaneous operational environmental limits (jet engines) | 16 | 16 | 1349.41 | 5640.3005
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 1 | 1 | 56.04 | 24.284
9696-Other miscellaneous operational environmental limits (hydro and PS) | 139 | 139 | 6089.43 | 559267.883
9700-OSHA-related retrofit or inspection | 1 | 1 | 88 | 242
9720-Other safety problems | 59 | 59 | 6747.58 | 1968220.7554
9900-Operator error | 360 | 360 | 84156.88 | 1299214.063
9910-Maintenance personnel error | 76 | 76 | 12771.81 | 224955.201
9920-Contractor error | 50 | 50 | 8976.66 | 164188.9417
9930-Operating procedure error | 45 | 45 | 9728.42 | 73903.2042
9940-Maintenance procdure error | 16 | 16 | 1913.75 | 1434.2479
9950-Contractor procedure error | 7 | 7 | 1165.37 | 34765.3865
9960-Staff shortage | 83 | 83 | 10151.91 | 288263.2804
9997-NERC Reliability Standards requirements | 10 | 10 | 1010.1 | 24893.7163
9998-Black Start testing | 3 | 3 | 202 | 1146.3332
9999-Total unit performance testing (use appropriate codes for individual component testing) | 189 | 189 | 5037.07 | 7714966.5698
Total Result | 63701 | 63701 | 7917548.81 | 431562894.1964

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0010 | Thaw shed failure or fire | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.3 | 3.3 | 1 | 1 | 0010-Thaw shed failure or fire | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2257.5 | 90 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.09 | 64.2 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9905.3331 | 380 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.31 | 87.8 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 91 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 191.5333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 119492 | 30 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 295.5 | 30 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 1285 | 30 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Summer | 120090 | 30 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 11.8 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 20.4 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 54.6 | 26 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 10.3 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 16.1 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1020 | 300 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 10.6333 | 11 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4.5 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 77.7 | 21 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 9.3333 | 7 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 13.8 | 6 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 26.95 | 11 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 476.325 | 328.5 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 718.3333 | 100 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34287.2799 | 139.2 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4504.6666 | 290 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 228.6667 | 20 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 781.083 | 455 | 1 | 1 | 0028-Dust collection system | U2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.6667 | 20 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.3333 | 20 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 67.6666 | 290 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24658.5 | 510 | 1 | 1 | 0028-Dust collection system | SF-Startup Failure | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149293.083 | 455 | 1 | 1 | 0028-Dust collection system | U2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 560 | 320 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.9167 | 5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 363.0633 | 29.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2330.3549 | 303.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3562.1666 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 33.9166 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 80 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.1 | 7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1336.95 | 297.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5230.3331 | 284 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 22.62 | 11.6 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 71.7653 | 37.12 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4844.2666 | 62 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16136.0833 | 145 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.3333 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1048.6666 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13650 | 420 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.2498 | 231 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 347.7 | 18.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 700 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 831.25 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6849.9996 | 600 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38790.4583 | 57.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 8.3692 | 9.13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 107.1 | 21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1.449 | 9.66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12279.3333 | 163 | 2 | 2 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136834.4998 | 495 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1567.4998 | 225 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55803.4162 | 677.5 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 38.78 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 430.0999 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1909 | 332 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43 | 21.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 829.3333 | 62.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1345.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1836.8165 | 473 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8570.2666 | 323 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3038 | 196 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7324.7999 | 144 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9843.75 | 315 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2.037 | 1.94 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 541.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1787.5 | 286 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 268.8666 | 37 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 901.5832 | 155 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2572.2665 | 371 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.5 | 135 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2499.9997 | 750 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3011.4831 | 357.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6012.5 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8400.9997 | 465 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10358.3332 | 550 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16027.433 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1529.03 | 64.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1604.1665 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.25 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 349.14 | 9.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1190.383 | 473 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1239 | 413 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2192.9163 | 475 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 40.064 | 12.52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.95 | 43 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2294.9332 | 331 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 831 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 610.9133 | 74.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2317 | 84 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1209.9996 | 600 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2065.8332 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2372.5 | 650 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78319.9999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 185.1563 | 24.47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1410 | 235 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1777.7044 | 206.31 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1024.9 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.8 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.13 | 91.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1013.3665 | 602 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1120.29 | 64.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9073 | 422 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47.2 | 59 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 936.225 | 328.5 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2173.2198 | 490.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3047 | 277 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 464.12 | 116.03 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 51.765 | 17.85 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.15 | 23 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1190.4 | 496 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1269.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 340 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1596.85 | 109 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2103.9666 | 127 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 408.24 | 170.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 833.34 | 245.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2260.2665 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7492.5 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2322.4999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1989.4666 | 344 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 552 | 276 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1913.333 | 560 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39544.75 | 413 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2125 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2499.6399 | 262.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3189.6997 | 501 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4716.2498 | 231 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.4 | 48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.8 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.8333 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2650.5 | 171 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6677.4 | 372 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 5977.66 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 908.56 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24633.3332 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 991.4999 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4719.8799 | 224.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9212.5 | 670 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 343.4999 | 90 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5125 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1349.0532 | 144.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1358.3333 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6031.6665 | 470 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 43.6983 | 16.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23852.1331 | 619 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 908.9998 | 270 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 947 | 94.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3803.25 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4127.15 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 552.5 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1242.9332 | 236 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2320.8497 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1545 | 309 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 739.7332 | 152 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1369.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7430.0833 | 163 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9266 | 123 | 2 | 2 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 2210.46 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 164.9 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 183.5 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 756.6 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1035 | 450 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.48 | 65.4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 621.5 | 226 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 679.3133 | 117.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 816.2833 | 227.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2134 | 388 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7607.4165 | 473 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.6667 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 689.3333 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1022.9332 | 224 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2377.47 | 490.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8053.7499 | 255 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8082.75 | 195 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 651.9333 | 127 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 477.3333 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1383.1998 | 228 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 642.8331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 670 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 975.8666 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39832 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 116.4166 | 55 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.75 | 209 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.1 | 67 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 560 | 280 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4275.5 | 503 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19200 | 600 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 155 | 31 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 663 | 39 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1700 | 340 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1186.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 238 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63.35 | 4.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.6 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1750.3 | 138 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5054.9999 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16444.633 | 473 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 720.13 | 313.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1790.2165 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 421.2 | 312 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 779.1 | 159 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 254.5833 | 65 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5156.8 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 434.3165 | 253 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 173.3333 | 52 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305 | 76.25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3615 | 482 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23114.2331 | 413 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 708.55 | 383 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 372.4 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8079.4999 | 330 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 618.6332 | 277 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 561.0666 | 128 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.5833 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45693.9732 | 354.4 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1238.12 | 119.05 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23282.1331 | 416 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.3375 | 24.89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.7833 | 167.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 716.0999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725.3833 | 71 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 771.47 | 64.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1055.5999 | 348 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1544.6664 | 331 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3183.333 | 500 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7414.4165 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 276.45 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1359.9996 | 600 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6797.6 | 87 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3001.5 | 345 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1897.3998 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 703.58 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2276.5 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 632.0833 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1293.4166 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 30 | 30 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 542.5 | 175 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3252.8331 | 290 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 3778.8333 | 79 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 5512 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 231.8333 | 130 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2214.9999 | 150 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2614.5166 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 159.6667 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 4278.3333 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 4008.3332 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1453.6666 | 89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 5.85 | 9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 260.55 | 579 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2933 | 419 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 22108.75 | 769 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 632.15 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 109.8 | 244 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 173.8332 | 149 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4825.2999 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1515.3666 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1969.3 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 191.4 | 319 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 879.9 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 36399.3331 | 769 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2032.15 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 466.2666 | 269 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 918.1831 | 619 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2653.6665 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 577.5832 | 239 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1571.25 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 281.6666 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 781.65 | 579 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2022 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 35 | 14 | 1 | 2 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 215.2499 | 369 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 23736.4662 | 769 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 174.6333 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 434.25 | 579 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1012.5831 | 419 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2199.6 | 234 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 85.5833 | 79 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1113.2499 | 219 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2195.6999 | 234 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 649.45 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4273.4999 | 198 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1308.9999 | 224.4 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 950.2498 | 315 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1973.9999 | 180 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1188 | 110 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0050 | Coal storage fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 785.1667 | 35 | 1 | 1 | 0050-Coal storage fires | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 461 | 60 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14.3333 | 4 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2437.7332 | 376 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6994.6666 | 160 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 139.15 | 69 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 950.3 | 221 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2093.5499 | 153 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 82 | 41 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 130 | 200 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300.5333 | 196 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3379.8999 | 219 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 849 | 212.25 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 919 | 229.75 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 303.1665 | 214 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 230.2667 | 44 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345.5 | 6 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 84.8 | 212 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186.3 | 69 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2250 | 90 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 489.6 | 272 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 231.9331 | 284 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 455.26 | 267.8 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 885.3999 | 114 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3264.4166 | 215 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.3333 | 10 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 840.1166 | 133 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 341.6666 | 100 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.7 | 23 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 440.1666 | 139 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 156 | 60 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30975 | 420 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1160 | 20 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3288.5831 | 335 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1854.9997 | 420 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 232.2 | 86 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12033 | 382 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5106.6666 | 80 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 39.6 | 36 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 262.1666 | 55 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 916 | 60 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 332.75 | 121 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1406 | 296 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 82.4 | 16 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1.15 | 3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13 | 30 | 1 | 1 | 0080-Stackers/reclaimers | U2-Forced - Delayed | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 369 | 246 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 938 | 268 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 103.29 | 19.8 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 323 | 51 | 1 | 1 | 0080-Stackers/reclaimers | U1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.6666 | 176 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 980.8333 | 214 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184.1666 | 170 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 952.5 | 63.5 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 961.5 | 64.1 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 9824.5832 | 475 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 465 | 310 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 6402 | 330 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1889.8331 | 290 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 650-Fluidized Bed
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 116 | 29 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 910.5833 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 290080 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 245 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 273 | 39 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 140 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 180 | 30 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 490 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 175 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 315 | 35 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 160428 | 461 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 732.7 | 102 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 164604 | 473 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 418.5 | 30 | 1 | 1 | 0085-Bunker feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4836 | 248 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243.3333 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.6 | 48 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1147.0359 | 86.46 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25541.2665 | 638 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26523.9331 | 308 | 1 | 1 | 0090-Bunker fires | U2-Forced - Delayed | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.2 | 48 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.6666 | 100 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1311.7122 | 168.89 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2432.6661 | 820 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1640.3572 | 417.04 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10186.7329 | 638 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64190.6665 | 620 | 1 | 1 | 0090-Bunker fires | U1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132 | 60 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 730.3333 | 35 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 219.9996 | 600 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 133.25 | 41 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 100.1 | 77 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.2654 | 77.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 575 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 600.6 | 231 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 462.8137 | 22.78 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 362.6987 | 23.68 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 110.5 | 51 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1800.5133 | 80.62 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.5 | 56.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 325.4515 | 37.77 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 389.175 | 51.89 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 394.6666 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.7333 | 56 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 824.1666 | 115 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 373.728 | 27.48 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2267.0662 | 694 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3203.9662 | 694 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.4 | 116 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.6665 | 560 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.1902 | 22.81 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290 | 725 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 957.3666 | 154 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 18.6 | 4 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 266.877 | 22.81 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 886.8833 | 127 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227.5 | 650 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.4037 | 18.91 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 37.1 | 37.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1355.4683 | 72.94 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 18.4 | 6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 56.4667 | 22 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.95 | 19 | 1 | 1 | 0095-Bunker flow problems | D3-Forced - Postponed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.6 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 534.06 | 24.84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1988.1033 | 101.09 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 186.4105 | 41.89 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 8.5 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 774.3332 | 505 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 242.6666 | 112 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 399.6665 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 518 | 740 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 271.18 | 62.58 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 51.6 | 72 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 269.1666 | 85 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 557.09 | 76.84 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 178.3332 | 535 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.6733 | 7.6 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.175 | 11.7 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 186.8333 | 56.05 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 663.9066 | 49.3 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 298.75 | 239 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.9995 | 675 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.5 | 51 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 168.8733 | 17.35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 246.6666 | 100 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.81 | 22.81 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1860 | 93 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.9997 | 525 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.2496 | 615 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.5786 | 54.44 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 239.6833 | 73 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 582.01 | 52.91 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2750 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 510.4167 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 7905 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 371.6667 | 20 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 13850.4166 | 65 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 827.3333 | 85 | 1 | 1 | 0095-Bunker flow problems | U1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 6106.3333 | 70 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 140 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2022.5833 | 65 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 650-Fluidized Bed
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 185 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 185 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 350 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 360 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 741 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1190 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 90 | 30 | 1 | 3 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 136 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 504 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 608 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 703.4667 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 245 | 35 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 407 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 480 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 640 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 3260.09 | 45.3 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 81 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 245 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 90 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 105 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1995 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 148851 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 175 | 35 | 1 | 3 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 96 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 179.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 189 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 513 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 120 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 168 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 75 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 156 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 775 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1140 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 363 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1671.3667 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 120 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 128 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 646 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 245 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 116 | 29 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 174.4167 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 296 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 3268 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 104 | 26 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 105 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 210 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 148 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 224 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 128 | 32 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 224 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 140 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 476 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 816 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 132 | 33 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 324 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 111.6166 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 640 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 120 | 30 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 342 | 38 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 141969 | 37 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 30 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 96 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 108 | 27 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 209.5 | 30 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 504 | 36 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1260 | 35 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 261 | 29 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 782 | 34 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 84 | 28 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 192 | 32 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 848.25 | 135 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.0399 | 174.03 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 177.6 | 11.1 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 408.5 | 43 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4461.25 | 75 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50400 | 100 | 1 | 1 | 0105-Bunker structures | D3-Forced - Postponed | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2.4 | 6 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0107 | Screen (prior to bunkers) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.1667 | 5 | 1 | 1 | 0107-Screen (prior to bunkers) | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.9999 | 168 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.633 | 52.06 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 506.7743 | 114.31 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.2166 | 157.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.8333 | 5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.585 | 162.34 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2589.2432 | 187.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 284.1667 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.1667 | 5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 228.2332 | 334 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 440.64 | 122.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1127.7 | 107.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 762.0832 | 295 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.3333 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.23 | 57.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 560 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 345.9866 | 259.49 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.4082 | 228.5 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4126.208 | 322.36 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.9999 | 201 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33.1 | 132.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 105 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 428.9998 | 257.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75 | 25 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.2666 | 112 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 596.8632 | 261.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2837.7 | 315.3 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54.7866 | 117.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.8 | 201 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.6663 | 82.58 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 73.99 | 10.57 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 502.8333 | 70 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 600 | 240 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.2653 | 18.92 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21508.2764 | 150.39 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 25.68 | 4.28 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 7.85 | 1.57 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3.26 | 1.63 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.1 | 1.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2.0067 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 1617 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Winter | 1285.1666 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 35 | 20 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 3.72 | 0.93 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 4.78 | 2.39 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 13.3933 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 18.5908 | 31.87 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 418 | 11 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 20.7 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 119.1666 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 19.4667 | 16 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 28.86 | 4.81 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 31.02 | 2.82 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 66.6 | 6.66 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 3956.7 | 10.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 19.27 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 6.6 | 3.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 33.48 | 5.58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 45.27 | 5.03 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 189.8333 | 6.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 163.0558 | 25.15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 13.2567 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 83.8 | 41.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 142.0833 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 167.9417 | 3.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D2-Forced - Delayed | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 170.8 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5 | 2.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 14.7 | 2.94 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 21.4567 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 4.08 | 2.04 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 27.87 | 9.29 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 154.0933 | 36.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 10.12 | 2.53 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 6741 | 21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 149.4 | 16.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 121.5933 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 812 | 105 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 43.38 | 7.23 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 51.48 | 12.87 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 9.36 | 4.68 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 21.27 | 7.09 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 306 | 38.25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 22.6667 | 17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 27.95 | 5.59 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 103.35 | 31.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 1043.8 | 102 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 97.38 | 5.41 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 44.7666 | 31.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 1018.4 | 26.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 167.7 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2.36 | 1.18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.78 | 3.26 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 19.24 | 4.81 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 29.37 | 9.79 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 8.72 | 4.36 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 17.85 | 3.57 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 403.7133 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 30.8 | 3.08 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 217.6367 | 21.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 8.44 | 4.22 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 57.75 | 21 | 1 | 2 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 25.06 | 3.58 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 475.2 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 210 | 42 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 907.2895 | 37.83 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 11.2647 | 11.08 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 352.5 | 30 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 7.525 | 4.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 22.85 | 4.57 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 39.5 | 7.9 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 23.4 | 5.85 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 31.6667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 262.5 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | WECC | Summer | 120 | 12 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 84.1667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 45 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 245.8333 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 14.5833 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 28.75 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | WECC | Winter | 152 | 19 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 25 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | WECC | Winter | 42 | 14 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 609.1667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 48.75 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 26.8666 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 123.9333 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 80.6 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 112.6666 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 45.9333 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 97.0666 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 497.4666 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 84.9333 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 248.7333 | 52 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D2-Forced - Delayed | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 9.1 | 9.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 54.6 | 18.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14.2 | 14.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.6 | 3.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 119.5 | 23.9 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 1053.25 | 55 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 15.3 | 5.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 88.4 | 6.8 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.2 | 3.3 | 1 | 2 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34.4 | 8.6 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 90.0333 | 37 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 50.1 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 34.65 | 9 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 72 | 27 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 121.3333 | 28 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 273 | 36 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 521.5833 | 55 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 849 | 60 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 12.3667 | 14 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 6.8333 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 75.6 | 18 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 4.95 | 3 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 96.8 | 24 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 42 | 21 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 96 | 24 | 1 | 2 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 52.6833 | 29 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 23.6667 | 20 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 26.4 | 12 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 10.8 | 9 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 8 | 4 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 10.65 | 9 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 200 | 25 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1084.1 | 74 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | SERC | Summer | 9.425 | 19.5 | 1 | 1 | 0115-Solid fuel gravimetric feeder | U1-Forced - Immediate | 800-Miscellaneous
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1512 | 90 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 30.8 | 2.8 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 3.45 | 2.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 47.8333 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2.5083 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 85.56 | 2.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 33 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 38.2667 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 39.01 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 175.13 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 440.0667 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 41.4613 | 8.32 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2011.23 | 24.3 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 677.565 | 24.3 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 12.45 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 13.695 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 76.6367 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 61.845 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 6.45 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3.77 | 5.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 10.7967 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 6.6 | 3.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1165.995 | 24.3 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 8.5167 | 7.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 16.56 | 8.28 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 496.8783 | 16.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 17.2267 | 3.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2.205 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 83.9683 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 13.8333 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 97.2483 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.075 | 3.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 13.6 | 4.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 5.1233 | 5.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 6.8333 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 174.64 | 4.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 10.79 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 66.5383 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.0033 | 7.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 11.5 | 2.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 106.655 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 341.96 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 303.4 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 1560.9999 | 105 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 3.7267 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 39.2983 | 7.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 55 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 160.4783 | 7.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 32.55 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 76.0833 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 10.9283 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 79.5417 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Off-Peak | 1239 | 105 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 66.2617 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 555.44 | 5.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 34.0017 | 2.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Winter | 2209.1666 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 13.8333 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 72.625 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 24.8733 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 31.6 | 7.9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 9.8333 | 10 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 321.1133 | 4.9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1.26 | 1.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 44.52 | 14.84 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 384.0833 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 3.675 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 98.9192 | 19.85 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 11.0283 | 1.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 149.31 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 6.3 | 6.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 16.7383 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 25.1767 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 189.6 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 61.2333 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 7.3383 | 25.9 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 83.1333 | 29 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 50.2667 | 13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 57.85 | 13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 984.8666 | 34 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14173 | 60 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17010 | 486 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.6 | 24 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 326 | 81.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201926.2 | 627.1 | 1 | 1 | 0129-Other coal processing system problems | U1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 293.94 | 127.8 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.54 | 94.2 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19239 | 53 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9 | 9 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 437.1332 | 158 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 195 | 78 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 228.2332 | 334 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 123.99 | 41.33 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2134.9999 | 420 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1088.9999 | 270 | 2 | 2 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89 | 44.5 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86 | 43 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 990.5 | 30 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1125.5 | 30 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2060 | 20 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 650-Fluidized Bed
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 721.6 | 16 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 249.4165 | 365 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 279.8331 | 365 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0152 | Sorbent feed volumetric feeder | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 710 | 355 | 1 | 1 | 0152-Sorbent feed volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 58160.3398 | 334.8 | 1 | 1 | 0160-Bed material tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | U1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 268403.6665 | 624.8 | 1 | 1 | 0160-Bed material tanks/hoppers | U1-Forced - Immediate | 650-Fluidized Bed
0160 | Bed material tanks/hoppers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 629480.64 | 364.8 | 1 | 1 | 0160-Bed material tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 910.2 | 66.6 | 1 | 1 | 0165-Bed material crushers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 172.8533 | 92.6 | 1 | 1 | 0165-Bed material crushers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 1657.14 | 42.6 | 1 | 1 | 0165-Bed material crushers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 19181.8131 | 365.6 | 1 | 1 | 0165-Bed material crushers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 27486.74 | 155.6 | 1 | 1 | 0165-Bed material crushers | D1-Forced - Immediate | 650-Fluidized Bed
0165 | Bed material crushers | Boiler | Bed Material Preparation System (fbc) | D3 | Forced - Postponed | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 20731.7332 | 361.6 | 1 | 1 | 0165-Bed material crushers | D3-Forced - Postponed | 650-Fluidized Bed
0174 | Other bed material handling equipment | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 1591.2 | 124.8 | 1 | 1 | 0174-Other bed material handling equipment | D1-Forced - Immediate | 650-Fluidized Bed
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4879.5833 | 35 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15280.98 | 82.2 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2418 | 130 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34 | 2 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33814.2999 | 114 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 638 | 29 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.7766 | 67.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.96 | 34.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2713.75 | 83.5 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9367.935 | 86.7 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1396.1999 | 93.6 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 50 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 106.6666 | 80 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 331.6 | 24 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.6 | 39.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1800 | 90 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6958.6666 | 80 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4603.2333 | 39.4 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5305.95 | 39 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 823.6 | 29 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2960 | 160 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.5 | 65 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1170 | 180 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23487.75 | 495 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1111.1666 | 282.5 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 222.1666 | 215 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.2965 | 403.4 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57.5 | 115 | 1 | 2 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365 | 150 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3788 | 48 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 234.6 | 102 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2207.1999 | 186 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 533.3333 | 250 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124 | 120 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.1797 | 20.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.8333 | 25.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.75 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.9666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81.6666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91.8333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129.6 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 169 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201.6031 | 390.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237.3333 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 242.5333 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 279 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 455 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 483.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1458.9166 | 305 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6743.7759 | 147.03 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.7 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 128.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163.35 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 261 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301 | 30.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 393.7 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 411.0166 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 853.7333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.1 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50.6333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.135 | 73.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 84 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.1333 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.2666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 225.0665 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 318.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 369.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 437.7333 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 632.1 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1488 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1729.6333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3725 | 500 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4610.9016 | 74.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 32.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 259 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 113.1499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 22.4 | 5.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.94 | 10.77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 295.8666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 446.3333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.04 | 13.86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.2 | 20.52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 85.6 | 12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 569.3666 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.3575 | 25.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.297 | 41.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.3666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.4667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 104.5333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186.7716 | 160.09 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192.5 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 193.6 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 242.55 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 314.7833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 323 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 366.4 | 73.28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 388.5 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 410.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 573.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 598.8166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1422.85 | 199 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2607.7333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3463.719 | 173.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.59 | 8.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 142 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 185.59 | 83.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 225 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 250.85 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 254.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 456.6333 | 133 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 466 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.8352 | 126.68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1106.8333 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1397.4999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1927.2 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10924.9999 | 172.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.606 | 12.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23.875 | 95.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.3764 | 380.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 202.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 278.425 | 47.73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 433.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 482.9166 | 152.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 490.75 | 151 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 619.4 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1046.2499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1482.6 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3680 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 287 | 41 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 619.2 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1156.7 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.01 | 18.67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.8333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.6167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 685.2 | 72 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 320.45 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26.5833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.25 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 101.5 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 129.8333 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 135.3333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.0333 | 29.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 514.6 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 548.25 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 550 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 661.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720.9666 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 729.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1871.8 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10093.9333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.01 | 270.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.4227 | 35.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.8463 | 70.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 901.5203 | 179.11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1090.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1100.95 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3355.5666 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.15 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 73.3333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 131.95 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 174.4166 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 244.86 | 92.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 374.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 814.4333 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1255.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2880 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8896.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 69.39 | 23.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150.8666 | 124 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 362.8332 | 217.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 172.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 289.92 | 12.08 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 839.96 | 36.52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 645.5666 | 107 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1162.8999 | 87 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.8 | 36 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 298.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6079.9998 | 600 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.2332 | 146 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.35 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.725 | 30.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.5666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 318.2833 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 467.41 | 108.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 514.8 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 534.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 593.6666 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 717.9666 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 720 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 962.7333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1000 | 400 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1233.8 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1946.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4242 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5857.2032 | 290.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6758.1866 | 80.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12825.648 | 431.84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.5233 | 51.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.7265 | 28.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.2 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.6 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 197.3333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.45 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 336 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 348.8333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 427.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 554.5166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 607.9593 | 72.52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1037.0832 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1957 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.5392 | 19.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.0667 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 66.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.4666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 147 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 224 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 369.2666 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 414.1666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 487.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 622.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1035 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1830.3999 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3400.5833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3471.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5389.7999 | 117 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.45 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2.72 | 9.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.9 | 7.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1323.3994 | 200.01 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390 | 32.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4821.12 | 100.44 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 169.7499 | 105 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.3 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 318.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.5 | 23.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.2 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 127.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 146.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 168 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.8833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 304.8333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 317.75 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 322 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 341.6665 | 410 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360.4166 | 86.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 384 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 703 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1040.1833 | 139 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1062.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1466.8499 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2271.9665 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3474.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5455.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.9666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74.8 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.8667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.1665 | 417.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.2 | 24 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 239.9999 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 407.5024 | 212.61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 458.5333 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 546.2833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 648.3266 | 123.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 870.8333 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1041.6 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4748.8 | 256 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.2 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 58.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180.99 | 60.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298.003 | 96.13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 439.803 | 112.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 535.4167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 604 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 685.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1572.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3095.8333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3158 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3.22 | 8.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 338.35 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 654.2333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 288.3999 | 216.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1119.9166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 220.4 | 114 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 466.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.0666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.9998 | 360 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 122.1 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.3166 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 143 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 288.75 | 231 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 298.8 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1000.0498 | 531 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1088.6666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2200 | 550 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.4425 | 77.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 71.1332 | 194 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.2433 | 51.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90.9 | 30.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.8333 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.3 | 7.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.8 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 774 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1282.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1362.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1480.4999 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9056 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17.7 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.8 | 56.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51.9999 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 71.1 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 552.123 | 334.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 563.1999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1035 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1047.3166 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1908 | 47.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2230.0802 | 135.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 257.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.5999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 236.6666 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93 | 23.25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 70 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1241.1 | 197 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.0167 | 29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 416.1 | 73 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 803.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9.1 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.594 | 15.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.1166 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.1666 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.6 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.3667 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86.25 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.99 | 29.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 99.9032 | 176.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 217.5166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223.3 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 237 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 333.25 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 400.1499 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 493.5 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 571.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 586.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1652.1665 | 431 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1795.833 | 431 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1938 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3293.3333 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3367.55 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3687.114 | 132.63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4768.5 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.7653 | 25.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.3999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.6666 | 344 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 314.3 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 373.5 | 249 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 383.8332 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 469.8 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522.8166 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 575 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 616.5 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4586.8166 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.375 | 109.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.8 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81.4782 | 32.81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98 | 280 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 147.6 | 164 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 186.6666 | 100 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.1 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 263.75 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346 | 69.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 505.7082 | 132.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1400 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4020.7333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2187.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 108.6953 | 34.69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 132 | 88 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 200.2 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360.9667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 94.4 | 96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 73.3833 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.8333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 150.2666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 165.7499 | 117 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1800 | 150 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.1083 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.8 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.3083 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.2166 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.9998 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.25 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106.6916 | 29.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 144 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.5 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 269 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 371.4667 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 378.6666 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 564.5333 | 116 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 688.2166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 770.5 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 867.8666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 881.9166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1272.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1671.9998 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2319.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10517.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16519.2666 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.05 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.1 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 31.5 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.085 | 93.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78.75 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125.4333 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 133.95 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.6916 | 53.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.8998 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 274.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 364.5 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 398.65 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1635.9 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.7499 | 166.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.9333 | 125.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 128.9166 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.9166 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184.4123 | 70.03 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 203.2 | 254 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 242.7332 | 331 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 295.2666 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 424.3332 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 632.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 652.5 | 145 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 687.5 | 275 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 757.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1836 | 135 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5301.3333 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12054 | 492 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 89.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.0166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.5667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231 | 15.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 840 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.8 | 51 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 176.04 | 6.52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.6 | 56 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 352.5 | 94 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1615.8332 | 277 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34979.9329 | 644 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15.9 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 41.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 93.2166 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156.8 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 176.75 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180.5 | 144.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 320.8333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 375 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 423.6666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 777 | 155.4 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 847.9999 | 192 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1037.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1089.375 | 262.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3315.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6485.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.05 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 105.3166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.1333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.2 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291.8999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 596 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 750 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 791.2998 | 246 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 860 | 215 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1024.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1875.6664 | 331 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2064.6 | 444 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2537.6 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7969.0665 | 241 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17943.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3.1667 | 19 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.6 | 94.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62.5476 | 121.06 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.5 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 167.9945 | 193.84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 516.1333 | 196 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 546 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 960 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1785 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3673.95 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34979.5831 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 62 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 100.2667 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 178.704 | 19.71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 34 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.4666 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.525 | 150.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.3667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.02 | 24.67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25.6 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33.2 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.1 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49.8 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.65 | 30.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 396.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 486.9508 | 157.93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 506 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2122.05 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2160.3766 | 75.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3716.9166 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54.2666 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 58.5 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.1 | 6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136.4 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 263 | 52.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 364.4666 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 513.3332 | 192.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 562.5 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 832.3 | 28.7 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 896.7999 | 114 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14448.9166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.289 | 5.98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.9799 | 107.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 998.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1018.6666 | 320 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1187.9666 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1590 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15435 | 420 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17385.5 | 290 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 86 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198.9666 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198.9667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.115 | 37.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 60 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 104.8 | 131 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285 | 60 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 224.8167 | 41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 344.25 | 81 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2716.0997 | 471 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1399.9166 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 280 | 350 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.604 | 26.51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.35 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.7199 | 104.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.45 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.0666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285.8332 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 293.85 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 328.9999 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 403.3333 | 220 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 522.5 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 807.4916 | 126.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 845.9666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 920 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1048.3333 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1375 | 550 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1652.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1875 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1891.9999 | 330 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2547.4999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8537.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11.0833 | 19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.05 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.6 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.2 | 244 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 88.9 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 90.9333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 125.4 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 269.8 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 400.5664 | 394 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 441.206 | 152.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.1333 | 154 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 643.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1392.4999 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1847.85 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 28351.4666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 20.5833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.825 | 99.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 145.6 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 239.1667 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 269.3333 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 381.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 449.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 562.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 572.3999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 575.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 677.3833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 935.8999 | 294 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1122.5665 | 198.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1146.7333 | 103 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1249.9998 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3035.9999 | 198 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3068 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 818.7666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.745 | 9.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40.3333 | 44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.6966 | 208.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.2583 | 209.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 162 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.9333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.08 | 11.06 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260.325 | 80.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.05 | 13.67 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1327.1 | 28.85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 186.75 | 135 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219.6 | 24 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 226.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 110.1333 | 112 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.015 | 80.1 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1789.65 | 123 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.9666 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.9999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94.9333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.6 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158.75 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247.2 | 61.8 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 303.9998 | 570 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 384 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 696.8 | 268 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1682.2666 | 341 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2719.15 | 119 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12456.6332 | 331 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.279 | 11.67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21 | 7 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40.4166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.2 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.2333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 99.3332 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.8 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 209.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 363.3333 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 520.65 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 621.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 701.8666 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1032.5 | 118 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2994.0666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 57.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 72.5333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.8333 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.99 | 52.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 210.6 | 140.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315.9 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 477.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1045 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1144 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1749.7333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3896.7 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8314.372 | 178.42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 38.7333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.9167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 205 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.8333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 844 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 121.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 122.0032 | 215.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.4 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.1667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 108.65 | 41 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 72106 | 620 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.825 | 30.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51.1833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.7 | 31.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.41 | 73.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 192.8333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 252.5 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.9333 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 508.3 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 513.3331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 699.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 727.0833 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 760.5333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1365.8666 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9210.6165 | 356.54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53.55 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 93.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195.2666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 202.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 301.02 | 50.17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308.4333 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 593.7499 | 142.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1245 | 332 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.35 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32.0008 | 34.91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35.85 | 119.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 43.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.8666 | 74 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 100 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 107.7167 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 128.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136.8 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 175 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 257.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 313.2666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 347.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 377.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 414.9929 | 289.53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 675 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 800 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 843.3149 | 188.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1038.479 | 64.77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1920 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2087.0833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4435.249 | 111.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5713.4682 | 129.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.9588 | 9.01 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 37.5666 | 46 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.4166 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 345 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 24.75 | 11 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 76.2667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 28 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 549.7333 | 76 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 750 | 90 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16969.4 | 644 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.5 | 5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.75 | 43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.5 | 98 | 2 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 105.3333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 121.5999 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 162.975 | 26.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 186.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 290.7333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 291.6665 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 387.9998 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 742.61 | 135.02 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1042.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1482 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1761.1999 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2872.324 | 141.96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.0833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.15 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 143.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 268.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 422.05 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 438.6666 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1143.95 | 83.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1878.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 110 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 143.66 | 65.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 601.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 607.6 | 93 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1120 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1330 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1543 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2704.1666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27439.9999 | 420 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 698.75 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2575 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 204.44 | 43.04 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 129.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 66 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.4 | 43 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 730.2432 | 300.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810.04 | 57.86 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1028 | 41.12 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3282.0666 | 91 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 328.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 963.5333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 554.6999 | 387 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 973.7 | 182 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.5 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11.7 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34.45 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.5 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 89.25 | 25.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 124.55 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.9999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.95 | 131 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 203.6833 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 355 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 385 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 405 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 460.35 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 558.7333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1243.9333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1631.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2641 | 190 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3906.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.8333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.5482 | 270.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.25 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166.6666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184.95 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 201.6 | 11.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 266 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 313.2666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 628.9333 | 178 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 680 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 689.9999 | 103.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 787.75 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 817.0832 | 132.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1182.1898 | 80.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1632.285 | 305.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5063.3333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2.7 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.8 | 42 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69.2999 | 297 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 203 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 264.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 467.6666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 300 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 637.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1249.6666 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3694.3607 | 174.95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 621.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 72.3333 | 31 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4227.9195 | 397.61 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222 | 55.5 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 228 | 45.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 563.6333 | 37 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 583.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 391.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.3 | 79 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 179.1 | 54 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 300.8333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 326.7 | 297 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 284.2 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 227.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 844.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 60 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 290.4 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 446.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 516.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 36 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1869.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 20 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 2754.1332 | 128 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 49.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 835 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 30 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1066.6666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1720.5 | 111 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 244.4 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 60 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 176 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 37.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 26 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 61.75 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 444.1667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 39 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 357.2833 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 253.9333 | 13 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 18774 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 917.7 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 741.6667 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 11324 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.8167 | 1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.9333 | 32 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 100 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 345 | 100 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182 | 36.4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131.75 | 85 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 37.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.6666 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 193.5 | 135 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 237.4866 | 145.4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27.5333 | 28 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.2 | 12.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.6666 | 55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 444 | 37 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 440 | 40 | 2 | 2 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.7833 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 661.2 | 152 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 687 | 90 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2907 | 102 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 296.8 | 28 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 289 | 68 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 960 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.6 | 72 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 238 | 140 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6105.8332 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11035.8332 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 464.1 | 26 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 96.7178 | 63.77 | 1 | 1 | 0253-Pulverizer feeder motor | U1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 45.4 | 45.4 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.6 | 28 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10015.8332 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 197.12 | 123.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260.3333 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4379.5666 | 74 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 117.6566 | 75.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.2666 | 28 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1370.2499 | 81 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1726.4833 | 71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 348.75 | 155 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 550 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 218 | 109 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.35 | 20.7 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.6666 | 350 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90 | 30 | 1 | 1 | 0255-Pulverizer feeder coal scales | D3-Forced - Postponed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 572.7 | 83 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1218.471 | 176.59 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.25 | 27 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 599.4 | 111 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 212 | 60 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 650-Fluidized Bed
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 45 | 50 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 650-Fluidized Bed
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.5 | 65 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 563.7166 | 149 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2349.6665 | 265 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17662.25 | 265 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 283.1333 | 124 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 933.75 | 415 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1169.9166 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.9666 | 149 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 370.6666 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2972.4165 | 265 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4945.8332 | 250 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74.75 | 65 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1086.5166 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 352.5 | 150 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1585.1 | 262 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.3333 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 560 | 160 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 127.5 | 255 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.4 | 72 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 390.5 | 30 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 95.8333 | 250 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 743.5997 | 507 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 48.75 | 75 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 204.25 | 142.5 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 262.5 | 250 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61232.5994 | 858 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 484.1833 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 410.05 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 187.9166 | 275 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 284.1666 | 275 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1397.25 | 135 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52 | 60 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 21834.6331 | 658 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.3166 | 139 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7027.8332 | 149 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2863.5 | 415 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1330.4166 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.3333 | 95 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.7207 | 41.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8897 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 160.457 | 110.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 656 | 320 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 110.6049 | 120.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2973.4166 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123 | 82 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.8666 | 107 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44.2419 | 120.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 129.1033 | 110.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65.569 | 135.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 266.6666 | 160 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1059.8833 | 19 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 927 | 30.9 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1725 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12495.62 | 82.1 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18206.9999 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12056.45 | 703 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 36.7333 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 357.5 | 50 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3235.7167 | 23 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.6 | 24 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1225.5 | 430 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1757.8666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 96 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 499.9998 | 600 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 65 | 30 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 180 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 298.4999 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 42061.5833 | 71 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 96589.6666 | 101 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.96 | 12.83 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 59.2 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 127311.9998 | 240 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418.4999 | 81 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1706.8 | 251 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3380.9999 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4307.9999 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43606.9665 | 518 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44907.5 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.4266 | 70.1 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 212.1 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 599.4 | 148 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1042.6665 | 368 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 216 | 54 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77.6833 | 79 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 999.9996 | 600 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98 | 24.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1564.3331 | 380 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1703.2499 | 135 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.6666 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.97 | 14.71 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 155.7 | 86.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 204.9333 | 29 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1096.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3616.6666 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1030.4998 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 59894.9999 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58.75 | 75 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 388.8333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 27.5 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 263 | 60 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276.9332 | 248 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2363.3165 | 431 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11264 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.425 | 117.14 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1005.3331 | 290 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229190.5 | 770 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86 | 43 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 643.0666 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2584.1665 | 175 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.5332 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2131.2 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1197 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 530.12 | 9.14 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 79.3333 | 68 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.3333 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 287.9167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1397 | 254 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5308.65 | 251 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 5564.1998 | 516 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22358.4782 | 219.38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 325 | 26 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.4167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.6664 | 340 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3307.2667 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.3333 | 32 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 417.0749 | 301.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3217.5 | 495 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 290.4999 | 105 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.95 | 15.45 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 575.9999 | 432 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 432.5 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1109.1666 | 242 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 255.2 | 58 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 439.25 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 16892.9998 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240.3333 | 28 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 897.8666 | 91 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 211.2 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293.3333 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1540.8 | 48 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1979.3333 | 10 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.65 | 17 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2451 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 162.6333 | 82 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 259.35 | 133 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1684.6666 | 133 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3788 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4718.4 | 96 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82 | 41 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 308.7666 | 157 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 693.5 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36068 | 508 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1263.3332 | 200 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 709.5 | 330 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 698.3333 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1472.6 | 39.8 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 16 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61 | 30.5 | 2 | 2 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 498.75 | 95 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129.8 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 100 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.08 | 5.11 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.02 | 2.89 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.7166 | 43 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.6167 | 23 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17543 | 530 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1431.7333 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8914.4166 | 115 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35726.6666 | 230 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40949.9998 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40 | 75 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2583.6666 | 115 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20588.7161 | 823 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 908.01 | 24.3 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 115.83 | 24.3 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 650 | Fluidized Bed | TRE | Winter | 14276.1666 | 130 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 0 | 0 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 926.7933 | 24.4 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 522906.6 | 114 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 10339.5 | 113 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 29754 | 174 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10088.7496 | 525 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1073 | 580 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 3957.4665 | 268 | 1 | 1 | 0262-Primary air fan lube oil system | U1-Forced - Immediate | 650-Fluidized Bed
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 399.6 | 81 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116.1333 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.1333 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5151.4666 | 104 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 30 | 75 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 133.3332 | 125 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 78.8666 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.344 | 23.84 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 582.726 | 114.26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7091.6666 | 185 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150.7333 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 289.8 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 297.2666 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.912 | 26.08 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 181 | 60 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 904.6666 | 115 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 282.3333 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4106.1666 | 347 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.5667 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 419.4667 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 275 | 13.75 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 428.5833 | 139 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.6667 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 154.98 | 22.14 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 79.9999 | 75 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3184 | 64 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 753.22 | 28.97 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.1 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86 | 8.6 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 3.75 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 276.0333 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224.9333 | 28 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1360.08 | 75.56 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8677.4999 | 450 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.0667 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4140 | 180 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 387 | 21.5 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1920.0666 | 347 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17330.7832 | 547 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 106.1667 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13206.1665 | 395 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5199.21 | 42.27 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 70 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4413 | 18 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1151.25 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1155 | 150 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5622.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1929.3333 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35464.9998 | 300 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2047.3333 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 40 | 2 | 2 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 344.8666 | 28 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 832 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83 | 41.5 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 464.9998 | 450 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 238.8648 | 333.3 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 428.3333 | 50 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 973.5 | 354 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4174.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.81 | 14.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248.4 | 54 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3885.1496 | 531 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.25 | 95 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 543 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4416 | 120 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1064.6666 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4909.9167 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.3333 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 624.75 | 45 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 694 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.3333 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.25 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.225 | 42.49 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.3333 | 29 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 262 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7542.9998 | 570 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1260 | 420 | 1 | 1 | 0264-Other primary air fan problems | D3-Forced - Postponed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 438.5 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 684 | 38 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.3333 | 40 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 249 | 30 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.3333 | 100 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 652.4 | 326.2 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 553.5375 | 147.61 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2050.0833 | 73 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 292 | 146 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 878.3332 | 340 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 109835.6999 | 117 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 599 | 60 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.0833 | 17 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 77325.9662 | 658 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23247.4998 | 510 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21672.2331 | 293 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 422.97 | 18.39 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 39.6667 | 20 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221.55 | 7 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2017.3333 | 8.5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3599.9167 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3081.2833 | 7 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 193.8133 | 12.64 | 1 | 1 | 0266-Primary air heater fouling | D2-Forced - Delayed | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3474.9167 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3719.9167 | 5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0266 | Primary air heater fouling | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2108.9917 | 8.5 | 1 | 1 | 0266-Primary air heater fouling | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1189.6664 | 430 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1554 | 222 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 299.1667 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 45 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 171.6666 | 103 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.3333 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 766.5 | 36.5 | 2 | 2 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8880 | 1110 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162.0833 | 25 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.8333 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1803.1 | 38 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2458.5863 | 526.84 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 455.6 | 268 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1135 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 100 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2152.8412 | 630.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.5333 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4686 | 284 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 124.95 | 51 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 327 | 60 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7054.1666 | 125 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1221 | 110 | 1 | 1 | 0267-Primary air flow instrumentation | U2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 93 | 62 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1100 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 551.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.3333 | 70 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1225.8333 | 50 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1092.5 | 115 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 484.5 | 51 | 1 | 1 | 0267-Primary air flow instrumentation | D3-Forced - Postponed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 10 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 123.95 | 67 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12922 | 284 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1678 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13070.75 | 55 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 143184.6 | 108 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8.4333 | 11 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8373.9 | 271 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 24 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 345 | 690 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10 | 12 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210.4832 | 173 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 331.7414 | 182.61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10205.6666 | 170 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 193.7166 | 59 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62.8333 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2231.1 | 111 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5227.8333 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 419.75 | 115 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 554.5533 | 43.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 686.7 | 126 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2511.1999 | 129 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42 | 18 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1217.4999 | 150 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39227.227 | 201.89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.7333 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 145.6 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42 | 36 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86.1666 | 94 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 603 | 201 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10956.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66.6666 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4344.5183 | 87.65 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 430.0333 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2837.7 | 315.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 519.75 | 189 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4178.9747 | 492.61 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.5 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 119892.05 | 101 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.1 | 29 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2638.9332 | 128 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3578.4 | 71 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.3667 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 533.5125 | 52.05 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 207884.9662 | 682 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 866.7796 | 159.53 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2912 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 153.5833 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.4999 | 195 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.8333 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.25 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.5667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 201.4 | 127.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 858 | 88 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.2833 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312.6666 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60346.7119 | 189.69 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.1666 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 222.4056 | 125.89 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.5 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 50.1 | 167 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99.8166 | 53 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410 | 82 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 440 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7644.4581 | 677.5 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13281.5 | 505 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.5033 | 32.05 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.6666 | 136 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 413.14 | 136.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1734.9925 | 223.87 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26367.9665 | 422 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 682.9166 | 149 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 891.8166 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93.4166 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10166.025 | 152.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.0666 | 74 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 395.9999 | 108 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 569.85 | 87 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1181.3833 | 73 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1830.55 | 93 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1152 | 160 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 406.25 | 39 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2514.2 | 78 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 130.6666 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23676.0832 | 505 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.9003 | 11.57 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1820 | 520 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3224.0999 | 198 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103 | 30 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2006.9999 | 135 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4234.204 | 814.27 | 1 | 1 | 0270-Primary air duct and dampers | SF-Startup Failure | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24069.9998 | 498 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 177.7333 | 62 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 192.665 | 124.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 344.9999 | 225 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.75 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3633 | 126 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.008 | 62.92 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 501.75 | 45 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 299.4333 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6806.835 | 720.3 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 15 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1334.9066 | 90.4 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.0833 | 109 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 463.2 | 48 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17185 | 140 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 65324.11 | 432.61 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2109 | 70.3 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186.55 | 91 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 717.8333 | 73 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 767 | 260 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1332 | 360 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1638.6333 | 109 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1539 | 342 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1872 | 160 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 299.6333 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 425.7166 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 553 | 42 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 224 | 56 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 428.4 | 72 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4200 | 300 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 599.2 | 107 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4062.6666 | 110 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 511.75 | 89 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 310.7233 | 19.22 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3027.1665 | 410 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 86.2333 | 26 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 464.4582 | 177.5 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 407.6999 | 162 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25791.9997 | 465 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21.0332 | 126.2 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3636.5333 | 208 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3157.3148 | 720.3 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 370613.1 | 858 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23 | 20 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 531.05 | 40.85 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D2-Forced - Delayed | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 426.5166 | 157 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 21924 | 261 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 14698.3666 | 98 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 92.1 | 30.7 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 885.4999 | 231 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4107.1333 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 340 | 170 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3080.5 | 122 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81 | 20.25 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1035 | 41.4 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 328 | 160 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1084.5 | 241 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1817 | 230 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11400 | 37.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63.7 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 607.0832 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2153.6666 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1351.1666 | 242 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7222.4833 | 217 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 125.2549 | 183.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31659 | 122 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 645.05 | 33.95 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1157.97 | 35.09 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 326.15 | 33 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 819 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.75 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 203.175 | 30.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1550 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 664.15 | 17.95 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158.99 | 12.23 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552 | 13.8 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1620 | 270 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4262.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2281.5 | 195 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 406.4332 | 274 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4465.0666 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6085.5 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.03 | 5.67 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.99 | 21.57 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2381.82 | 44.94 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63 | 21 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 160 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1057.05 | 81 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6312.5332 | 269 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.92 | 7.64 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.94 | 10.77 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 986.04 | 14.94 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 157.1666 | 115 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 693.25 | 235 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 796.5 | 29.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 183.6 | 25.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2220 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6812.8499 | 99 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12816 | 18 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54 | 5.4 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.8332 | 250 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 175.5832 | 245 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 986.9998 | 252 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3611.4665 | 232 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5335.3999 | 222 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16244 | 262 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2645.5 | 185 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7454.9999 | 225 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3657.5599 | 179.88 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 206.2666 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1512.8 | 124 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4110 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 213.3666 | 37 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 307.2667 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 921.5 | 97 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.25 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 444.99 | 68.46 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 909 | 50.5 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 483 | 60 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1233.4166 | 95 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3024.5833 | 175 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.6 | 91 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310.8 | 259 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 436.8 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5354.1 | 9 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70 | 42 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 134.6666 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3865.333 | 446 | 1 | 1 | 0300-Pulverizer motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2910 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 447.3333 | 244 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 501.15 | 19.5 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1139.6 | 51.8 | 2 | 2 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3700 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2232 | 96 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.04 | 5.16 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.13 | 4.67 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3633.3333 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 286 | 28.6 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7221 | 174 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.9999 | 180 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 462.1666 | 94 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11016.6666 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3880.5 | 78 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 105.3 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.4 | 72 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2749.95 | 97 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5427.7665 | 262 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 935.1666 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18023.4 | 279 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.008 | 26.04 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1204 | 43 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2211.3 | 24.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 207.1 | 38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 417.86 | 12.29 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 934.1333 | 124 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1300.86 | 39.42 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 211.3999 | 84 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3461.3333 | 220 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.3333 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 436.25 | 15 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215.5998 | 264 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2373.7166 | 73 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.08 | 3.56 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 130.98 | 21.83 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.01 | 3.87 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1661.1 | 79.1 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3785.5 | 134 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 3051 | 113 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.1999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 303.4 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 327.25 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 330.5333 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1161.1133 | 27.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1449.3183 | 104.77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1813.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9375 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6666 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.5733 | 15.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.1 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 103.85 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192.6166 | 165.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 259.2 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 667.4 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 679 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 703.5 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1356.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2473.38 | 109.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.7833 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 334.8333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 405.9999 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 421.1833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 520.5333 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1394.7199 | 227.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2742.75 | 95.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3768 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18845.2 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25536 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.1333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 93.4999 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 628.6 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124.4833 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 460.75 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.8333 | 10 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 148.2833 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 257.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1804.8 | 72 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.8833 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 65.45 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1250.7833 | 71 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 212.5499 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9.3996 | 564 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 60.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.25 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96.5833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.1666 | 37 | 1 | 3 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.0333 | 57.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 331.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 338.13 | 57.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.1666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 530.1333 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 548.7999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 632.0833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 636 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 841.5 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2522.3332 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3400 | 272 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5466.6333 | 87.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137494.4999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.6166 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 103.8666 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.4 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 243.54 | 221.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 345 | 138 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 366.9167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 369 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 428.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 483.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1523.5466 | 117.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5959.25 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43.0666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 51 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 154.7625 | 123.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 359 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 766.5932 | 164.27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1150 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1212.5 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21299.85 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 32692.4999 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1798.3333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.4975 | 30.63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 145.2 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138 | 138 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 238 | 29.75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 800.25 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 75.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.65 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.5 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 496.6 | 382 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 734.9998 | 252 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 796 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26221.0832 | 415 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.6933 | 46.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.7 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 54 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 93.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153 | 4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 179.1999 | 192 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 202.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.25 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 283.6666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 456 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 484.5 | 285 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1306.25 | 475 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1730.85 | 314.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1937.75 | 337 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2128.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35470.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53076.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 37.9666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182.3833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 205.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 349.0666 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 607.0066 | 109.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 768.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1987.3233 | 74.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13.0333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.8 | 173 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 398.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 486.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1220.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1840.7166 | 179 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2146.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15768.4 | 31.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 277.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 375.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1099.4667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.5333 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 338.8 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.6333 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98997.024 | 197.52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 479.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1183.9333 | 86 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4321.1666 | 55 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10 | 12 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 116.5333 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 240.9333 | 52 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 62.3333 | 34 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1025.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38883 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2351.6666 | 83 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 356.9414 | 738.5 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52.2562 | 165.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73.6 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 109 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.6567 | 14.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 191.6999 | 162 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 235.6 | 117.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 351 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 361.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 801.85 | 17.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1153.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1694.3499 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1815.0181 | 163.27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2610.4733 | 70.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2893.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4956.25 | 162.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7734 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.8333 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17.1 | 28.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79.75 | 319 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.8 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.25 | 35 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.8333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.26 | 141.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 139.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 197.4 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 214 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 382 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 431.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 496.3833 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 641.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 789.6666 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1055.7733 | 121.82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1175.7233 | 104.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1462.34 | 112.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2300.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7835.3 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 20 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 46.6666 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 81.6666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 349.812 | 44.28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 409.3375 | 125.95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1066 | 410 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1162.4166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3333.6665 | 274 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.4 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 431.25 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 4.7667 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.5666 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 585.2 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 606.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 128.9166 | 65 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 152.0833 | 73 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19324.4999 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 182.4 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 351.3333 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 544.8667 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 806 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 847 | 242 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1370.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2731.25 | 287.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3688.8999 | 222 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4360.4166 | 162.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.3 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.9833 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 172.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 216.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 339 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362.8 | 90.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 460 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 591.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1858.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3439.3833 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.6667 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 754.4 | 164 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 854.4 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1567.8 | 234 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1584.9166 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3843 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.7333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 101.05 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 533.338 | 56.94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.55 | 29 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 207.7583 | 26.75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.4333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.6 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 656.1333 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.75 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282.9 | 73.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.8333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1285.3499 | 171 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 119.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 673.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1281.15 | 73 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 216 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 473.2 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.8 | 92 | 1 | 2 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 378.9333 | 98 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6539.0498 | 471 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.4933 | 72.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47 | 235 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61.5 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.5333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 170.8166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 183.7166 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 296 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.5467 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 599.5 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 674 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 703.8 | 82.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2649.975 | 119.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3719.6333 | 151 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6714.9999 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.3367 | 14.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.68 | 67.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 79.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.8666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 286.9999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 358.9665 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 372.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 384.2 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 391.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 510.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 647.8333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1435 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1730 | 200 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2711.8 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3391.8831 | 360.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.9993 | 23.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 207 | 230 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 321.0165 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 325.6066 | 44.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 340.75 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 528 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2160 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4068 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6836.5416 | 117.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 165.2 | 41.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1228.3 | 173 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2566.2 | 91 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 125.4 | 76 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 617.5 | 325 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.9333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.6667 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.9667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.2166 | 87.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.6665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 440.0532 | 165.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 588.5712 | 165.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 975.9166 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 987.0833 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1054.0666 | 326 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1198.75 | 175 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4916.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5687.9165 | 182.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 76.2667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 91.2 | 152 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.36 | 119.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 230.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276.9333 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 772.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 962.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1119.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3502.8716 | 165.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134.1667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.95 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 175.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 425.3333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 472.32 | 49.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 631.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1107 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1419.4332 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1440 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2727.45 | 191.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7830 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.7333 | 11.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 376.6833 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.65 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.6 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 273 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2552.933 | 467 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15993.6498 | 537 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1158.9998 | 570 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 375.0666 | 97 | 1 | 1 | 0310-Pulverizer mills | U2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.7499 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.4167 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.7 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.75 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 234.85 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.515 | 74.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 348.3 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 467.4 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 935 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 969 | 190 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1471.2333 | 202 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1655.7066 | 214.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2947.2 | 92.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30095.8999 | 177 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.2333 | 94 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.2 | 75.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.5833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.2916 | 26.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 381.33 | 401.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 462.5833 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 797.9833 | 165.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 902.7199 | 109.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1402.2498 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1496.25 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1511.2499 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1611.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 19.6 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52.065 | 80.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 107.2366 | 121.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 118.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 144 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 330.9166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4339.8333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12577.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 76.5333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 78.3 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.9 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.8442 | 21.31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.0667 | 30.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 297.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 589.85 | 141 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3859 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222.3 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.8 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.3833 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 154.7 | 78 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 351.05 | 119 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 250.2 | 18 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1280.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80.5 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 265.1666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 312.0549 | 134.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 327.9999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 428.1333 | 169 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 644.8333 | 106 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1320 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2248.4666 | 116 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2494.9165 | 235 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4096 | 128 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5291 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7692.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14.1 | 94 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48.7166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.8633 | 134.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.25 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.6166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.75 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 193.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 194.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 273.1417 | 36.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 575 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576.7133 | 62.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1307.1999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.4395 | 20.49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48.8 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.6 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 209.0666 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.45 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 328.49 | 64.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 579.6666 | 74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 583.3625 | 66.67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 697.4499 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 735 | 294 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 816.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1261 | 19.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2156 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2903.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4736 | 320 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.85 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 33.0667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 106.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 201.94 | 8.78 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 242.06 | 17.29 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 305.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1181.5 | 139 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 153.45 | 31 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 588 | 72 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 328.8166 | 109 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.0333 | 74 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 70.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 238 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 230 | 115 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8021.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 893.2332 | 254 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.22 | 4.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 22.6666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.4333 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.9333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 99.048 | 123.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 140 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 177.1667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 195.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 216 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242.55 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 294.5332 | 188 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 365.8 | 236 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 508.8 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 658.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 673.5832 | 137 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1072.8666 | 209 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1142.9999 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1865.7865 | 189.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2434 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2872.7333 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4384.9998 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5244.2833 | 55.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11657 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23100.3333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.8167 | 3.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.3666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.6 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.5 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.77 | 141.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.9167 | 14.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.7581 | 280.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 332.5 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342.3333 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 343.8 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 354.5833 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 387.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 449.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 498 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 680.625 | 82.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1460.6083 | 240.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1774.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2798.05 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39.9667 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.9999 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 68.25 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.6666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 170.4 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 266.6664 | 400 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 363.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 457.9981 | 392.57 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 684.4166 | 38.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1450.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2584.1666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5911.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5975.2 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.9333 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 393.6 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 661.5 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5.6666 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 13 | 13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 526.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1148.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1799.3 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1353.2 | 199 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 76 | 19 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 166.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3183.2 | 92 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7809.75 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1361.25 | 363 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 49.5 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156.3333 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 303.0833 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 352.1 | 42 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 385 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 403.3 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 421.9166 | 305 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 503.8233 | 57.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2567.5999 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2761 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3924 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5872.5 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6473.9581 | 282.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7091 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.8 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.425 | 21.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154.7833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.6667 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 207.1999 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 438 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 551.05 | 64.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576.1116 | 214.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1019.16 | 89.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1048 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2325 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7242.0833 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8736 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.65 | 21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 106.2 | 236 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128.3333 | 12.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.4167 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.4833 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 290.0866 | 82.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 296.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 382.3333 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 584.25 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 607.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 756.8 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1690 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1971.989 | 165.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 262.8 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.3 | 3.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.457 | 35.87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 101.2 | 69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 381.25 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.5667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2234.7 | 117 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36204.3332 | 170 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1006.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1249.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 164.85 | 63 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 340.7333 | 76 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55506.9 | 95.4 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 838.2 | 254 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55.5 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.6325 | 20.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.4015 | 27.81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1647.8 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5331.7333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.4 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.75 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 105 | 420 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 137.7999 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154.05 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.9999 | 156 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260.85 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307.5266 | 113.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 362.5 | 290 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 751.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1023.75 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1296.6249 | 82.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2310.8 | 424 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2324.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6267.4998 | 345 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43000 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.39 | 74.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 165.3666 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 241.7333 | 148 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269.7 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 584.2 | 254 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 593.3999 | 387 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 781.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1972.3333 | 244 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3017 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3414.4 | 194 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12696.1666 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15414.75 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 77.7 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 132.8 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1296.9667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 149.6 | 34 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 595.55 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 274.5833 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 641.25 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.9 | 42 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 220.8 | 368 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35919 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1597.75 | 415 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.3366 | 74.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.9999 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 203.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 222.345 | 164.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 325.89 | 115.02 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 335.2666 | 94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 459.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 745.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1155.6449 | 164.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2025.1997 | 498 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19.35 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.5332 | 206 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.4666 | 35.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.12 | 141.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.0833 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.3533 | 134.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 193 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 412.5 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 583.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 924.9999 | 300 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2925 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5865 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18001.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56524.6333 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62.05 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.2082 | 250.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 131 | 131 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255.9166 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 279 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 355.4998 | 270 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 473.85 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 602.9333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1312.3333 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2236.6736 | 82.13 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71787.4666 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 55.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71.55 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 902.3665 | 214 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.1 | 20.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 93.445 | 33.98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 394.7333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 32.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 246.4 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 105 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 159.4667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 180.05 | 39 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1649.6666 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.6666 | 34 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49783.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.7 | 12.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258.5833 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 560 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 563.75 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 600.6 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 685.4166 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 932.2266 | 111.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1667.4165 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2337.5 | 187 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3743.3333 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4112 | 257 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.46 | 46.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.7 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.7666 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.25 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142.5666 | 122.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.75 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.9167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 278.4833 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 409.5 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 507.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 531.1333 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 546 | 78 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 573.8 | 28.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 583 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1188.76 | 105.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1729.6533 | 90.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2736 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24.9333 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33.6 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.2 | 12 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227.3333 | 22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 231 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 285.1666 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 295 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 385.4466 | 340.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 385.7333 | 88 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 865.8 | 37 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1003.2 | 114 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2073.3332 | 400 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2500 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13347.1332 | 259 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14066 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14394.8666 | 82.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.3833 | 67 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138 | 92 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.9583 | 17.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 120 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 460.5333 | 88 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 544.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1131.2999 | 162 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 710.1 | 263 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1538.6 | 21 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18016.35 | 537 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32.4166 | 77.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.61 | 119.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.76 | 44.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 141.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 145.6664 | 460 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 196.8 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 216.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 217.8666 | 172 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 315.95 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 403.7867 | 11.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 757.7499 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 851.1982 | 160.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1071.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6195.75 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8098.9999 | 267 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8906.3333 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12226.5 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.1083 | 103.46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111.2033 | 91.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 256.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 258.8166 | 26.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 527.7999 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 936.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1400 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2632.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11623.95 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46.134 | 41.94 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 59.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.85 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 125.19 | 64.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 145.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 244.5499 | 219 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2203.5 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4331.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159.3 | 118 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 419.4 | 108 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102 | 6.8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1160 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 117 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1311.6999 | 78 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 557.4833 | 83 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 69 | 11.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 42.1667 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3425 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 636 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 4825 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1100 | 44 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 987 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1212 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 4189.5 | 133 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 187392 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1536 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 6867 | 218 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 9084 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 452.6 | 73 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 560.55 | 111 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1392 | 96 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1444.12 | 91.4 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 932.75 | 91 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.2433 | 54.2 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 53.0833 | 91 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 229.9999 | 120 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 545.5166 | 71 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34374.45 | 91.3 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.28 | 116.4 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 243.8333 | 38 | 1 | 1 | 0312-Pulverizer mill classifiers | D2-Forced - Delayed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.8833 | 101 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.3333 | 50 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3341.5 | 410 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24216.5 | 170 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8898.3333 | 100 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D3-Forced - Postponed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1104.4166 | 145 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1643.2666 | 157 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0314 | Pulverizer mill ball charger hopper (ball mills only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.6666 | 50 | 1 | 1 | 0314-Pulverizer mill ball charger hopper (ball mills only) | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 40 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 402.6 | 61 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106.25 | 85 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 202 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 321.5333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.5 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 155 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 398.6666 | 130 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 103.1333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2331.0466 | 53.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51 | 25.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.6 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 117.6 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.1667 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 331.9333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 70 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.2666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 91.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.05 | 49 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.3 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 601.5333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 255 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 186.0832 | 159.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 289.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.91 | 5.13 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2708.7666 | 53.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.6666 | 37 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 126.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 140 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1666 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.25 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156 | 90 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 224 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 590.8 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 235 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 636.8 | 96 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125.3333 | 40 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.95 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61.3833 | 127 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.8 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 142 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 341.25 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.8333 | 37 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.8333 | 94 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.5 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.8 | 118 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 348.993 | 22.81 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1962.5 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12.1333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 258 | 12.9 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 479.7 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 58.8 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 112.9333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 259 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 12 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.4 | 72 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 354.9666 | 46 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 461.8667 | 32 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 128.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 288.1667 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 67 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 150.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 258 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.3333 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.05 | 27 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.1 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 138 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 104.4333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.9333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 171 | 45 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 236.8 | 29.6 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.75 | 33 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.8667 | 29 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.55 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 145.1667 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.15 | 80.2 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D3-Forced - Postponed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 64.75 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.4455 | 20.81 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.1643 | 44.81 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1329.1666 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9867.7133 | 86.8 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.032 | 18.81 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22.2236 | 121.22 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14604.6931 | 297.65 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 379.0333 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1316.3933 | 104.2 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319 | 44 | 1 | 2 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1015 | 145 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188.9333 | 26 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 686 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110.8333 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 636.0833 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.1 | 43.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.45 | 141 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 489.3333 | 20 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 900 | 250 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242 | 44 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.02 | 43.17 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 466.1833 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.15 | 31 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 150.2666 | 56 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 440 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3074.9999 | 180 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2950 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 270.6666 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1073.1 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1533 | 210 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 360.45 | 80.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 156.6333 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250.5833 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.0833 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 161.95 | 79 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 400 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1075 | 430 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3499.9999 | 240 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.45 | 41 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1395.3733 | 91.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 487.4998 | 225 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 99.75 | 21 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.25 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 403.3333 | 88 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.98 | 10.22 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84.6 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 420 | 240 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1105.0666 | 112 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 216.18 | 120.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.5 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 126.4167 | 41 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 239.9333 | 59 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 309.3999 | 78 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 194.4 | 81 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 358 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.8333 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1237.3332 | 128 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6591.9998 | 240 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174.5166 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 221.6666 | 95 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5473.3333 | 100 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 245 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 671.55 | 111 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.1667 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 713.8 | 172 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.4166 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.4997 | 450 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.5 | 250 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.85 | 31 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 149.8333 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1548 | 430 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 754.4766 | 151.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 899.9999 | 135 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.6 | 39 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 735.9998 | 240 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 160.2249 | 113.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.7166 | 37 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6198 | 120 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 293.2666 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 375 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 404.0666 | 58 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 56.6666 | 50 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 359.6666 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 55 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2700 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2904 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 463.995 | 147.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 310.3333 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 491.3333 | 88 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 88 | 33 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1386 | 210 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1682.8333 | 115 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 965.25 | 143 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 455.9 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.3 | 54 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 384.8 | 104 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 94.0666 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 350.35 | 91 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4189.3333 | 160 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 546.5166 | 298.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 760.8 | 36 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 60 | 10 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 98.4 | 48 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 169.6 | 32 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 360.6833 | 67 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.2 | 32 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 537.75 | 135 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1167.7899 | 101.4 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 272.9166 | 131 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.2 | 24 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.45 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 20 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 962.5 | 50 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 453.1 | 69 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 206.8666 | 58 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 166.6 | 51 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172.5 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 28 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14 | 28 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D3-Forced - Postponed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1587.6 | 216 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.4 | 67 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.8333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.7666 | 227 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96.6667 | 29 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 176 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 152.8333 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 372.5 | 149 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1976 | 114 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 185.5832 | 131 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2809.3333 | 80 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.3 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.75 | 15 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.9667 | 19 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.8333 | 25 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6995.45 | 69 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.9 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.65 | 39 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 244.4766 | 103.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 783.84 | 16.33 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2865.4166 | 115 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 87.5 | 70 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.5833 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5022.5 | 82 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 443.3332 | 140 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1387.5 | 185 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1425 | 114 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.1666 | 85 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 574.5 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 3288 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 297 | 99 | 2 | 2 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5394.6665 | 238 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.2728 | 10.13 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108.1 | 94 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 765 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 787.4 | 254 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1498.3333 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1352.4 | 184 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 393.3232 | 126.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236.2499 | 81 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 242.5333 | 214 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97 | 60 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 253.1666 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 322.5333 | 41 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13.2 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 574.9459 | 167.46 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1602.5 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 230.3 | 49 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 184.6 | 39 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84.2333 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1751.3332 | 370 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 234.5 | 35 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3485.85 | 136.7 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7945.44 | 331.06 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 632.3332 | 140 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35.7 | 238 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 229.254 | 120.66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1097.1 | 95.4 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 229.2632 | 126.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 157.2 | 72 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12938.3 | 218 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.74 | 133.2 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.75 | 21 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 384.5833 | 65 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185.5833 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.9867 | 10.3 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 302.94 | 17.82 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 398.6666 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 197.1666 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26054.1999 | 237 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 108.35 | 33 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 226.8 | 54 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 750.89 | 126.2 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83.5833 | 85 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 71.5667 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 6.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 50.4166 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.6666 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 84.7333 | 41 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.2833 | 43 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 435 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 210 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1016.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1780.7999 | 95.4 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.9 | 66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58 | 29 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1076.6666 | 170 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.8833 | 83 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.8166 | 89 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36 | 18 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28 | 21 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.5 | 90 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150.5 | 70 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 160 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.1 | 42 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.45 | 57 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 268.7333 | 58 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52.8666 | 52 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 127.8 | 36 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420.96 | 35.08 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 444 | 30 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.7333 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 543 | 181 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 186.6666 | 320 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1569.5 | 365 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.6666 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 142.0832 | 155 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.25 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 549.2499 | 195 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99 | 99 | 2 | 2 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.6833 | 79 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 878.1666 | 110 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 117.75 | 45 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 281.6666 | 100 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.75 | 15 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 246.6666 | 185 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.6667 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 358.5 | 90 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1886.5 | 147 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 237.6 | 72 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 510.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.8333 | 19 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5156.2 | 40.6 | 2 | 2 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.423 | 15.06 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.8 | 68 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 168 | 96 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 462.1666 | 94 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 90.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.5 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.2166 | 79 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.1333 | 79 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 544 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.6666 | 115 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 148.75 | 75 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.8333 | 25 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 85.5 | 135 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 110.9166 | 55 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 118 | 120 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 498.6666 | 160 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 725.4833 | 29 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 594.0665 | 268 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 650-Fluidized Bed
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 353.3333 | 80 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71197.9162 | 625 | 1 | 1 | 0339-Pulverizer System Puff | U2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23262.5 | 250 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 839.5 | 365 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 346.5 | 30 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 358.5 | 90 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26346.6 | 492 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 276.6666 | 100 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 336199.9998 | 492 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 769.8 | 128.3 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 229.7166 | 77 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 390.775 | 223.3 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 286.8 | 72 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1166.8377 | 292.93 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6879.2166 | 157 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 338.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 397.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 425.3333 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 696.1333 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 12 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.5 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.12 | 101.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.35 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.4167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2006.8 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 66.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 209.0666 | 128 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2896.6666 | 88 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15.8333 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22.8 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 297.0332 | 134 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 768 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7049 | 106 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.0667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.3333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 206.4 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.3166 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 529.1 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 945.8749 | 172.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1098.3 | 52.3 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1662.3999 | 96 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3526.2499 | 262.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 226.8 | 378 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 376.8333 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 510 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1126.0415 | 287.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59 | 29.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.4166 | 104.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.8333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 136 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2006.4 | 91.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2386.875 | 142.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2434.25 | 267.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2456.6666 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.6667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5712.5 | 250 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 270 | 450 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1731.9665 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.9 | 118 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132 | 66 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 546 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.7666 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.5 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.2 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 202.5 | 450 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.0333 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 978.25 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 21228.05 | 127 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 71.4 | 63 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10441.3331 | 820 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.95 | 123 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 355.2666 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 596.7 | 153 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.1 | 5.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 17.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 106.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 178.1999 | 243 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 271.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 312.625 | 152.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 671.3332 | 132.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2286.25 | 147.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2537.6 | 97.6 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 390 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3699.4165 | 515 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1428.5333 | 88 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330.27 | 90.9 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1616.2665 | 638 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 800.625 | 152.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2104.2 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27.1333 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.8999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.5833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 676.8 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 796.25 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1015.8332 | 132.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1984.3749 | 187.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5820 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8206.6 | 148 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 199.4198 | 460.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8913 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9621.9166 | 147.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 844.8 | 18 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1304.55 | 223 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.2 | 116 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 115 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 238 | 28 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 795.7833 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 837 | 31 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2044.5 | 705 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31.6333 | 36.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.0333 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 112.0833 | 134.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135.9167 | 35 | 1 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 141.6 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.9 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 250.3666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 318.7665 | 262 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 443.6666 | 121 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 594.1666 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1038.8 | 19.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1364 | 62 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1652.4 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113.1 | 37.7 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 276.3 | 30.7 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 412.5 | 150 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477.4 | 42 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 371.7998 | 507 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12557.05 | 869 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13219.6497 | 783 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 20 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.3333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.775 | 38.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 261 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 113.75 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 149.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 574.1665 | 265 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78 | 26 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117 | 23.4 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52 | 520 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.6666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.12 | 111.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.6667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 46.5 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 282.1333 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 715.875 | 207.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3760.15 | 157 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17551.95 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 286.6664 | 430 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1337.7 | 98 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6144 | 256 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84.3333 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2755.9 | 217 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7961.3955 | 74.79 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154.7833 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 176.1667 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1057 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65 | 50 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 207.9167 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 235.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 611.5832 | 179 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.6 | 36 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1267.9166 | 179 | 1 | 1 | 0340-Other pulverizer problems | U3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 17 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 380.6 | 34.6 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 615 | 205 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12912.6816 | 97.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.6666 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 142.8 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.2 | 36 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 220.5 | 105 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 317.5833 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 404.8 | 36.8 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 520.625 | 297.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 604.1 | 86.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 874.5365 | 207.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1058.85 | 39 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1069.375 | 147.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1646.8749 | 187.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27.75 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 87.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.3366 | 69.8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275 | 550 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 13 | 3 | 3 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25.9667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 85.4 | 122 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 244.2 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.8333 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 636.7166 | 151 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.75 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 332.5 | 13.3 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 609.6666 | 124 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5850 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 339.3 | 26.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 513 | 57 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 563.5 | 490 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1106.25 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3712 | 320 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8457.9 | 23.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.3333 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312.65 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.8333 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371.1666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1338.1333 | 104 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2005.9999 | 204 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2589.6 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3193.2 | 72 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7234.9998 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.454 | 19.22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.3333 | 110 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 235.1664 | 415 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 309.7333 | 46 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1236 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8596.4666 | 91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17311.9999 | 240 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 385.4666 | 98 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 74 | 30 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1151.5666 | 179 | 1 | 1 | 0340-Other pulverizer problems | U3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 17.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 267.5 | 107 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 40 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1476.45 | 153 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.0166 | 37 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.4 | 134.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312.0833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 373.9167 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 414.625 | 267.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 560.625 | 162.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 644 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1333.1999 | 99 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.1 | 6.7 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 341.25 | 455 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 412.0832 | 287.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 446.25 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2170.2083 | 137.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 492 | 48 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 179.01 | 19.89 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 875.4665 | 268 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1292 | 340 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41200.35 | 770.1 | 1 | 1 | 0340-Other pulverizer problems | U2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21.7 | 217 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 64.35 | 117 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 166.6 | 102 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 230.85 | 81 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429.6 | 35.8 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 792.4 | 56.6 | 2 | 2 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 971.7 | 23.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8831.39 | 175.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9875.25 | 133 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13337.4998 | 330 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110.4166 | 132.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 129 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 178.5 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.5 | 45 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 184.8083 | 33.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 644.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 839.5 | 146 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1619.3666 | 101 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4095 | 23.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6247.2 | 91.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 211.2 | 176 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 310.5 | 115 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 326.6665 | 196 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 359.1667 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 921.1333 | 82 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3768.75 | 225 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6029.1 | 783 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 603 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3342.5 | 70 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0341 | Pulverizer deluge system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1026.1666 | 94 | 1 | 1 | 0341-Pulverizer deluge system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 217.5333 | 52 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 321.6 | 144 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2332.8 | 144 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 22000.8 | 824 | 1 | 1 | 0342-Pulverizer inert system | U1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 115.4833 | 169 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 809 | 30 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 235.8 | 393 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 479.8665 | 244 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.4 | 144 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1686.4 | 124 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1364 | 62 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 546 | 91 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3480 | 290 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 491.5333 | 73 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 558.3333 | 125 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21 | 22.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 253 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 343.5833 | 35 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 24 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.4 | 32 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51 | 3 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 225.93 | 13.29 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 904.23 | 17.73 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 467.6666 | 152.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 510 | 75 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368.6666 | 56 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 322.3166 | 83 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 411.75 | 152.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23.25 | 22.5 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 675 | 100 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.6666 | 55 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 218.1167 | 23 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.8333 | 25 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 890.016 | 46.72 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2747.35 | 69 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227.8332 | 136.7 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8495.8332 | 250 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 216 | 9 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4137.5 | 75 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1340 | 67 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2210 | 26 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 683.3333 | 41 | 1 | 2 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15127.1666 | 170 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2253.6333 | 41 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17810.35 | 71 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3762.5 | 30.1 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4326.3 | 25.3 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6687 | 9 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2775.2 | 48 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1659.8333 | 46 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4514.1 | 41 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 577.5 | 42 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7081.25 | 55 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2074.8 | 36.4 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.1 | 6 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2226 | 45 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22791.3333 | 85 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6092.1666 | 55 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2986.8 | 39.3 | 2 | 2 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2282.3667 | 26 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2801.6667 | 50 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 382.5 | 18 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2304 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3244 | 120 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5520.8 | 41.2 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5014.92 | 72.68 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 744 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1392 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 563.04 | 62.56 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4523.9997 | 468 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 474 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1128 | 37.6 | 2 | 2 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2687.55 | 19 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1671 | 45 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8568 | 35.7 | 2 | 2 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1252.8099 | 89.7 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.85 | 3 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3420 | 38 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9975 | 70 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9559.15 | 41 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3191.2833 | 11 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160.27 | 291.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2.0833 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 65.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 293.5333 | 148 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 150 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1056 | 165 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.45 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.0595 | 41.37 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.9999 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.5 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3377.45 | 217.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.6 | 24 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 68.8333 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 86.3833 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.7833 | 59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 224.8333 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 511.2333 | 49 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 737.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.1999 | 123 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 362.6666 | 128 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 230 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 114.4666 | 68 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 545.7832 | 143 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 77.0833 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17 | 8.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 264.5 | 230 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1994.4 | 144 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 294 | 126 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.8 | 36 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.1916 | 126.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 277.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 435 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3418.25 | 55 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.9331 | 284 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 178 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 282.5 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.3333 | 70 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.6667 | 20 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 97.0666 | 52 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29.5166 | 126.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.75 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186.8333 | 95 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2212.5 | 118 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2152.47 | 91.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69.9999 | 150 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.5 | 490 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1020 | 102 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 269.75 | 83 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 21.6 | 18 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.45 | 27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 78.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 449.7666 | 103 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15226.6664 | 800 | 1 | 1 | 0346-Pulverizer pyrite removal system | U1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 600.875 | 126.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.4165 | 455 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1764.3166 | 221 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2328.1833 | 163 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125 | 60 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 128.9166 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 90.0333 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 17.5 | 15 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.6666 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.2333 | 58 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.75 | 43 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36 | 48 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 168.7833 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.56 | 88.84 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.083 | 425 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.1667 | 22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 127.6 | 44 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.4333 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.4 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 126.4 | 79 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 282.5166 | 126.5 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.9999 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 457.5 | 90 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1620 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 60.8333 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 71.7833 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1196.9165 | 271 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.5 | 116.4 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47.25 | 9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 469.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200.9 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 275.2167 | 7 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 83.5833 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4855.5933 | 140.2 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 474.4999 | 195 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 178.75 | 39 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.5832 | 185 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.6 | 27 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.9332 | 152 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 625.0833 | 65 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.4 | 72 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 150 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1743.4999 | 330 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 167.6674 | 182.91 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 582.0833 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222.25 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1184.1652 | 148.64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22.3167 | 13 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 79.0745 | 28.41 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420.9333 | 56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 106.5 | 355 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 653.9999 | 90 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2280.6666 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2021.25 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1131.78 | 145.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 5 | 2 | 2 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187.92 | 117.45 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2865.7466 | 126.43 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 281.5166 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.4 | 24 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.5 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 211.1665 | 181 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1326.8331 | 318.44 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 492.1 | 70.3 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.3333 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.35 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 490.6666 | 128 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.56 | 95.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 75.9666 | 106 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 324.6832 | 126.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3371.8 | 69 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.512 | 12.56 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.3333 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.5 | 63 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.3941 | 86.39 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.75 | 15 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21680.2664 | 836 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | SF-Startup Failure | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 181.6533 | 104.8 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1566.3333 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1344.75 | 55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36.7225 | 59.55 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 259.325 | 126.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5976 | 240 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | SF-Startup Failure | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 60 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 256.2 | 244 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 699.74 | 349.87 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.793 | 163.26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 337.3332 | 126.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2242.8499 | 93 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249.5 | 30 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 593.0666 | 128 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D3-Forced - Postponed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.2383 | 12.22 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164.5832 | 125 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.6667 | 26 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7565.8 | 836 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | SF-Startup Failure | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 562.5375 | 150.01 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 99.4833 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3389.6415 | 435.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 3587.42 | 396.4 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 6125.3865 | 466.4 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.8331 | 280.1 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1803.5016 | 120.1 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156.12 | 130.1 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 3832.9499 | 99 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5238.9333 | 44 | 1 | 1 | 0358-Oil burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4587.15 | 159 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 44.25 | 59 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1269.3499 | 159 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 76.8 | 128 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 673.75 | 35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 405.6 | 169 | 2 | 2 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1683.6 | 552 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 121.6666 | 146 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 689.1866 | 81.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 188.3333 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2743.2 | 108 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1988.4996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 34367.1 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 938.6666 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 478.8333 | 169 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 242.55 | 231 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8874.58 | 150.8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.205 | 8.35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 96.04 | 7.35 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 164.8332 | 230 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1241.74 | 56.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 68.1332 | 292 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1074.1165 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1181.9 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2133.9996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 42.9 | 66 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 960 | 120 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 144.2 | 21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 58774.6833 | 79 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1066.6833 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 512.6333 | 169 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 96.6333 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 20052 | 360 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 391.6332 | 379 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1430.8666 | 169 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 367.233 | 479 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 343.4999 | 90 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 644 | 115 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1075.4331 | 419 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1975.1331 | 559 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 294.5 | 31 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1104.4998 | 282 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 831.9 | 118 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1720.5 | 465 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 392.45 | 167 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1503.188 | 326.78 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4225.85 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 65171.5332 | 412 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 27.7367 | 31.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 51.3 | 342 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 407.4664 | 382 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | DI | 100 | Fossil-Steam | NPCC | Summer | 87.4315 | 276.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 3.0333 | 13 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 345.65 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 73.4999 | 90 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 219.2833 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 289.9 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 23950 | 479 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28929.0666 | 74 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 131.9999 | 90 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1302.9 | 202 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3426.7665 | 223 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3535 | 202 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 140 | 280 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 20.3167 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 424 | 80 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 343.6333 | 169 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 128.9666 | 146 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1526.2331 | 422 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2116.6663 | 508 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1198 | 599 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 594.1 | 457 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1204 | 42 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 185.1666 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 406 | 58 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3762.7996 | 552 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2743.18 | 81.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3649 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1248.9 | 362 | 1 | 1 | 0359-Gas burner piping and valves | U3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 650 | Fluidized Bed | TRE | Off-Peak | 448.5 | 130 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 650-Fluidized Bed
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 549 | 73.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 11.6667 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 142.2283 | 25.55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 11160 | 62 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 202.2666 | 82 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 112 | 42 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 98.8166 | 49 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 399 | 45.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 206.4332 | 281.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 5085.7665 | 281.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 30.6666 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 255.75 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 529.3164 | 349 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 14.9833 | 29 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 39.95 | 17 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 7.425 | 16.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1689 | 281.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1432.9333 | 44 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2.8 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 8865.9998 | 312 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 12.25 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 93.5 | 17 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1064.95 | 59 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1528.7166 | 67 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 18215.4999 | 255 | 1 | 1 | 0359-Gas burner piping and valves | U2-Forced - Delayed | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 21803.6167 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 99.0833 | 145 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 917.8233 | 219.4 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 921.48 | 219.4 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 10381.6883 | 219.1 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 297.25 | 145 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 117.13 | 15.9 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 234.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 9.1883 | 55.13 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 94.5 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 44.3555 | 46.69 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 267.75 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 507.4383 | 121.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 38.25 | 27 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 2601 | 25.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 140.4333 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 295.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 4.6 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 3507 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 30.6167 | 11 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 124.077 | 63.09 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 11724.6667 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 110.3895 | 59.67 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 222 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 375 | 50 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 259 | 60 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 4.4833 | 1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 2587.9 | 2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 31.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 203 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 509.46 | 121.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5747.5983 | 121.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 7.65 | 3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 80.4999 | 105 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 1241.625 | 52.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 2957.4999 | 105 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 905.2 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 656.95 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 116.6666 | 100 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 267.5 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 286.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1078.5 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 165.6 | 41.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 43.9833 | 29 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 176 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1026 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 17.75 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 281.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 224.94 | 41.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 108.6249 | 82.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 284 | 15 | 1 | 2 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 82.1333 | 56 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 743.9667 | 2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 54.25 | 52.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 229.25 | 105 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1681 | 205 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1001 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 271.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 282.25 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 289.75 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1843.8333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 2026.4999 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 299.5667 | 22 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 489.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Winter | 22.7499 | 105 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 56.6666 | 40 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 132 | 44 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 218 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 266 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 278.75 | 15 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Summer | 29.3333 | 10 | 1 | 1 | 0359-Gas burner piping and valves | D3-Forced - Postponed | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1261.3333 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1067.15 | 152.45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1159.6499 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3869.3333 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50.92 | 2.68 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2434.4 | 17.9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173 | 8.65 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.96 | 12.44 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 649.08 | 36.06 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 421.3333 | 160 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 522.5 | 150 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 597.9998 | 552 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97778.3332 | 140 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4699.74 | 64.38 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13650 | 260 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378 | 15.75 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441.98 | 20.09 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 805.2 | 14.64 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1283.84 | 21.76 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1069.9999 | 150 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186.9333 | 140.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.08 | 7.17 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1068.21 | 10.79 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2387.14 | 20.23 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402.8 | 10.07 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 830.02 | 17.66 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1196.92 | 26.02 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1444.67 | 19.79 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1662.93 | 61.59 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 246.96 | 30.87 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500.92 | 17.89 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364.1666 | 115 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 990.9665 | 434 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 90.825 | 86.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12364 | 30 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.1999 | 175.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1014 | 135.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 366.0667 | 38 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 229.1667 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4300.84 | 56.59 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406.98 | 22.61 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810.26 | 13.97 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 866.31 | 12.93 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.5 | 150 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 128.7998 | 552 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 125.5833 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 485.4373 | 95.81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2410.8333 | 110 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 39.4167 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 591 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 782.72 | 24.46 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1241.1 | 27.58 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4971.25 | 51.25 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 23 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 426.02 | 25.06 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 108 | 81 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 412.5 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362.97 | 9.81 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 994.98 | 23.69 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1836.57 | 21.11 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1487.5 | 170 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1275 | 500 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1374.9999 | 165 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1801.8 | 23.4 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 271.83 | 6.97 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392.95 | 13.55 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 738.01 | 56.77 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 979.02 | 15.54 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 920.8332 | 170 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1195.2 | 747 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 91.2499 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5635 | 140 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1372 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2309.5 | 149 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 17.25 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3204.29 | 54.31 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 307 | 15.35 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392 | 12.25 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 790.86 | 16.14 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 878.94 | 23.13 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1745.24 | 18.97 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3768.55 | 33.35 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.1 | 6.65 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 960 | 30 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.0533 | 122.2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108 | 180 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 310 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2714.25 | 165 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7183.3666 | 143 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 177.3333 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 31.5 | 18 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.96 | 15.44 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 702.61 | 41.33 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 13.5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163 | 16.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174.96 | 7.29 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 944.9 | 42.95 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 977.28 | 15.27 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1820.84 | 37.16 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 498.96 | 62.37 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 592 | 23.68 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 193.4166 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219.01 | 19.91 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2198.79 | 22.21 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 696.37 | 8.39 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 744.14 | 25.66 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1365 | 21 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 641.6666 | 110 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2465.5996 | 552 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102.5 | 123 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11880 | 165 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5360 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61640 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 85 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 87.5 | 35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2011.23 | 24.83 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244.89 | 9.07 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 534.4 | 16.7 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 990.08 | 38.08 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3054.3332 | 170 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2633.9828 | 749 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 509.76 | 566.4 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.7498 | 375 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41.1666 | 95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3126.75 | 165 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.98 | 12.83 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 9 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1186 | 29.65 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 220 | 20 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4508.4 | 37.57 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20428.3331 | 721 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33036.25 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12853.3333 | 160 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 498.8333 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 216.04 | 9.82 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 751.08 | 11.38 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2848.95 | 43.83 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4986 | 41.55 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1039.89 | 20.39 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1260.27 | 22.11 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 487.5 | 150 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2298.6666 | 160 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3381.3333 | 160 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1960.233 | 434 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 233.6 | 146 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2841.3333 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 826.8333 | 205 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9316.8226 | 322.01 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 425 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 187.91 | 9.89 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215 | 4.3 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1582 | 39.55 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 397.02 | 30.54 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.11 | 20.49 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1731.09 | 91.11 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 205.3333 | 160 | 1 | 1 | 0360-Burners | D3-Forced - Postponed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1976.85 | 191 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 25 | 125 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 6366.7333 | 196 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 34.4505 | 10.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 21.5 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2844.3333 | 28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1388.3333 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1974.5 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 9259.075 | 117.95 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 448.8 | 204 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 17.2 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | OG | 850 | Combined Cycle Block | SERC | Winter | 68.8 | 86 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 52.479 | 10.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 421.4167 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 5.355 | 10.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 4063.5833 | 55 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3446.125 | 142.5 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 4570.1999 | 108 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 135.255 | 38.1 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 15515.8332 | 215 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 2028.5833 | 55 | 1 | 1 | 0360-Burners | U2-Forced - Delayed | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | TRE | Summer | 1978.5 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1971.65 | 141 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 672.9166 | 85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 0 | 0 | 1 | 2 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 78.0083 | 18.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 125.3333 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 16.44 | 164.4 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 365.425 | 23.5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1616.9999 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 8489.1166 | 59 | 2 | 2 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 67.9433 | 21.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1200 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 8490.1 | 59 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1489.8666 | 151 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 489 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 757.0833 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 28.8 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 665.2099 | 132.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 35.1999 | 96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 244 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 5.0633 | 1.24 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 78.015 | 52.01 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3650 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0362 | Burner tilts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68.5 | 15 | 1 | 1 | 0362-Burner tilts | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6592.0439 | 154.26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 659.1 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1294.4166 | 245 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 348.9583 | 156.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 69.375 | 92.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 8488.8 | 432 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 249.2 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 41226.8333 | 190 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 287.3 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.672 | 4.64 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 60.9166 | 43 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 7.3333 | 55 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1651.0416 | 156.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 98.1666 | 31 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 220 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 668 | 167 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 188.6498 | 231 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 368.6667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 340 | 85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17642.5 | 50 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 258.5832 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 196.9333 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 294.8333 | 61 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30.8 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 362.1 | 213 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 324.9999 | 300 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121 | 121 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.9999 | 165 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 151.9666 | 194 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2919.3333 | 29 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 286.8 | 18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 285.6 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 683.9999 | 432 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1379.19 | 148.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 49.3333 | 92.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 55699.9164 | 415 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36.942 | 16.92 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7987.2 | 832 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 140.8332 | 325 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 90.9583 | 92.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1061.0832 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 10 | 2 | 2 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11336.25 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.6966 | 117.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1097.2497 | 495 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 67.15 | 51 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 134.75 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6281.6 | 832 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 5.775 | 8.25 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 5.8333 | 17.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1579.5 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 86.9766 | 53.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 3.1667 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1.5667 | 47 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2.1333 | 32 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Winter | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 324 | 27 | 1 | 6 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2718 | 302 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 349.65 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 238.7 | 154 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 521.55 | 61 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 297 | 27 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 210.45 | 69 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 47.74 | 30.8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1711.4766 | 57.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 645.05 | 21 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1029.4803 | 222.19 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 747.5 | 65 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 77.5 | 31 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 41230.7999 | 108 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 618.4288 | 222.19 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 223.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 119.9999 | 180 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 222.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 215.4666 | 128 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 447.75 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1867.7 | 114 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 838.0488 | 85.37 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 138.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 51 | 25.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 62.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1441.8331 | 410 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Summer | 43.0167 | 29 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 234.4999 | 210 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 219.0666 | 53 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 38.95 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 454.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 5.425 | 10.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 71.1667 | 14 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 463.8333 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 131472.2499 | 105 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2214.75 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 130.5167 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 148.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 71.75 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 54 | 54 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2.35 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 157.5 | 90 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 556.7 | 114 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 82 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 134.6666 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 14.25 | 45 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 10.65 | 71 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 72.6666 | 109 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4906.6664 | 800 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3681.6 | 416 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 760 | 380 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.41 | 91.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1330 | 190 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 145.8 | 27 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.4167 | 5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.6033 | 91.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 889.3333 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31638.6681 | 124.13 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3164.55 | 867 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 38305.7492 | 1239 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 379.8333 | 53 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1693.71 | 110.7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120 | 40 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298.6666 | 112 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1315.6732 | 326.2 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18960 | 800 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 701.448 | 159.42 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.6583 | 111.19 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 220.9997 | 390 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.8333 | 91 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25968.75 | 625 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79.4667 | 32 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5 | 20 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1514.8331 | 745 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14640.45 | 627 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 486.7661 | 859 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 167.9166 | 155 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.698 | 94.62 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3900 | 325 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.9 | 293 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.1666 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75.7166 | 77 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145 | 29 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 407.75 | 233 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4960 | 310 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 275.48 | 29.1 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 105 | 7 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 999.6 | 285.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 21.7 | 42 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D3-Forced - Postponed | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 150 | 10 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 30.9167 | 18.55 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 46.6666 | 80 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 71.05 | 147 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 78.4 | 147 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 296 | 48 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 19544.0667 | 44 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 11990 | 110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 158.9332 | 298 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 860-Co-generator Block
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 21.3332 | 128 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 860-Co-generator Block
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 1358.5 | 418 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 860-Co-generator Block
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 494.0499 | 144.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 860-Co-generator Block
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.5833 | 85 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 118.3333 | 100 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 973.6665 | 635 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 160 | 40 | 2 | 2 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 525.96 | 43.83 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 834.25 | 235 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 246.75 | 15 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14.3999 | 216 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3350.1331 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24981.3331 | 320 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.28 | 40.4 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1615 | 142.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 153.3333 | 80 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 308.1041 | 147.89 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8.9166 | 107 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2820.5162 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64 | 64 | 2 | 2 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 202.5 | 225 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 717.3333 | 80 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9900 | 660 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 227 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 263.5 | 30 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 945 | 100 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.6666 | 80 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 513.3332 | 400 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5698.7578 | 738.5 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1640 | 80 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 261 | 58 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 19 | 15 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 682 | 33 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 158 | 79 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1203.6666 | 314 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4741.9162 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 70.35 | 63 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 85.5 | 38 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7303.7831 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2624.6665 | 635 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1466.3 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 170.6833 | 104.5 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 174.1666 | 104.5 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4988.25 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 94.5166 | 107 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 858.4998 | 510 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 749.2333 | 247 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4551.7499 | 189 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87.7092 | 169.76 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1386.4165 | 635 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.1166 | 89 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 32.6131 | 177.89 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1260 | 252 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2067.8 | 738.5 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 56 | 40 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 28.5833 | 35 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 849.85 | 739 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1905 | 635 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3014.35 | 361 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 505.9998 | 345 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 496.3333 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 76.1433 | 43.1 | 1 | 1 | 0385-Igniters | U2-Forced - Delayed | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1044.42 | 535.6 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2162.4166 | 192.5 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 782.9665 | 283 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 3531 | 20 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 187.4929 | 274.38 | 1 | 1 | 0385-Igniters | U2-Forced - Delayed | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 919.75 | 283 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 96.033 | 274.38 | 1 | 1 | 0385-Igniters | U2-Forced - Delayed | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 442.68 | 285.6 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 2026.875 | 103.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 328.7067 | 35.6 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | WECC | Winter | 3484 | 268 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 861-CoG GT units
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 666.7153 | 55.87 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4570.3166 | 257 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1293.4166 | 85 | 1 | 1 | 0390-Burner wind boxes and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 393.2 | 98.3 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3686.5 | 146 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 393.75 | 225 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 8175.5833 | 85 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191882.1664 | 415 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7250.4 | 477 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1220 | 100 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2277.9164 | 385 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10162.6666 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 167.75 | 55 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 23.8333 | 110 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 156 | 130 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.5 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1.0833 | 5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 191.6667 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 43.4 | 217 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 81.0833 | 139 | 1 | 1 | 0410-Other burner problems | SF-Startup Failure | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 115 | 230 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2555.2833 | 139 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 203.1666 | 230 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1074.4999 | 210 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 387.1666 | 230 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 938.6 | 247 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18.25 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 129 | 215 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 378 | 280 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 113.6666 | 110 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 247 | 247 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 107.3332 | 230 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 126.5833 | 217 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 828 | 230 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.3333 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7.8333 | 10 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18.0833 | 217 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4740 | 50 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.7333 | 8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3416.82 | 200.4 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 46 | 230 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 201.1666 | 71 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 124.8333 | 70 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2400.1332 | 376 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 47 | 20 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 70.1233 | 19.3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 30.6367 | 14.14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 40.6 | 3 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2515.1 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 40.8 | 102 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 72.75 | 45 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 344.6666 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2681.4667 | 14 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 28.2333 | 22 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3426.1333 | 64 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1352.4 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 11.0833 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 221.4 | 36 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 108 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2.7833 | 1 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 40.5 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 73.5625 | 26.75 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 23.3333 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1.79 | 17.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2.685 | 17.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 18967.5 | 90 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1.4917 | 17.9 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 302.1667 | 7 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 614.4995 | 46.73 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 842.96 | 105.37 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.2 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 345.4333 | 86 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 26.4 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5.95 | 17 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 25.2 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 588 | 24 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29.8667 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 153.6 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 95.6717 | 41.9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1086 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 93.6333 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 308 | 77 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.2 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 71.01 | 23.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6667 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 52.8 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 336.4333 | 2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84.48 | 52.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 198.44 | 32.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4.8333 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12.9166 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 822.25 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 120 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.8 | 71 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 233.1266 | 57.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 105 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8.75 | 15 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18 | 18 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 95.8333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 288 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 259.7 | 42 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2650.6666 | 160 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43 | 10.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 49.1333 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1216.8 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55 | 13.75 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 106 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 881.5 | 86 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 9.8667 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.5 | 54 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 258.78 | 22.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 576.2 | 86 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1954.55 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2713.3333 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 151.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3611 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2324.0167 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 203.06 | 9.23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1208.0833 | 95 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 19.7 | 1 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83 | 16.6 | 1 | 1 | 0415-Cyclone feeders | D3-Forced - Postponed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12 | 12 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161.2 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1773.9575 | 25.05 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25 | 12.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28 | 28 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.3642 | 15.05 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85 | 42.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4235.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 39.1666 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 223.0666 | 56 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65 | 32.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38182.3 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.02 | 24.67 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1561.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7 | 7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.6666 | 80 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 154.4 | 48 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15.9333 | 4 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107 | 10.7 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 759.3333 | 85 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 40 | 10 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.5 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 27 | 60 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 108 | 27 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1794 | 69 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 65 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 23.2 | 24 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 93 | 20 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 10.4 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 51.3333 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106.6666 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 282.2167 | 41 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2602.0833 | 25 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 390 | 40 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 7.4 | 12 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 725.6667 | 7 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 27.8 | 3 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 0 | 0 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3034.5 | 85 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27 | 27 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1746.78 | 83.18 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 209.4167 | 7 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 562.5 | 27 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 39.4333 | 13 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 11.5333 | 2 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 612.5 | 25 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.2 | 44 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24.5833 | 5 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5.7 | 6 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2687.5333 | 28 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 865.8666 | 34 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4900.1 | 38 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9491.4 | 36 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12877.7 | 69 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20394.7333 | 28 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24727.0666 | 68 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25487.5833 | 91 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.2 | 51 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 146.5333 | 62.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 725.7633 | 47.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2824.7199 | 160.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 329.1166 | 49 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43996.833 | 554 | 1 | 1 | 0435-Other cyclone problems | U2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 588.4399 | 112.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 556.5366 | 167.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 849.4 | 62 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28610.4043 | 98.02 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30426 | 99 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.6667 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.7166 | 77.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 319.92 | 13.33 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 32 | 48 | 1 | 2 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 34 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 135 | 45 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 46.3333 | 27.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5339.7 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 33.15 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 36.55 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 89.3 | 38 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1.3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 27.8667 | 38 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1623.1599 | 142.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22021.2333 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1023.75 | 455 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.3633 | 87.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 142.56 | 52.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 299.53 | 77.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 35.2 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 23.4667 | 8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12872.5333 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42.98 | 6.14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1351.7667 | 42.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.9466 | 32.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13 | 3.25 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 381.04 | 52.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6079.06 | 267.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2646.6 | 132 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33465 | 230 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.9667 | 47 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1755.1933 | 57.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 97.0666 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 543.95 | 23 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2.5 | 6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 217.75 | 65 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24 | 12 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 22.1 | 51 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4380.3333 | 34 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 37.6 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 18.6 | 12 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 79.6666 | 47.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 890.6 | 24.4 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2025.4667 | 44 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2881.35 | 19 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 7690 | 769 | 1 | 1 | 0435-Other cyclone problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 26.65 | 39 | 1 | 1 | 0435-Other cyclone problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 2975.7932 | 375.1 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 168.3333 | 100 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 750 | 100 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 14443 | 202 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5694 | 876 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1180 | 118 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 299.6666 | 62 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 221 | 260 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 507.3998 | 258 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 851-CC GT units
0440 | Fuel oil pumps (general) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 643.0998 | 327 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 852-CC steam units
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 0.91666 | 5 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 11 | 110 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 125.5997 | 471 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 121.333 | 455 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1.25 | 5 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 2144.9663 | 562 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 249.6 | 208 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 703.6165 | 259 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 851-CC GT units
0441 | Fuel oil pumps (burner supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 518.8832 | 191 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 852-CC steam units
0442 | Fuel oil pumps (forwarding/transfer) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 1485.495 | 300.1 | 1 | 1 | 0442-Fuel oil pumps (forwarding/transfer) | D1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 1220.5333 | 184 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 861-CoG GT units
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Summer | 668.0999 | 153 | 1 | 1 | 0460-Fuel oil atomizers | U1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 619.6666 | 52 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 392.3666 | 149 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 89.25 | 255 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 207.6 | 12 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 667 | 60 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82528.3329 | 650 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 18.2 | 12 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1495.2833 | 73 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2830 | 60 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 769.8 | 12 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 57.4 | 12 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3972 | 60 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1172.64 | 558.4 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 12931.4367 | 43.1 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1300 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 350.3 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 73.3833 | 17 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 170.3332 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 24.3332 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 235.5666 | 95.5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1924.7666 | 73 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8271.96 | 713.1 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 177.9166 | 175 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 852.5 | 155 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 14 | 28 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 48.4 | 44 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 201.5 | 130 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 219.3332 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 41002 | 494 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1659.3331 | 380 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 193.4833 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 591.9998 | 480 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 359.4 | 36 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1.5 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 5400 | 45 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1306.5999 | 417 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 349.333 | 524 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1330.4166 | 155 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U3-Forced - Postponed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 79.9 | 102 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 82.5 | 330 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1512.5333 | 64 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1499.5 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 168.6666 | 230 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1659.2 | 51 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 93 | 155 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 638.0833 | 95 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36076.5332 | 472 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 91.8333 | 19 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 94.4666 | 52 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 309.5164 | 379 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 116.2164 | 367 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1668.6 | 412 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3282.9333 | 208 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 214.65 | 53 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 176.6998 | 342 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1169 | 28 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 518.7 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 18905.3663 | 333.33 | 3 | 3 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 138.8333 | 14 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 326.6665 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | DI | 100 | Fossil-Steam | RFC | Summer | 90 | 90 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 12140.3666 | 251.18 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 220662.7998 | 474 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 189.8 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 3999.96 | 333.33 | 3 | 3 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3500 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 85.25 | 55 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1741.3329 | 653 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 230.5333 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 235.0832 | 155 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 35.5333 | 82 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 135.2 | 52 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1215.6667 | 35 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 65.8 | 42 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 124 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 251 | 60 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116 | 116 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 176.25 | 235 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6795.8333 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 340 | 75 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 344.65 | 113 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23294.1666 | 50 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 72.7666 | 118 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 207.8333 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1894 | 120 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 317.46 | 8.58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 200 | 5 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 650-Fluidized Bed
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1692.9417 | 22.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 180 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 533.8667 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 800-Miscellaneous
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 75.2333 | 61 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 612 | 68 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 4657.9333 | 109 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 4587.2833 | 153.25 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 587.7329 | 608 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 5356 | 52 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 1991.5164 | 361 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 80.8467 | 18.1 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 755.4166 | 185 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 348.9664 | 361 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1400 | 175 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | SF-Startup Failure | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 1305.6164 | 361 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 50.4733 | 11.3 | 2 | 2 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 78.6133 | 17.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 851-CC GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 391.4997 | 405 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 396.236 | 58.27 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D2-Forced - Delayed | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 377.8799 | 84.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 391.2799 | 87.6 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 5 | 30 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D3-Forced - Postponed | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 1464.7497 | 405 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 861 | CoG GT units | TRE | Winter | 33266.1333 | 104 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 861-CoG GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Winter | 691.6 | 104 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 861-CoG GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2022 | Gas | GG | 861 | CoG GT units | TRE | Winter | 6360.6666 | 94 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U2-Forced - Delayed | 861-CoG GT units
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 385.7 | 58 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 862-CoG steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12831 | 611 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5937.033 | 554 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44552.5 | 710 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30372.5329 | 614 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92157.4165 | 637.4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6516.9 | 234 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 44.4 | 74 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2862.6665 | 190 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3441.75 | 195 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81613.9994 | 876 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49297.6664 | 710 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 411025.86 | 637.2 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13440 | 800 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | SF-Startup Failure | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38512.3329 | 620 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 408957.36 | 637.8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21640.6831 | 703 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114126.6664 | 680 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280.5 | 110 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46463.25 | 615 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3456 | 480 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4649.0833 | 237.4 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5967.5 | 770 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7172.7499 | 195 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32596.6664 | 770 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 250 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 768.2639 | 193.68 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2496 | 195 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 126.6 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 650-Fluidized Bed
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 5178.4864 | 374.8 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D3-Forced - Postponed | 650-Fluidized Bed
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1470 | 18 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 650-Fluidized Bed
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 11.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 4.5 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 9.9 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6293 | 310 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 1422 | 180 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 111.65 | 203 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 233.1 | 126 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 750.5 | 95 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 111.925 | 60.5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1518.9332 | 256 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 433.4662 | 650.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1688.4666 | 76 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6439.2333 | 170.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 297.9164 | 325 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9593.3099 | 160.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.6 | 78 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.725 | 142.9 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 303.5233 | 170.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2827.3066 | 91.4 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 612.5 | 30 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21408.6664 | 680 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5377.5 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3717.35 | 39 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 455 | 42 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1588.0666 | 287 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 74.8 | 102 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1347.0999 | 114 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 500.5 | 100.1 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 409.9999 | 120 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.5 | 650 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 378.5666 | 82 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.4 | 127.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 392.4666 | 116 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 200.2 | 100.1 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3665.9999 | 180 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 450 | 180 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.6665 | 650 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129708.3666 | 140.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 49.2 | 82 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12547.75 | 265 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11625.1666 | 170 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17726.5498 | 531 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.4466 | 140.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1386.6666 | 160 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.9333 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.3332 | 140 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1204.1666 | 170 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 18612 | 440 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.8 | 32 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 981.9333 | 52 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55.2 | 46 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2599.9997 | 390 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84 | 60 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26134.6664 | 680 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 6976.6666 | 100 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 650-Fluidized Bed
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 531.3165 | 449 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 896.4998 | 489 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 259 | 60 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 81.75 | 109 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 204.25 | 129 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 488.8331 | 419 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 834.1 | 439 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 159.5 | 319 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 214.5 | 429 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1012.5831 | 419 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4324.5 | 279 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 147 | 294 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 32.25 | 129 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 662.4999 | 150 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 279.3331 | 419 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 57332.5499 | 99 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 39.1667 | 2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 830-Geothermal
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 11571.525 | 195.3 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 8429.64 | 159.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 671.5333 | 28 | 2 | 2 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 745.7166 | 101 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 839.4167 | 35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 285 | 50 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4903.55 | 101 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6720.6497 | 417 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 328.8561 | 334.43 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3753.9166 | 107 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 226.3333 | 14 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.7333 | 16 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6318.7664 | 418 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 667.7667 | 23 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | RFC | Winter | 1927.3333 | 20 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20822.0831 | 275 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2695.35 | 51 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10681.9496 | 531 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 3.5 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68105.9165 | 455 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88476.8498 | 720.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315 | 630 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 490.45 | 51 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47960 | 800 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21050 | 842 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6779.7999 | 327 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3088.2 | 514.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 391 | 460 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3019.5 | 330 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 650 | Fluidized Bed | TRE | Winter | 24433.5 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 650 | Fluidized Bed | TRE | Winter | 2606.5 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2645.3332 | 310 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 7971.9662 | 769 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 69161 | 713 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 192236.6829 | 713 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 5249.1481 | 633.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 85473.1665 | 485 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 4899.7665 | 322 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 630.3333 | 244 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2749.9498 | 243 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6646.0664 | 761 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 339.5 | 485 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 307.1 | 74 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2556.4 | 166 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 783.4133 | 158.8 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 195.3 | 195.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 1014 | 84.5 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 538.3333 | 10 | 2 | 2 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 543.9332 | 164 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 420.5 | 145 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2044.1399 | 195.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 2141.4 | 172 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 305.8666 | 74 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 19165.3716 | 200.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 15041.9666 | 179 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 564 | 47 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 380.3999 | 285.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 937.9 | 113 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 615.1166 | 221 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 321.9 | 111 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1863.4 | 121 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 262.4666 | 62 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2462.5 | 75 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8769.4662 | 739 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1990.6868 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 3990.9391 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1731.7333 | 68 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25193.7 | 387 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15737.3331 | 290 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1950.2991 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 23.3823 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 48.8903 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.9167 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 233.8233 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 780.1196 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 3950.5515 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 262.5198 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 613.5 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1249.9999 | 120 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25191.8328 | 770 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 509.0971 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 82.901 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1946.583 | 497 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 95.655 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104000 | 650 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 790.6933 | 79.6 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14.85 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 280.588 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 646.2026 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 281.6508 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 110.5346 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16524 | 405 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7505 | 395 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 743.9833 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63156.75 | 535 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 93.5293 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 100.9691 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 594.1238 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 37.1991 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 116.9116 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44537.0662 | 739 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 645.0497 | 399 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2030 | 70 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2209.3062 | 637.3 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 306.096 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 153.048 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 555.8618 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 724.5 | 21 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17883.8 | 739 | 1 | 1 | 0530-Other main steam system problems | SF-Startup Failure | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 767.3656 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 69.0841 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 973 | 35 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 193.4356 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1052.205 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1084.09 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.0667 | 11 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 683.0333 | 31 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 748.71 | 35.4 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 127.54 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 573.93 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1026.6666 | 200 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1225.4166 | 85 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 59.4167 | 23 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 830-Geothermal
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1250.5917 | 51.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 73.7917 | 11.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 715.85 | 51.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1872.8833 | 51.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 119.7 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 142.5 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 525.5083 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 117.1667 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 970.2667 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 93.4167 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 101.4917 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 103.3917 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 123.025 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 541.8167 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1426.0332 | 358 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 79.8 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 145.0333 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 145.9833 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 172.7417 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 102.6 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 154.5333 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 16874.4915 | 206.5 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 112.4167 | 9.5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 306.6665 | 184 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 34040 | 230 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 249.6666 | 107 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 790.5 | 62 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 17179.6 | 116 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Summer | 11960.9999 | 162 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 861-CoG GT units
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Summer | 11186.1 | 162 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 861-CoG GT units
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 13116.6999 | 174 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 862-CoG steam units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160333.5663 | 526 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 249062.0595 | 713.1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11228.0831 | 335 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2009 | 98 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 2282.939 | 404.06 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 800-Miscellaneous
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 24090.3 | 261 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 800-Miscellaneous
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 66.3 | 78 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2442.8948 | 598.26 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 24589.5 | 485 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2763.75 | 335 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 22.75 | 91 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3273 | 12 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 28183.5466 | 164.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 908.9666 | 74 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 62.1 | 138 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 198 | 180 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 552.05 | 181 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 13.95 | 46.5 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 7888.8 | 173 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 356.85 | 117 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 306.5332 | 152 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 575.4742 | 46.85 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1159.398 | 282.78 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | SF-Startup Failure | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 9481.5 | 90 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2885.9999 | 90 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 8.025 | 26.75 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1480.2666 | 112 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192380.1664 | 415 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | SF-Startup Failure | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 40054.24 | 222.4 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 27834.84 | 156.2 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 31441.1199 | 177.6 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 103.5 | 230 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 6076.5208 | 171.25 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 5593.6506 | 171.76 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 28812.0666 | 166 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 1657.2333 | 166 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 455.7 | 217 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 4152.5999 | 162 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 3843.4666 | 284 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 215.8332 | 259 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 2034.5 | 130 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 23436 | 135 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 208.95 | 99.5 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 2585.6832 | 259 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 9143.7001 | 257.69 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 852-CC steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 25.0832 | 215 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 47.2 | 48 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 161.5833 | 35 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 2311.6166 | 227 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 297.2499 | 123 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 8.75 | 105 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10.6666 | 80 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 418.7166 | 97 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 13.75 | 55 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 35.7 | 42 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 80.5 | 230 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 919.35 | 227 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9520.55 | 151 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 130.5333 | 44 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 114.6666 | 40 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9.8 | 42 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 240 | 50 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 92.5 | 50 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 65 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.4 | 66 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 16 | 20 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 242.3166 | 67 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 7.8 | 39 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9.5 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 47.9999 | 180 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 600.4167 | 25 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 800-Miscellaneous
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 104148.2331 | 769 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 66.0333 | 56.6 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1809.3666 | 103 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 5.3816 | 32.29 | 3 | 3 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1831.832 | 77.62 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 694.5 | 18 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3414.4 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3282.4 | 176 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 179.6666 | 245 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 3.1815 | 27.27 | 3 | 3 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 3.96 | 29.7 | 3 | 3 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 11100 | 250 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 617.3333 | 16 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1125 | 250 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 506.3332 | 245 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1803.6945 | 76.59 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 13066.6666 | 245 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1087.815 | 46.29 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 1061.6666 | 100 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 501.5833 | 13 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 465.0665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 5.3333 | 40 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 120552.25 | 65 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 657.0665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 7551.9166 | 65 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 16191.5 | 65 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 580.2665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 4.4333 | 38 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 7.5 | 45 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 19639.75 | 65 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 448 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 12113.0665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 852-CC steam units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1399.4665 | 256 | 1 | 1 | 0550-Reheat steam relief/safety valves | SF-Startup Failure | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.225 | 28.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 128.6332 | 227 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 25444.5999 | 174 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 15.1332 | 227 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 359.1249 | 127.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 23213.7497 | 525 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 650-Fluidized Bed
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 387.2 | 242 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 800-Miscellaneous
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 39382 | 388 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 6842 | 622 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 495.0832 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 479.85 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 974.9332 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1248.8381 | 663.1 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1024.8331 | 559 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1363.3832 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 137.1 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 144.7164 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1553.8 | 457 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 129.1666 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 517.3666 | 166 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 12402.5832 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1745.8 | 203 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 834.1333 | 184 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 569.5 | 170 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 201.5 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 66.8 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 918 | 153 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 28069.0666 | 176 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 110.5 | 170 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 4516.2916 | 267.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 32.25 | 215 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 14081.3332 | 147.5 | 2 | 2 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 157.25 | 185 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 712.8332 | 182 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 39501.75 | 93 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 455.6 | 136 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 824.1499 | 159 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 468.0416 | 119.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 913.75 | 129 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2329.35 | 159 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1109.4 | 129 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 612 | 135 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 900.5833 | 101 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 96510 | 75 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 31503.9998 | 330 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 5843.25 | 159 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 209.9999 | 180 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 20413.8666 | 128 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2062.5 | 75 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4910.9999 | 90 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15512.5 | 850 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 438.5665 | 223 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 66.9 | 223 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2683.1329 | 668 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 647.0331 | 413 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1972.7164 | 457 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 55.11 | 183.7 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 366.3333 | 157 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | SF-Startup Failure | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 651.8165 | 259 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 992.3332 | 260 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 4085.6666 | 170 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U2-Forced - Delayed | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 6179 | 167 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 419.25 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 573.3332 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 346.0666 | 179 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 378.8832 | 179 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 568.0166 | 173 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 874.3332 | 215 | 1 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 702.3332 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 273.7 | 161 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 5635.5 | 221 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 967.5 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 55.3636 | 81.02 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 502.2 | 186 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 557.1333 | 244 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 553.0665 | 244 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 708.75 | 157.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1359.5165 | 271 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 166.25 | 133 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 254.6664 | 382 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 206.25 | 75 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 185.6 | 96 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 3268.5333 | 136 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D2-Forced - Delayed | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 457.3 | 269 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 1370.4665 | 244 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 71.4766 | 104.6 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 103.6 | 148 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 172.3333 | 235 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 9.8666 | 148 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 1195.6 | 244 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 532.8 | 148 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 14992.4 | 148 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 49562.0666 | 169 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 861-CoG GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 54022.5 | 175 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 862-CoG steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.5 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 180.6667 | 20 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1049.8333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 991 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18 | 3 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 14.5332 | 218 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4245 | 100 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55.25 | 2.21 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1066.1667 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 378.6666 | 80 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46.97 | 4.27 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3859.8333 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8 | 1.6 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34 | 30 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 391 | 85 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64 | 32 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 642 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 72.6666 | 218 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1 | 1 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1054 | 210.8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6081.2737 | 390.66 | 1 | 1 | 0570-Other reheat steam problems | U3-Forced - Postponed | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2 | 2 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Summer | 1350.9 | 237 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 800-Miscellaneous
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2216.15 | 349 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 30617.1666 | 338 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2800.23 | 27.9 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 13901.2371 | 262.37 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 62.79 | 209.3 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 324.7066 | 137.2 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 8.235 | 164.7 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 9209.3666 | 173 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 283.86 | 149.4 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 1403.85 | 191 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 100.5482 | 140.3 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 35.2263 | 34.09 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 360.1032 | 140.3 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1054.6666 | 113 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 526.9332 | 152 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 850.6666 | 110 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 14609.65 | 101 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 2335.3333 | 113 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 4599.36 | 86.4 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1432.95 | 41 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53201.4997 | 510 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 885 | 15 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1317.0833 | 145 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3515.9666 | 86 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.5 | 267 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 466.5 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 0 | 0 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25048.5082 | 345.1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2037.3331 | 320 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 22196.9166 | 185 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2895.7498 | 243 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53.3498 | 320.1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6520.2666 | 49 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.25 | 45 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1633.35 | 9 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2353.8331 | 290 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15721.775 | 558.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30238.5494 | 849 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29224.75 | 841 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34349.4665 | 494 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27211.6663 | 580 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 607.5 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 2431 | 170 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1283.8 | 262 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13651.4994 | 855 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21365.5 | 494 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 104.9999 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 15347.25 | 855 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15894.5 | 415 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1941.14 | 273.4 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.2791 | 27.07 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.25 | 45 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 304.5 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82665.9165 | 455 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 717.5 | 287 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11716.125 | 298.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3326.5333 | 244 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 39.6 | 54 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2102.0999 | 117 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20720.9332 | 149 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 39.75 | 53 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22250 | 625 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.4999 | 90 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1611.1699 | 320.1 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7521 | 690 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 6728.1499 | 429 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3104.1665 | 298 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 5181 | 99 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 50618.7496 | 525 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 14055.2166 | 69.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 200.2 | 39 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 5736.58 | 116.4 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1358.9866 | 66.4 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | D1-Forced - Immediate | 100-Fossil-Steam
0600 | Desuperheater/attemperator spray nozzles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3509 | 290 | 1 | 1 | 0600-Desuperheater/attemperator spray nozzles | U1-Forced - Immediate | 100-Fossil-Steam
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 352.8606 | 63.77 | 1 | 1 | 0610-Desuperheater/attemperator drums | U1-Forced - Immediate | 100-Fossil-Steam
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468.1299 | 101.4 | 1 | 1 | 0610-Desuperheater/attemperator drums | D1-Forced - Immediate | 100-Fossil-Steam
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 95.655 | 63.77 | 1 | 1 | 0610-Desuperheater/attemperator drums | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69 | 60 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 396 | 135 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 20 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.3333 | 50 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10.5 | 35 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8865.3332 | 436 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.6666 | 40 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4226.025 | 84.1 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6021.1665 | 455 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16259.9 | 554 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2521.8 | 467 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.64 | 38.08 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 223.75 | 179 | 1 | 1 | 0640-Startup bypass system valves | D2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1521.6667 | 44 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2535 | 130 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58052.7047 | 770.1 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8106.8329 | 635 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3470.3498 | 741 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19650 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 16237.5 | 750 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11330.4997 | 465 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 37522.7997 | 756 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31461.1 | 773 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 345015.2498 | 705 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4656.1665 | 455 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3619.9998 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6889.75 | 635 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10325.2795 | 790.2 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101520 | 705 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7895.9998 | 630 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10959.9996 | 600 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17118.5 | 511 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 17791.6665 | 244 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 650-Fluidized Bed
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 34054.2665 | 244 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 650-Fluidized Bed
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27876.3178 | 814.7 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4927.0831 | 625 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 100-Fossil-Steam
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 100.3 | 102 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 650-Fluidized Bed
0655 | Steam by-pass system instrumentation and controls | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 380.8 | 102 | 1 | 1 | 0655-Steam by-pass system instrumentation and controls | U1-Forced - Immediate | 650-Fluidized Bed
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1422 | 360 | 1 | 1 | 0660-Other startup bypass system problems | D1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29596.6658 | 1300 | 1 | 1 | 0660-Other startup bypass system problems | U1-Forced - Immediate | 100-Fossil-Steam
0660 | Other startup bypass system problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 12011.3331 | 419 | 1 | 1 | 0660-Other startup bypass system problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 912.4333 | 62 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.0833 | 25 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.9333 | 44 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2333.3333 | 80 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24514.6663 | 580 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 27.45 | 27 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 733.92 | 152.9 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 430.3833 | 217 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1455 | 485 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 417.8333 | 109 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1969.4845 | 271.03 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 850-Combined Cycle Block
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 727.0499 | 166.5 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 93.75 | 75 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2175 | 75 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1890.1 | 82 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1212.2333 | 82 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1256.1833 | 113 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Summer | 10258.7333 | 178 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 861-CoG GT units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1738.0079 | 129.06 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 765 | 300 | 2 | 2 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34 | 17 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4162.6666 | 80 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44 | 22 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.4 | 6.6 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154.1666 | 37 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21035 | 601 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7263.5329 | 1156 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14874.9998 | 750 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 192.5 | 3.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 399.9998 | 240 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 241.5833 | 65 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 8937.4995 | 750 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 286.965 | 63.77 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 366 | 73.2 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1073.3332 | 140 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2876 | 40 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1125.8997 | 486 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 230.7066 | 106.48 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 800-Miscellaneous
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 86.5167 | 29 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 800-Miscellaneous
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3283 | 469 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5690.6 | 769 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 4320 | 360 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 101.9625 | 135.95 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 7873.5 | 543 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D3-Forced - Postponed | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1645.2 | 457 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1438.6898 | 270.6 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 629.8 | 134 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 775.5 | 165 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1489.2799 | 279.24 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 300.9 | 118 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 5.9 | 118 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | SF-Startup Failure | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 17647.7667 | 41 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 49.1909 | 155.34 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 75.5594 | 156.33 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1214.5831 | 275 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 4694.9999 | 225 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 19.6 | 42 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1928.5 | 145 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 17.2666 | 37 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 16151.9282 | 272.3 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 162.4999 | 195 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 915.0165 | 217 | 2 | 2 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 9353.3231 | 224.39 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 143.65 | 169 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1955.1 | 147 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 644.8332 | 146 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 71.3786 | 147.68 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 182.4665 | 238 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 6346.7043 | 152.26 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 303.6 | 72 | 2 | 2 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 7269.8816 | 157.3 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 169 | 65 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 212.4 | 236 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 19.8333 | 23.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1968.4 | 148 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 100.4999 | 90 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 32.06 | 68.7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 60336.6666 | 50 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 64 | 76.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 134.3 | 158 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | MRO | Off-Peak | 13603 | 244 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 860-Co-generator Block
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 973.75 | 19 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 915.6665 | 268 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4849.4997 | 477 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77 | 21 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4004 | 520 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3051.5 | 10 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 199.3333 | 46 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 925.2 | 18 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1190.4 | 248 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11552.5 | 10 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5315.4666 | 248 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2975.5999 | 258 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 779.8333 | 10 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34297.2 | 252 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 563.3333 | 20 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2165.3333 | 29 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12620.3 | 298 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 102 | 34 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 800-Miscellaneous
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 990.1332 | 188 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 14329 | 178 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 8633.3333 | 175 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4263 | 87 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 937.0833 | 65 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15587.6665 | 404 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.6666 | 175 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24069.5 | 529 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.2999 | 174 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154161.3997 | 876 | 1 | 1 | 0700-Blowdown system valves A | U2-Forced - Delayed | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 56.4667 | 22 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 454.4983 | 114.1 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1333.53 | 269.4 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 228.2 | 114.1 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 32.3283 | 114.1 | 2 | 2 | 0700-Blowdown system valves A | D1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 75.8333 | 91 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 506 | 88 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 206.25 | 125 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 850-Combined Cycle Block
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Summer | 926.8333 | 166 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 288.75 | 175 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 156.2282 | 191.3 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4783.35 | 223 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 78.87 | 47.8 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10268.75 | 155 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9226.7998 | 297 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9564.6589 | 390.66 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 5576.6665 | 175 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9624 | 401 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2821.5 | 190 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16897.3331 | 380 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 13092.3332 | 310 | 1 | 1 | 0710-Blowdown system piping B | D2-Forced - Delayed | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 63010.5331 | 808 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 850-Combined Cycle Block
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 3018.6 | 156 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 6488.4166 | 227 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 3695.2 | 149 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U3 | Forced - Postponed | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 2469.9999 | 156 | 1 | 1 | 0710-Blowdown system piping B | U3-Forced - Postponed | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 4357.3832 | 221 | 2 | 2 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 8499.5999 | 162 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D3 | Forced - Postponed | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 4018 | 287 | 1 | 1 | 0710-Blowdown system piping B | D3-Forced - Postponed | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 1698.7333 | 83 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Winter | 2523.7332 | 128 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Winter | 2563.1666 | 130 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 3718.1332 | 146 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 852-CC steam units
0730 | Other blowdown system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6310.5664 | 394 | 1 | 1 | 0730-Other blowdown system problems | SF-Startup Failure | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 132129.9997 | 876 | 1 | 1 | 0730-Other blowdown system problems | U3-Forced - Postponed | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2808 | 160 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 59601.5365 | 466.67 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3599.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 41378.1503 | 86.78 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111869.3333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1534.1666 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22975.1662 | 658 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13865 | 235 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4060 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 100759.1666 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156174.75 | 765 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25920 | 480 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14023.3333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77083.5 | 295 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1419.3333 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19708.5 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 267.6665 | 292 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2450.8331 | 850 | 1 | 1 | 0740-Boiler recirculation pumps | SF-Startup Failure | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10197.8333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 60784 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2475 | 495 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 329086.3331 | 380 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3719.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3719.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2628.5 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1248.6398 | 585.3 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3604.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 384 | 384 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3220 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46105.5 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23324.65 | 613 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1375 | 500 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9833.9998 | 360 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12320 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5424 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 391635.348 | 306.78 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3153.8329 | 635 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1048.0567 | 22.9 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47172 | 240 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.6666 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1196.7667 | 7 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 356184 | 97 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1500 | 400 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3147.8333 | 85 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3730.025 | 6.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 8458.6231 | 368.3 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6048 | 480 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 788.1417 | 22.9 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 13.8168 | 63.77 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 21540.2481 | 326.78 | 1 | 1 | 0740-Boiler recirculation pumps | U3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102.2666 | 52 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1602.2499 | 255 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54079.9999 | 384 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1332 | 72 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2534.5 | 30 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4111.3333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6984 | 97 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 192.5 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3983.3332 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 525 | 500 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5385.6667 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2175.8333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1374.75 | 135 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58083.3333 | 85 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 133.0626 | 86.78 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5785.65 | 6.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 64400 | 115 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3555.11 | 6.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 648 | 432 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 320.9756 | 63.77 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39142.5 | 255 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 49647.5 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 875 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1888.8333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6018.8333 | 70 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 5445.3333 | 160 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 0740-Boiler recirculation pumps | D3-Forced - Postponed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31294.9999 | 330 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 714 | 280 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 852-CC steam units
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73469.6666 | 230 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19768.5 | 414 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 124378.7066 | 103.6 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 171386.3333 | 190 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 8.9999 | 135 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 10.5 | 105 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38595.15 | 339 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2.3332 | 140 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 313334.5 | 370 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5788.6665 | 380 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206848.2032 | 124.7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50883.5 | 149 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3253.4333 | 19 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D3-Forced - Postponed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 138877.05 | 229 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2011.3333 | 20 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5909.6333 | 19 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 7 | 30 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 44 | 40 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 12 | 80 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2 | 40 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9 | 60 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 19137.3333 | 20 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6556.2499 | 375 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2520.4997 | 426 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15029 | 380 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 8472.3333 | 35 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 852-CC steam units
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.6666 | 160 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 542.6333 | 223 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 678.7165 | 211 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1560 | 480 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.8 | 144 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4926.6662 | 739 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | SF-Startup Failure | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4839.1 | 446 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16352.5 | 155 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 15916.9333 | 244 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D2-Forced - Delayed | 860-Co-generator Block
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 17751 | 244 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D2-Forced - Delayed | 860-Co-generator Block
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 480 | 160 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1097.08 | 274.27 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 679.4998 | 270 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6953.9166 | 245 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 444.8332 | 170 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 414 | 552 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13810.0665 | 404 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1011.8333 | 130 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24780.9501 | 814.27 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2467.0195 | 314.27 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8647.4997 | 450 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4642.1 | 761 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2386.6666 | 160 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 51472.9166 | 125 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10935.4166 | 125 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10322 | 520 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1772.4 | 422 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43073.333 | 455 | 1 | 1 | 0760-Boiler recirculation valves | U2-Forced - Delayed | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15995.2764 | 814.7 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6056.1667 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40898.5999 | 204 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3978.6666 | 64 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21008.5999 | 204 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1373.6667 | 20 | 1 | 1 | 0770-Other boiler recirculation problems | D2-Forced - Delayed | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5429.25 | 855 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52120 | 400 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1547.6333 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1287.6 | 24 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9648.1 | 179 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8444.3167 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18.9 | 54 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.05 | 39 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.2333 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1150.8167 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.9333 | 64 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 380.1 | 21 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4862.3333 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1653.9667 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.0666 | 64 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6482.1666 | 89 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7589.9331 | 362 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1602.7333 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 567.4333 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 628.9333 | 89 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1127.5333 | 26 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.5167 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 143.55 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3906.7833 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 70 | 280 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4833.3333 | 29 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 788.55 | 21 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 7.6666 | 230 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 52 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 104 | 13 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49475.7998 | 516 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8415 | 306 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57066.6665 | 500 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2946.5333 | 196 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 12449.6999 | 243 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1457.8666 | 112 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 299.5667 | 22 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 30368 | 292 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 130791.6665 | 500 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22191.9497 | 471 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12457.4332 | 406 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 609 | 21 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 807.45 | 21 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 554.3 | 23 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 278.25 | 21 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 35.7 | 21 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 902.2833 | 43 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 800-Miscellaneous
0775 | Economizer piping | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 4200.5329 | 704 | 1 | 1 | 0775-Economizer piping | SF-Startup Failure | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 54219.7329 | 704 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 29374.833 | 485 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 9182.6 | 98 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 5871.732 | 274.38 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 1427.4999 | 150 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 879.75 | 153 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4590 | 170 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11098.2666 | 161 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1688.75 | 175 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 7650 | 150 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 852-CC steam units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 961 | 155 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 852-CC steam units
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 187.0833 | 25 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 3315 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 3060 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 4335 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 14.8796 | 63.77 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6421.6531 | 336.8 | 1 | 1 | 0782-Headers and caps | SF-Startup Failure | 100-Fossil-Steam
0782 | Headers and caps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 772.875 | 22.9 | 1 | 1 | 0782-Headers and caps | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 531849.9991 | 1320 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1855.3333 | 220 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3156 | 120 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 39846.6666 | 200 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 851-CC GT units
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 14344.8 | 72 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22028.9333 | 104 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4609.4664 | 764 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3480.5333 | 208 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11873.7496 | 525 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7613.9999 | 243 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 744.95 | 317 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11000.5832 | 505 | 1 | 1 | 0799-Other miscellaneous piping system problems | SF-Startup Failure | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 28 | 48 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 787.5 | 315 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 40965.75 | 315 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 882 | 315 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1487.4998 | 525 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 650-Fluidized Bed
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | MRO | Summer | 1008945.4999 | 213 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 19261.3665 | 262 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1755.9166 | 95 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 4724.9982 | 254.26 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 8665.5833 | 95 | 1 | 1 | 0799-Other miscellaneous piping system problems | D2-Forced - Delayed | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 295.1667 | 35 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 3455.4666 | 248 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 9707.9999 | 180 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 119.5999 | 156 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 29.1666 | 175 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 185.9999 | 180 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 7491.1382 | 167.9 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 764.4 | 156 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 401.7432 | 189.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2151.2666 | 122 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 735 | 150 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 852-CC steam units
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Winter | 208.1667 | 2 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 860-Co-generator Block
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 168.2333 | 49 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3056.4467 | 14.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2829 | 690 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3124.2998 | 471 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 802.9999 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1561.0954 | 333.33 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17521.25 | 535 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21349.6667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11107.7659 | 390.66 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1122 | 510 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 881.5253 | 77.44 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.0017 | 19.1 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 887.9333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 951.2667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1965.8667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 324.4999 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 722.2148 | 333.33 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1475.1165 | 206.31 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4960.9998 | 363 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 909.85 | 587 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7419.975 | 77.9 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 429 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9030.7 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1024.7333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4407.9665 | 446 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 142.3333 | 244 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12748.1665 | 446 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 384.75 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8086.8329 | 605 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 618.7499 | 297 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 523.7333 | 64 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1107.0667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 802.9999 | 330 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2022 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1034 | 47 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1297.3833 | 241 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1627.7166 | 127 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 840.4583 | 87.7 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 389.1999 | 168 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 29.5832 | 355 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 45.1133 | 26.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 8919.7675 | 431.95 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 139.425 | 19.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 1003.5458 | 124.15 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3192.9331 | 622 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 4849.4526 | 322.58 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 417.9998 | 570 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3937.955 | 190.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 687.083 | 485 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 166.5366 | 106.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 796.8329 | 683 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 126.8749 | 217.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 121.5999 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 187.6 | 268 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 307.1665 | 485 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 1059.1665 | 205 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 529.4216 | 197.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 63.6 | 106 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 261.0833 | 241 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1990.9996 | 543 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 3.9665 | 238 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 23.0067 | 47.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 127.0833 | 61 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 161.4137 | 440.22 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 104.8 | 262 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 150.3333 | 205 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 14577.75 | 171 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 51.925 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 65.3399 | 178.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 264.8333 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2600.7449 | 195.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 305.0833 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 41.85 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 48.895 | 38.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 7903.3999 | 258 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2930.0782 | 191.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 1364.2649 | 164.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 245.1 | 258 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 108.5 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 199.4666 | 272 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 215.4166 | 275 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 569.9333 | 166 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 233.8332 | 140.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 19721.2999 | 183 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 76.2666 | 176 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 22.225 | 38.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 667.8 | 159 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 54.1666 | 62.5 | 2 | 2 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 27.9166 | 67 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 253.1732 | 161.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 282.1 | 182 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 421.6332 | 182 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 561.05 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 170 | 136 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11.625 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 250.8333 | 175 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 867.1435 | 219.53 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13.4167 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 12177.8997 | 378 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1333 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 106.1667 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Winter | 141.2165 | 229 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 358.8 | 138 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 1956.5666 | 79 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 7781.6666 | 161 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 36010.7997 | 378 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 16.35 | 27.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 30.225 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 99.7332 | 176 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 447.6 | 72 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 751.8 | 179 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 54.25 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 65.875 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 253.82 | 137.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 1823.5833 | 79 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4155.7599 | 172.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 1287.4666 | 71 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 198.9 | 265.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3651.4166 | 215 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 83.85 | 129 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 25.075 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 66.3 | 265.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 18.3833 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 543.3331 | 326 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 786.6666 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2377.5833 | 103 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 41.9249 | 193.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 64.05 | 27.45 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 471.2 | 48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Gas | GG | 852 | CC steam units | WECC | Winter | 3250.8665 | 286 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 160.55 | 169 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 56.6666 | 100 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 24.075 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 37.8958 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 1354.9998 | 300 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3.3333 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 531.4332 | 149 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6.375 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 31.2083 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 6.6667 | 20 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 66.2999 | 234 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 184.9998 | 300 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 114.3666 | 146 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 10206.1666 | 209 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 285.9666 | 46 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 27.996 | 46.66 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 176.7998 | 265.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 25.7366 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 150 | 120 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 598.4 | 33 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 9806.7666 | 91 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D2-Forced - Delayed | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 23.79 | 27.45 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 1021.65 | 417 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 106.75 | 305 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 234 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 17.8425 | 27.45 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 231 | 210 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4.0125 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 85.9999 | 129 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 395.5833 | 235 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 1550.8333 | 50 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1621.55 | 113 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 42.9 | 99 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 368.1125 | 150.25 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 81.6998 | 258 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 4904.5332 | 209 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 5177.0333 | 169 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 36.7666 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 237.0865 | 233.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 464.1332 | 236 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 2268.5333 | 94 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 108.4999 | 210 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 29.8708 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 31.2516 | 110.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 7580 | 379 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | SERC | Winter | 4042.2666 | 142 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Summer | 1204.5 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 862 | CoG steam units | SERC | Winter | 2520 | 120 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 52.5166 | 137 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 717.0233 | 85.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 304.0833 | 205 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4.0165 | 241 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 93.7175 | 98.65 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 249.4165 | 205 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 369 | 205 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 516 | 240 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 85.4966 | 197.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 526.1665 | 205 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 0.23333 | 0.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1309.6066 | 147.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 437.8165 | 241 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 22786.9165 | 485 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 440.75 | 205 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 101.9382 | 197.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3995.4165 | 223 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 229.4831 | 281 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 826.0265 | 387.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 321.9999 | 168 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 15.5 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 580.5 | 258 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 130.34 | 137.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 24226.1332 | 256 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 53.0616 | 102.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 27.9166 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 251.625 | 152.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 283.5466 | 137.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 335.5 | 152.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 4782.2665 | 178 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 33.5 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 14.105 | 27.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 184.25 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1127.5 | 275 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 99.9998 | 240 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 165.2083 | 152.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 381.705 | 254.47 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 156.7999 | 192 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3685.9999 | 142.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 109.2916 | 152.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 124.5416 | 152.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 850.9 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 27.9166 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 192.0666 | 67 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 13.4999 | 162 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 181.1179 | 159.81 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 777.7799 | 313.2 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 636.8666 | 164 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 211.5 | 30 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 366.75 | 163 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 352.5 | 235 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 177.6666 | 164 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 2993 | 164 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 6642 | 164 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 43 | 30 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 243.1 | 221 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 488.6699 | 163.8 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 214 | 30 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 11.5 | 138 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 230.295 | 153.53 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 358.05 | 217 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 842.5331 | 284 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 20.2216 | 110.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 18.3833 | 110.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2323.9666 | 86.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 390.6905 | 266.38 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 144.924 | 241.54 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 3283.5 | 165 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 1791 | 90 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | NULL | NULL | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 730.188 | 540.88 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 800-Miscellaneous
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 5306.25 | 75 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1785.1925 | 268.45 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 3329.4332 | 266 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1429.8882 | 274.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2329.9998 | 600 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3402.7531 | 401.9 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 224.5833 | 175 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 194.3666 | 119 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 3091.3999 | 156 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 90.5 | 181 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1250.8333 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 160 | 160 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 122.25 | 163 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 2670.9332 | 256 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 4947.5 | 150 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 0.764 | 15.28 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 58.68 | 48.9 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | TRE | Summer | 258.4 | 323 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 49 | 98 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 4.4182 | 265.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 612.25 | 93 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 20000 | 250 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 35.3466 | 265.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 185.92 | 265.6 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1.3725 | 27.45 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 163.7865 | 265.6 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 653.9132 | 265.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 43.725 | 26.5 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3007.5 | 150 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1222.65 | 37.05 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Summer | 82.6666 | 155 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3847.5 | 50 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 2800.8333 | 50 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 8816.6666 | 50 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 32676.6666 | 50 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 55.4167 | 35 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2363.7333 | 8 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 817.3188 | 63.77 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3305.2666 | 172 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 851-CC GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | NPCC | Winter | 210240 | 24 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20817.5716 | 150.67 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1732.9333 | 82 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5547.3332 | 212 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 9379.9999 | 402 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2469.15 | 31 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34596 | 496 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 406.25 | 75 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 29568.7996 | 552 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2843.75 | 125 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3971.3333 | 35 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 168 | 140 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6480.1 | 66 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14219.9166 | 95 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 42017.7333 | 28 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 948.9999 | 195 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 232 | 40 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 18113.3333 | 190 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 453.4832 | 161 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8412.2998 | 351 | 1 | 1 | 0820-Casing | U2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1960.7997 | 387 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 33418 | 77 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 28356.25 | 325 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 972.3166 | 227 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198588 | 494 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2271.2083 | 32.5 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 650-Fluidized Bed
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 245.8085 | 38.71 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 650-Fluidized Bed
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 11342.128 | 100.64 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 650-Fluidized Bed
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 141.6 | 118 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 4953.5333 | 110.9 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 852-CC steam units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 8821.6665 | 197.5 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 852-CC steam units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 78 | 65 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 852-CC steam units
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2022 | Gas | GG | 861 | CoG GT units | SERC | Summer | 2226.8332 | 155 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 861-CoG GT units
0820 | Casing | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2022 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 0 | 0 | 1 | 1 | 0820-Casing | D3-Forced - Postponed | 862-CoG steam units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6274.35 | 219 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 89710.5165 | 307 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 88129.5 | 410 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 13570.7 | 169 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1277.5 | 30 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4208.85 | 199 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11655.4166 | 275 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 861.3282 | 190.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2119.9998 | 600 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 5652.6665 | 244 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 173.7 | 193 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 440.1 | 163 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 605.8166 | 163 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 276.4665 | 188.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4282.57 | 177.7 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 88.2 | 98 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1310.7499 | 321 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 532.8333 | 23 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 48960 | 360 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14252 | 56 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.8667 | 44 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 205.1333 | 34 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 441.3333 | 40 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1496.6666 | 40 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 202.6666 | 40 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 287.3333 | 40 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1437.5 | 50 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 650-Fluidized Bed
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 178.5 | 90 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 8472 | 90 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 68813.3333 | 160 | 1 | 1 | 0840-Refractory and insulation | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 149.05 | 11 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 181.3333 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 213.0667 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 219.0393 | 17.57 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 250.6667 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 377.9547 | 21.68 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 393.75 | 27 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 6194.364 | 30.91 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 227.75 | 15 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 259.5167 | 23 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 268.4 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 313.8167 | 19 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 389.1627 | 26.06 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 252.5333 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 314.6667 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 316.3333 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1192.5 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 248.1 | 18 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 266.9333 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 276.4667 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 479.4666 | 31 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 520.0167 | 41 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 9.1833 | 29 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 193.2333 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 219.75 | 15 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 282.1333 | 23 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 338.3333 | 25 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 420.3333 | 26 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 422.5 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 257.83 | 21.85 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 321.2 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 333.5 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 373.3333 | 25 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 410.793 | 26.82 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 538.35 | 37 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 7.7 | 21 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 211.4667 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 251.5333 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 291.368 | 18.06 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 303.2333 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 401.0395 | 29.67 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 471.3496 | 49.27 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 476.28 | 30.24 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 272.4333 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 309.5 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 345.8 | 21 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 454.8 | 36 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 35.8333 | 50 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 173.4 | 12 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 219.2 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 226.734 | 19.08 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 234.9833 | 23 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 273.7 | 21 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 283.3333 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 318.75 | 25 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 376.567 | 26.06 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 444.5 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 168.883 | 11.81 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 211 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 305.536 | 24.64 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 324 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 331.3813 | 30.08 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 437.4167 | 29 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2289.88 | 26.2 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3584.5333 | 26 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 440.2 | 31 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 466.9875 | 29.65 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 497 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1903.2113 | 17.56 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 239.6667 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 255.2808 | 21.85 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 276.3333 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 374.55 | 33 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 226.4 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 263.75 | 25 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 271.2 | 18 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 356.8866 | 26.8 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 417.7333 | 26 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 450 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 461.5333 | 43 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8.75 | 21 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 182.4 | 16 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 212 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 231.4833 | 17 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 274.6333 | 22 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 367.9167 | 25 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 400.021 | 26.06 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 512.5333 | 31 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 256.0635 | 20.79 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 257.3333 | 20 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 302.45 | 23 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 389 | 30 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 407.7 | 27 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 416.4333 | 31 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 458.5866 | 29.65 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 488.5333 | 32 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1154.0785 | 27.91 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 850-Combined Cycle Block
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 6100 | 244 | 1 | 1 | 0840-Refractory and insulation | D2-Forced - Delayed | 860-Co-generator Block
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1935 | 430 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 802 | 200.5 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51297.4165 | 635 | 1 | 1 | 0845-Windbox expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
0845 | Windbox expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 770.921 | 31.66 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 852-CC steam units
0845 | Windbox expansion joints | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 342.4 | 32 | 1 | 1 | 0845-Windbox expansion joints | D1-Forced - Immediate | 852-CC steam units
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.2167 | 7 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4649.25 | 45 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 937.9333 | 22 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3052.485 | 24.3 | 1 | 1 | 0847-Other expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 30.9547 | 0.64 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | RFC | Off-Peak | 26601.75 | 563 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 800-Miscellaneous
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 453.5 | 30 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5857.4999 | 99 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1188.3333 | 50 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 560 | 40 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 650-Fluidized Bed
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 356 | 20 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 800-Miscellaneous
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1053.1499 | 153 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 850-Combined Cycle Block
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 657.72 | 313.2 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 19040 | 160 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Summer | 34.5 | 230 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 20960 | 160 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 681.2 | 262 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 22134 | 186 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | MRO | Summer | 488.6699 | 163.8 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | WECC | Winter | 4861.2667 | 44 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 861-CoG GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 15688.6333 | 142 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 862-CoG steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.3333 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24818.4 | 108 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18164.9997 | 450 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 14787.3331 | 410 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.6666 | 119 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1082.4 | 66 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 724.3333 | 41 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 80.5 | 230 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 6308.1333 | 184 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 126.2 | 63.1 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 172.0833 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 163.3332 | 280 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 570 | 380 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 82.3332 | 260 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 129 | 129 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 320.6666 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 463.2498 | 255 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 776.5 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.1999 | 159 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8841.25 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 58.5 | 130 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 116.8 | 292 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 176.6998 | 342 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1524.5 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 196.7 | 42 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 359.9167 | 5 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17267.5 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.9499 | 87 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2041.25 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.65 | 47 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2543.75 | 25 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 42 | 105 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1795.8332 | 250 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D2-Forced - Delayed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 108 | 135 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.9999 | 180 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 105 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1622.4 | 62.4 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4.8 | 3 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 57502.4 | 332 | 1 | 1 | 0856-HP Drum relief/safety valves | D3-Forced - Postponed | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2191.0166 | 209 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 106.1666 | 70 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 92.1666 | 70 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 303.1666 | 107 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 288.1665 | 190 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 738.99 | 48.3 | 1 | 1 | 0856-HP Drum relief/safety valves | D2-Forced - Delayed | 852-CC steam units
0856 | HP Drum relief/safety valves | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Winter | 2473.4 | 74.5 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 860-Co-generator Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 858.15 | 190.7 | 1 | 1 | 0857-IP Drum relief/safety valves | SF-Startup Failure | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8746.7732 | 190.7 | 1 | 1 | 0857-IP Drum relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 5818.0265 | 194.8 | 1 | 1 | 0857-IP Drum relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1847.9999 | 180 | 1 | 1 | 0857-IP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11096 | 292 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1421.0665 | 292 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2628 | 292 | 1 | 1 | 0859-Tube external fins/membranes A | U1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16647.1166 | 167 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | U2-Forced - Delayed | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1614.9999 | 300 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | U1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 104.5333 | 98 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | D1-Forced - Immediate | 100-Fossil-Steam
0860 | Soot blowers - air (see code 3844 for air delivery system) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 264.5 | 529 | 1 | 1 | 0860-Soot blowers - air (see code 3844 for air delivery system) | U1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135.091 | 122.81 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 680 | 85 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 814.5931 | 414.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 608.3333 | 125 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.4167 | 35 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11716.6832 | 221 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39174.9998 | 750 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2309.96 | 67.94 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 19975 | 50 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 20160 | 28 | 1 | 2 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164 | 82 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6250.3832 | 331 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 246.5 | 30 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61.4166 | 335 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 17.48 | 3.04 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 337 | 337 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 915.4165 | 325 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 929.9997 | 450 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.5 | 6.25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 215 | 172 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3712.5 | 25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 868 | 620 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3428.1662 | 670 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3529.5999 | 192 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2953.6 | 284 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 987.1765 | 414.2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.3333 | 40 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 546.8331 | 386 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 222 | 20 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 983.0665 | 202 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2007.5 | 55 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1183.26 | 577.2 | 1 | 1 | 0870-Soot blowers - steam | U3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2058.6532 | 315.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.96 | 5.61 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | WECC | Winter | 79.04 | 12.35 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | WECC | Winter | 541.645 | 25.35 | 1 | 1 | 0870-Soot blowers - steam | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3797.9132 | 291.4 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6060.3666 | 266 | 1 | 1 | 0872-Soot blowers - water | D1-Forced - Immediate | 100-Fossil-Steam
0872 | Soot blowers - water | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 271.35 | 81 | 1 | 1 | 0872-Soot blowers - water | D2-Forced - Delayed | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.1999 | 258 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1198.3333 | 100 | 1 | 1 | 0873-Soot blower drives | D2-Forced - Delayed | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5977.8333 | 178 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1705.8333 | 178 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2196 | 183 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 327.6 | 168 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.05 | 8.2 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.5 | 16.5 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 102.0833 | 49 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 577.8 | 81 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 182.2167 | 29 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2051.6666 | 100 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 108.6166 | 49 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 242.5666 | 153.2 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4133.3332 | 200 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 997.9 | 51 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 117.1666 | 37 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3293.6866 | 228.2 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.48 | 66.6 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12436.6666 | 260 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 79120 | 230 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 204975.8331 | 275 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 53.6666 | 140 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.3333 | 32 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.65 | 19 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 22 | 120 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 987 | 105 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1855.7499 | 195 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 42 | 10.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 79.212 | 14.49 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.6 | 12.2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5369.4 | 188.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 287.5 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91179.4664 | 662 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 578.8333 | 151 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.35 | 10.55 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 33.25 | 95 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.9833 | 31 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 182 | 42 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2714.78 | 36.44 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6088.4599 | 188.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 63.4667 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 667.9499 | 328.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 124.25 | 105 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1569.6665 | 277 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 770 | 105 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 124.5132 | 20.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168.98 | 241.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 520.7333 | 214 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1480.1599 | 191.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1683.2833 | 91.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 95 | 95 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13426.0832 | 367 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 99.1666 | 175 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6489.6 | 507 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448 | 14 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 667.2332 | 270.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1608.5733 | 216.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4779 | 180 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8316 | 308 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 12.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 289.0666 | 27.1 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3286.712 | 145.86 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 153 | 15.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2892.633 | 539 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 565.75 | 155 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4434.9999 | 150 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 30.774 | 8.92 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 61.2 | 51 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4096.8 | 113.8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17110 | 295 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19279.9999 | 240 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3040.17 | 144.77 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 86.25 | 75 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1702.0832 | 125 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1815.6 | 106.8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 460.5333 | 88 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 44 | 22 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | SERC | Summer | 638.625 | 19.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 800-Miscellaneous
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 4278.5 | 398 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1157 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1838.2 | 404 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10350 | 414 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1591.5 | 106.1 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 720 | 144 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1427.8833 | 7 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3833.5 | 374 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1049.4 | 104.94 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1066.44 | 88.87 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 5790.4 | 13.16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 683.7999 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7612 | 220 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8520 | 710 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 103417.9 | 401 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2907 | 170 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1464.75 | 105 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5978 | 305 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 658 | 13.16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 839.5 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 55.8 | 9.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1734.4 | 271 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23734.2162 | 739 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2945.6 | 224 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9275.25 | 223.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 147.7 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34868 | 379 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 939.6 | 93.96 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9499.8 | 446 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5676.35 | 107 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 294.6666 | 40 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17787.1665 | 410 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 270.3 | 102 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 899.25 | 81.75 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 947 | 94.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 57.8 | 14.45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 267.75 | 51 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3534.9998 | 303 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 90.1333 | 20.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1306.7664 | 394 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2955.3332 | 310 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 45.45 | 10.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 103110.6664 | 680 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 518 | 105 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 692.5 | 277 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 790 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 189.6166 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4108.5 | 330 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 8.0833 | 5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 92446 | 680 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5517.8662 | 739 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 391.4435 | 20.37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4633.4666 | 248 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2829.0083 | 116.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2142.8333 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40948.6997 | 507 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3536.0333 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19584.1664 | 710 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69387.6664 | 860 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 908.56 | 22.16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.2 | 11.05 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275 | 500 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4672.4999 | 450 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8423.7333 | 124 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.5067 | 17.6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10944 | 304 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33515.7832 | 493 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120838.8162 | 739 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11997.2663 | 508 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 172.5 | 115 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 394.8333 | 103 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 605 | 22 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3509.3331 | 329 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3408.4666 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1058.6666 | 40 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1760.373 | 507.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 920 | 8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 48.2605 | 11.01 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 35739.7664 | 659 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 379885.3662 | 682 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 663.205 | 23.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 4609.2 | 184 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 541.2 | 8.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1026.9817 | 13.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 8.475 | 11.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 46.97 | 18.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 6.3933 | 2.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 277.2 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 4.515 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 8.6 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 11.3233 | 15.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 20.0667 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 33.2 | 8.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 87.15 | 8.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1594.485 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 79.1917 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 11.205 | 8.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.6 | 0.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 5375.16 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3018.75 | 45 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 6.3 | 6.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 193.3833 | 8.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 276.34 | 8.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 21.9267 | 2.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 77.9 | 8.2 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 748.425 | 15.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 114.615 | 24.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 170 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 352 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 418 | 38 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1644.4167 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 660.7833 | 41 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 280 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 480 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 480 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2130 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 6.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 136 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 460.6 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 465 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 31.1667 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 180 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 106.3833 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 150 | 30 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2257 | 37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 464.4833 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 589 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 210 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 272 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 68.25 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 419.4167 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1260.6 | 36 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 280 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 99 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 288 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 304 | 38 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 330 | 33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 576 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1260 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1925 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 160 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 24.7333 | 14 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 61.05 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 350 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 132 | 33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 239.2 | 26 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 773.5 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 80.3 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 495 | 33 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 341 | 31 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 480 | 32 | 1 | 2 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1849.3833 | 37 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 420 | 35 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1190 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 102 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 100 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 564.75 | 27 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1020 | 34 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1664 | 32 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 144 | 4 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 156.1 | 42 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.9541 | 129.85 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2874.6664 | 352 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3377.9166 | 275 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2038.9498 | 621 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3400.5 | 680.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67363.905 | 680.1 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1562.5 | 250 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2870.8333 | 250 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62714.1664 | 650 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 842.5333 | 89 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8161.2 | 680.1 | 1 | 2 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200 | 50 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D3-Forced - Postponed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2442.3332 | 170 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4069.7499 | 109.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8549.6082 | 189.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81348.15 | 507 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 759.8666 | 164 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.8999 | 78 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.5833 | 35 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3691.9997 | 390 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2907 | 170 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1131 | 130 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3756.1665 | 310 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 666.9332 | 164 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1573.5 | 90 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2250 | 450 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 560.8582 | 314.5 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9921.9998 | 615 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 173.11 | 24.73 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2606.2832 | 523 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6207.3665 | 518 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2688.2665 | 593 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3229.5833 | 115 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2437.3333 | 160 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3655.4166 | 155 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49591.29 | 441.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6326.7332 | 441.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 508.7499 | 165 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3921.4933 | 141.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 245.4232 | 241.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1532.8333 | 216.4 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1829.7499 | 195 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2713.6 | 256 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2648.25 | 33 | 1 | 1 | 0894-Bottom ash piping and valves | U1-Forced - Immediate | 650-Fluidized Bed
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1477.9166 | 25 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 143 | 12 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 154 | 20 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1109.7333 | 7 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 148.75 | 35 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 504 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1138.55 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1534.75 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1558.3333 | 25 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 26.8667 | 13 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 553.8666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3294 | 244 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2317.95 | 303 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15932 | 227.6 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3073.1 | 389 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 586.684 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45596.1998 | 507 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 440.8 | 58 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1027.4998 | 225 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1603.7 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15968.933 | 458 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 190.2471 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.6 | 42 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 956.9999 | 198 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1153.35 | 233 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4018.8 | 204 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 10564.9165 | 485 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5582.4999 | 150 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48434 | 610 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 147.7338 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 227.4463 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 255.08 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 661.6666 | 100 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1530 | 170 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1663.6666 | 124 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1063.1166 | 227 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1192.2499 | 285 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2460.9999 | 345 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 110.5346 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20095.1665 | 485 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2548 | 392 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2993.0665 | 244 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1118.2833 | 229 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 24779.8328 | 785 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 439.7666 | 158 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7263.0665 | 244 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6870 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 25.2 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12912.4665 | 611 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 546.6666 | 164 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1993.35 | 291 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2083.2832 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 88115.5332 | 493 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 905.9332 | 254 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5268.3331 | 580 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5308.45 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43371 | 610 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 535.668 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11423.1996 | 654 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24745.5 | 705 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36377.25 | 455 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 622.9333 | 73 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 300 | 200 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 203.2333 | 91 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.0832 | 349 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 809.1333 | 229 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 123.2886 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.4333 | 98 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2597 | 140 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 562.5832 | 215 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40550.6664 | 680 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1612.5 | 150 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.6833 | 73 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 863.5833 | 241 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1497.5998 | 351 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41531.7497 | 507 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 193.4356 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41561.0663 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2802.6666 | 160 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4427.4999 | 150 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 731.3997 | 414 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3509.9164 | 385 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 117 | 108 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1022.9332 | 274 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7425 | 540 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 103.0948 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 552.6733 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7744 | 484 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 996.8 | 178 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1449.0665 | 304 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1236.1332 | 254 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2876.4 | 423 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23515.98 | 437.1 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 61.5 | 45 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 172.405 | 12.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 398.7933 | 8.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 650-Fluidized Bed
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | WECC | Winter | 42 | 14 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 162.6135 | 63.77 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 326.2898 | 63.77 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 520.8 | 124 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 747.1718 | 63.77 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 298.6561 | 63.77 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 462.3325 | 63.77 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | U1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 945 | 420 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1713.88 | 61.21 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1720.08 | 95.56 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0899 | Bottom ash controls and instrumentation | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 714.2666 | 88 | 1 | 1 | 0899-Bottom ash controls and instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 21270.6 | 108 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3730.3666 | 34 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 64162.5 | 590 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1170 | 26 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 513.5 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 598 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 624 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 715 | 13 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21918 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 32019.0666 | 92 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.8667 | 8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43.8 | 36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2460.9832 | 149 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13.75 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3706.9 | 390.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7674.6666 | 320 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2575 | 515 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.65 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3987.9 | 126 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 329.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7209.8132 | 241.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 453.4832 | 161 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 506.25 | 405 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1280 | 320 | 1 | 16 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 7.1167 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1698.2833 | 31 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 855.6666 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80 | 32 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 198.25 | 305 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3588.75 | 145 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 106.1667 | 35 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1011.92 | 361.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 102.3667 | 7.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 3668.2667 | 38 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1280 | 320 | 1 | 2 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1541.3998 | 252 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5566 | 242 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2830.2 | 89 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4.1666 | 25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285.6566 | 241.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61048 | 416 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 598.32 | 22.16 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.95 | 33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 199 | 199 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9040.8333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 855 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2005.1665 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 501.3333 | 94 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1952 | 64 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.3333 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162.5 | 25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1010.1665 | 190 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 149.8667 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 527 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 953 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1110 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 489.6666 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 900 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39447.5663 | 586 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 405.6333 | 86 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 3974.8 | 38 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 747.5 | 150 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1180.9735 | 400.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 450 | 300 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 202.5 | 75 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 573.0833 | 115 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 10.16 | 4.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2303.2 | 48 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12997.4166 | 121 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2060 | 515 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 225 | 60 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5417.9998 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 52.5 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90.6667 | 16 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 781.75 | 265 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 619.1667 | 25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1185.8333 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1221.1666 | 170 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 888 | 120 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1115.8333 | 130 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1669.7999 | 217.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6839.6664 | 355 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 427.98 | 30.57 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16742.6663 | 580 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 7455.4999 | 111 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 237 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 237.5 | 50 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2463.75 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1518 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 31.5 | 6.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 884.0917 | 38.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 203.8833 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 327.1667 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 580.6667 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 18060 | 344 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 4 | 4 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 200 | 10 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2329.1666 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 7.8667 | 8 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 11 | 11 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 94.5 | 18 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 10 | 10 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1397.5 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U2 | Forced - Delayed | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 15875.1999 | 96 | 1 | 1 | 0930-Bed material coolers | U2-Forced - Delayed | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 3 | 3 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 9 | 6 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 25 | 10 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 5.5 | 5.5 | 1 | 1 | 0930-Bed material coolers | D1-Forced - Immediate | 650-Fluidized Bed
0931 | Bed material transport piping/valves | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1267.4999 | 225 | 1 | 1 | 0931-Bed material transport piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 552.5 | 85 | 1 | 1 | 0936-Bed material conveyors B | U1-Forced - Immediate | 650-Fluidized Bed
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 192 | 16 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0937 | Bed material mechanical separators and baghouse | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 223.8333 | 34 | 1 | 1 | 0937-Bed material mechanical separators and baghouse | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 25.7283 | 4.3 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 74.2333 | 6.8 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 56.24 | 4.8 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0959 | Other char reinjection equipment problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 3.6667 | 4 | 1 | 1 | 0959-Other char reinjection equipment problems | D1-Forced - Immediate | 650-Fluidized Bed
0970 | Flue gas-solids separator | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 516 | 344 | 1 | 1 | 0970-Flue gas-solids separator | D1-Forced - Immediate | 650-Fluidized Bed
0980 | High pressure loop seal recirculation fans/blowers | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 127.2916 | 32.5 | 1 | 1 | 0980-High pressure loop seal recirculation fans/blowers | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 907.0497 | 37.82 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 905.131 | 37.74 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 3165.3318 | 37.69 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3952.5 | 25.5 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 6768.8998 | 372.6 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 95210.01 | 382.6 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 188 | 9.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 222.3 | 11.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10950.75 | 155 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 1815.2095 | 37.83 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 36 | 4.5 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Summer | 6294.3355 | 37.47 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 166332.1729 | 624.8 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 236.5 | 30 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 4506.574 | 37.56 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 2128 | 152 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2 | 2 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 322.4 | 12.4 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 75.2 | 4.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 1079.5 | 12.7 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 13065.9198 | 364.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 211.6667 | 25 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 450 | 60 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1487.5866 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2122.2 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1844.2333 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 354.8077 | 35.54 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 8195 | 55 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1308.6533 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1807.92 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 188.6 | 8.2 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 37.1467 | 1.6 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1520.775 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1692.14 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 604.5 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 31992.75 | 241 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2009.1 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1908.765 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 3140.7 | 38 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2050.4133 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 3673.3333 | 38 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 453.6 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 191.2872 | 31.97 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 38.61 | 38.61 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 11460 | 90 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10.8 | 3.6 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 6448.75 | 77 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 19 | 3.8 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.5 | 3.5 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 30 | 2.5 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.6 | 3.3 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 17.5 | 3.5 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 24.5 | 3.5 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.2 | 3.2 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 32 | 3.2 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 12.8 | 3.2 | 1 | 2 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 22.4 | 3.2 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3 | 3 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.4 | 3.2 | 1 | 3 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 28 | 2.8 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 16.8 | 2.4 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | U2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 39037.3333 | 160 | 1 | 1 | 0999-Other heat exchanger problems | U2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1398.9333 | 244 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2232.6666 | 170 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4524.8 | 20.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4566.105 | 22.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 35728.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48955.7499 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54873 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9018.6665 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17400.2333 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25595.1496 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28847 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46265.3112 | 1330.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60763.0414 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113714.9995 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200825.7162 | 1331 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41643.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 12345.3 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19245.4165 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31739.8665 | 434 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 41142.733 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 18342.4666 | 146 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 56774.2 | 749 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 3384.3333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34275.9998 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85661.5 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2972.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29570.6663 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 73901.3328 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27154.2495 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24205.0866 | 339.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.4333 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3360 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 7347.6 | 314 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 227759.5667 | 26 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5743.6 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6164.1333 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6360 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25931.2191 | 815.02 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44439.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7917.2499 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10073.4499 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13078.3999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34941.9 | 713.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1489 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35985 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36646.3332 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41621.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148219.55 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 50895 | 675 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 28897.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7436 | 143 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7338.4166 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21409.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 24927.0998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 28164.0625 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 30329.3333 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 43464.125 | 231.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 13053.3333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 15997.1375 | 447.89 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 30700.4382 | 406.18 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 667.25 | 51 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15208.8016 | 117.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31476.6 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 12017.6 | 203 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57604.56 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33699 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1201.3166 | 49 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2935.5 | 45 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2447.4994 | 825 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2612.8 | 28.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 6381.3333 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2131.0832 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.3333 | 80 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5973.0332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6806 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16817.5 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20880 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37719.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8086.8333 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20853.5331 | 336.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25064 | 208 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29485.8331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31805.3665 | 494 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30624 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31204.52 | 336.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40644.1661 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65629.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 24165 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13195.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3310.153 | 426.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19237.8333 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35545.95 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30138.7332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10817.7665 | 362 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25045.5332 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 194234.2664 | 764 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41459.3664 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2784.8 | 23.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11980.8 | 23.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2384.7 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70710 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2148.8 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2388.4332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4194.1999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4338.2499 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4971.7332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8932.2666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12990.2332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19511.25 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20633.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29019.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30098.4997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35365.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56218.8924 | 1330.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60111.2814 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 160682.2585 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5408.3166 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17372.55 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31557.9545 | 815.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35779.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41322.75 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46665 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 71100.3999 | 168 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 161428.7328 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6765 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 56794.2708 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3825.6666 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5360.8166 | 122.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5942.7083 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8295.0833 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9576.6666 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 98844.0998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 99335.9375 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 54680 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 8732.5 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1528 | 764 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25456.4331 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36158.6999 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38894.8 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45936.9 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84226.65 | 487 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17772.3 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 686.961 | 416.34 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 975 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3986.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7095.6 | 21.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 667.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1461.4164 | 355 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3148.2 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26926.9 | 538 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16468.65 | 99 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34790.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15724.8999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 16352.8329 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36718.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39140.8329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57712.6664 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73029.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11284.7333 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18434 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 41436.85 | 637 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43287.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70779.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 87856.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9890.4997 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 580 | 145 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7508.85 | 113 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16912.5 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17324.7 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 82895.8333 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 12672 | 528 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 273487.5 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 32024.6665 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 19006.8 | 564 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 390438.3996 | 564 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9548.2333 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10800 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12553.3331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25454 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 91232.633 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17736.2999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18538.3331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34377.3329 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48 | 48 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5280 | 27.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1536 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2162 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4421.1333 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54214.0831 | 619 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57318.4164 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 61000.1328 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85414.9998 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 132743.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4937.9999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14056.7332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18516.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35966.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63309.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5348.7499 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12615.5 | 115 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25597.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42124.5 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46740 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62928 | 570 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64939.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16529.9997 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 25911.8 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5286.4 | 56 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8355.5999 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9752.75 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 63676.8 | 536 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | SERC | Summer | 58717.66 | 787.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33593.3499 | 123 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17306.3798 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145278 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18188.3331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38012.2165 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20056.4 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4540.6716 | 317.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2198.4 | 22.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 7781.0395 | 28.57 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4867 | 31.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24256.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24940 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34790.2498 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50089.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 51966.2995 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 154328.3329 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5911.8332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10688.7 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14400 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9591.6666 | 100 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10734.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12739.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 162227 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18413.75 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 22665.3 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 320 | 64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4485 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15543.15 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 42778.1995 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 23241.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 39526.9997 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 59202 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 9098.5999 | 402 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4938.5 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3769.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14204.34 | 216.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226270.26 | 638.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67466.6664 | 800 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 836.25 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2796.5 | 23.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6084.4 | 21.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9752.6 | 28.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 901 | 26.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20757.6 | 27.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1269.3333 | 70 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3970.9999 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6418.6666 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14418.3999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18490.7496 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34771 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65988.5 | 677.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 247455 | 1300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3483.3332 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5940 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16516.8833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16774.3332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35778.7331 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36789.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39303.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46429 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102170.6 | 532 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4330.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7291.4999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41389.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 11622.1083 | 92.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 13366.8 | 141 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 51033.8541 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4091.9666 | 92.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8348.6 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18747.0832 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22600 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 26521.25 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 70207.4999 | 225 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 24379.75 | 113 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36386.208 | 567.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86167.8332 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17914.4999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28492.5 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44375.9997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70259.5 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 102516.3331 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 719.1333 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2432.4667 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8070.397 | 209.53 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1911.1466 | 131.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2356.2499 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 348.833 | 455 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10338.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18923.3331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23014.5 | 670 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32781.9314 | 337.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41394.1664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98104.9998 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7411.365 | 110.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9837.2498 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14153.75 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15783.8332 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22130.1 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25639.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25929.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25996.5998 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61034.6078 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1544.3331 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9442.9162 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 29802.5 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43462 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49045.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137407.4996 | 1350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 20602.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8849.0497 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 17862.5 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8416.7497 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12924.1665 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 20430.4999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 97602.0495 | 741 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 16006.6665 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 17302.6665 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 17901.15 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11287.5 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13329.9999 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26818.4994 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 90 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3673.1383 | 25.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 2368.75 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 2 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 699.5666 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 295.75 | 91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1188.1332 | 266 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20399.05 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51960 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2891.4 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7830 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24310.9165 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 27542.75 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50269.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 80302.5 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102378.4496 | 639 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150229.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4178.1999 | 156 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7320.0333 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9963.4833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10502.7998 | 231 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16065.8499 | 123 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33633.7998 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 34103.6662 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 47581.1 | 673 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 79903.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 22050 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2372.45 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 4784.85 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 14101.2497 | 435 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 29562.4995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8733.1666 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 16805.5 | 145 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 280683.6 | 68 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 6370.8332 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6617.325 | 49.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 29670.0333 | 113 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29441.4998 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76869.3329 | 710 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40313.25 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310393.8164 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 344.8025 | 67.83 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8152.4 | 22.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 175199.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1634.6333 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5472.0332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14157.0999 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14683.6663 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30929.1665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32397.75 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8689.9998 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12256.1666 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15020.5332 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20662.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29160.6664 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37142.82 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42525 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46546.5 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5566.5999 | 156 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27550 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49843.3331 | 760 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51429.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 27134.3332 | 203 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30637.4997 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7155.75 | 203 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 99239.9998 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 11079.8666 | 92 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14632.5833 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 18833.0833 | 145 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23213.75 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 23869.2998 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 30814.3333 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 46615.9997 | 480 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 8531.25 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 230006 | 245 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1311.6666 | 50 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31288.95 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9870.3666 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35419.9999 | 330 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6420.4164 | 475 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1020 | 60 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 397.8 | 22.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 508.4 | 12.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 955.8 | 531 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 823.5 | 15 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26829.7495 | 747 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5780.95 | 199 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10935.2332 | 502 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23284.9998 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45446.6999 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62705.8265 | 241.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23059.8 | 414 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27722.5 | 325 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30783.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60819.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 90953.333 | 560 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133170.4 | 818 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3849.9999 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9918 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21535 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36459.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46231.6 | 328 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83324.9998 | 495 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93653.3331 | 320 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98693.6665 | 620 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15715.5832 | 203 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6465.9832 | 143 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10254.1666 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21925.6999 | 258 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 25145.1666 | 98 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 38205.5 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 19959.1666 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 1432.2 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 5166.3333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 13621.0999 | 402 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 2006 | 40 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16540.2 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25029.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 34730.4545 | 723.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 127282.5832 | 361 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5033.3332 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31952.6661 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9769.4999 | 270 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34698.75 | 487 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 69947.5996 | 552 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14030.6833 | 91 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 235 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.2 | 23.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 621.4 | 23.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3344.3 | 63.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 891 | 18 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29892.4162 | 673 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34347.7331 | 832 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6512.4 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7038.6325 | 25.05 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8023.3332 | 200 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9791.433 | 467 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5982.0833 | 175 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7584 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20049.9999 | 300 | 2 | 2 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59230.8331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97432.5795 | 720.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 111814.4998 | 630 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 25987.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16668 | 240 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 27898.4375 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 37516.5 | 397 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3239.4998 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25846.3666 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 211704.4 | 764 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28771.8664 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 4524 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88665.4995 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26767.4997 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 55960.2 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2715.284 | 288.86 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 140 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2906.25 | 155 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8101.2 | 31.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17775.8332 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3933.0666 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8985.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13214.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21619.7499 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31482.7496 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40126.5332 | 502 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45998.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102020.8331 | 625 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8853.2666 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8966.5 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36150.4998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42919.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64489.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6446.2 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7590 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8748.3331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10828.9998 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30425.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80319.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120650 | 635 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2039.9998 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 34612.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25265.25 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 9054.1666 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 27589.5832 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 5402.7748 | 258.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7075.7316 | 117.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13700.28 | 117.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15536.7 | 28.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 507.5332 | 331 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2569.3332 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.06 | 105.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1018.1665 | 205 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1851.68 | 56.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23336.8332 | 415 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207275.7498 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4498.75 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 24366 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5953.8666 | 166 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32280 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42240 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56876.1331 | 652 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101797.4997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4844.7999 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14569.0998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19931.7 | 158 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28201.1665 | 410 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48847.4 | 644 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80606.8663 | 532 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5964.5 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12129.9431 | 637.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13156.0499 | 206.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20276.7999 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156000 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 241523.9912 | 1330.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16716.6666 | 125 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6270 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16795.7833 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 20226.3997 | 393 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20278.75 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 35461.8333 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3028.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25531.4798 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7598.55 | 179 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2236.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2453.75 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1430 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 27924.75 | 315 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 15540 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 487.5 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 388.5 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 617.5 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1573 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1560 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 536.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 351.05 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 520.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 621.25 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1019.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1401.3767 | 20.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 435 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 826 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2621 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 360 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 522 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 380.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 3999.1583 | 38.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 3960.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 714.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 1465.0766 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 441.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1995 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2885.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1275 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2326.5 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 36359.1 | 213 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1685.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 990.5 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1395 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 92619.5995 | 711 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 3480.75 | 25.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 37353.85 | 419 | 1 | 1 | 1000-Waterwall (Furnace wall) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 72581.2498 | 711 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 32899.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 776.1598 | 27.41 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 1944.54 | 70.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 3194.1 | 23.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 140159.7333 | 16 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 37950 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5186.05 | 57 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 297.6 | 9.3 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14131.2498 | 255 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | SF-Startup Failure | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 382.85 | 11.4 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1264.5 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63142.1732 | 253.6 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32693.7 | 606 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 58.5 | 90 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22794.3 | 589 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26884.3665 | 374 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11211.4998 | 510 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 294.4 | 9.2 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 32784.4998 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88112.1498 | 609 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1877.75 | 105 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 475.2333 | 10.6 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19692.7663 | 601 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80386.9732 | 253.6 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 936.3 | 18 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21719.4998 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 935.55 | 231 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 26971.2 | 108 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 4812 | 40 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7747 | 127 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36489.2496 | 609 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 364.8333 | 22 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27474.9998 | 471 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15097.5 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1400 | 70 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 5707.1 | 21 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 69772.9999 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 752.5 | 30 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 28482 | 404 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 862.4455 | 58.87 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7882.2045 | 178.87 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34543.6665 | 220 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26691.4999 | 330 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 5710.6666 | 40 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26944.5 | 330 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3729 | 33 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 650-Fluidized Bed
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 205.85 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2202.2 | 42 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 371.8333 | 23 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 800-Miscellaneous
1006 | In-bed reheat tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 16683.1666 | 155 | 1 | 1 | 1006-In-bed reheat tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1171.2 | 48.8 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35454.0998 | 579 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 188.5 | 130 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2488.1067 | 42.8 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 70803.7164 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36771.5 | 586 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1087.9999 | 120 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 933.9167 | 35 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 18698.3 | 289 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 290 | 14.5 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24549.2666 | 76 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 68 | 170 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 186.8333 | 190 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 76636.9999 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 34.6666 | 160 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 149 | 37.25 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1441.9999 | 210 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1948 | 120 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 28466.6664 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48286.4 | 586 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 473.3332 | 200 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27983.4666 | 142 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 930.43 | 224.2 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 86.9999 | 180 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 815.4363 | 15.11 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37584.9 | 54 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 24628.9999 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 54.1666 | 25 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 588.55 | 79 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 37372.5 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 44319 | 330 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 14603.4 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 32.4999 | 150 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 21122.2664 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 294.03 | 10.89 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 209104.5 | 1265 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 22422.9165 | 235 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28128 | 586 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 276.08 | 9.52 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15234.89 | 814.7 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9879.3332 | 203 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18388.3333 | 220 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11870.2497 | 855 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22576.054 | 815.02 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30260.2497 | 405 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 30286.5 | 305 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1938 | 285 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6768.3332 | 155 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 650-Fluidized Bed
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11313.15 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40709.2497 | 405 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 32608.5666 | 203 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46063.5 | 615 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 222.1666 | 43 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1891.75 | 115 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9616.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98480.25 | 1265 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 755.7333 | 32 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29966.0833 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13046.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10241.6665 | 250 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7273.45 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9173.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13936.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14090 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22281.9999 | 195 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11512.4999 | 225 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 19249.5333 | 247 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47005 | 395 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6732 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42641.4998 | 330 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.5 | 45 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7545.6 | 192 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18612.0832 | 475 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13366.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9563.0165 | 247 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3822.6666 | 305 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5378.9999 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13399.3333 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 22868.0833 | 247 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 428.9999 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17993.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23631.25 | 475 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48314.4 | 491 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3034.2 | 156 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5495.75 | 247 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5220.7999 | 156 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12350 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1016.9833 | 37.9 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17258.9999 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18576.65 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12012.4333 | 247 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5355.9999 | 156 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4725.2833 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26540.7165 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2257.5 | 350 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16710 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2112.7497 | 405 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18373.8 | 271 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 49546.9332 | 532 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1150 | 115 | 2 | 2 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110192.6662 | 670 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3099.2 | 52 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 26337.6665 | 605 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69859.5164 | 361 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97047.4126 | 814.27 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113768.0832 | 505 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 53343.059 | 815.02 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 7954.6665 | 380 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 26439.983 | 467 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107604.2498 | 339 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 28193 | 605 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46915.75 | 415 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41881.4665 | 644 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107053.3328 | 740 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 25228.8 | 432 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30552.1997 | 417 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25537.5 | 567.5 | 1 | 1 | 1035-Platen superheater | U3-Forced - Postponed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96134.75 | 415 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 204.75 | 455 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.3999 | 234 | 1 | 1 | 1035-Platen superheater | D2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70769.9998 | 630 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51678.4165 | 635 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6076 | 80 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36235.015 | 814.27 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86815.5 | 465 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39739.2496 | 615 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 41451 | 410 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57903.3331 | 580 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2926.4 | 49.6 | 2 | 2 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 602.7 | 86.1 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1479.2 | 184.9 | 2 | 2 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 259.2 | 64.8 | 2 | 2 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 489.6666 | 260 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 78698.5 | 535 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13058.815 | 117.7 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1078.4 | 134.8 | 2 | 2 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14757.6183 | 117.7 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 73000.7999 | 432 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38125 | 125 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4368 | 80 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18182.5 | 350 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3905 | 220 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 5113.4999 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 40744.3332 | 310 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 5388.3331 | 305 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 101998.7498 | 525 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 5197.5 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 10023.3332 | 310 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 52043.2498 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 11462.4999 | 210 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4676.6666 | 305 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 34046.2499 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 19049.5 | 310 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 23625 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3339.375 | 32.5 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 595.5966 | 181.4 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14675.25 | 255 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5178.7665 | 247 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13557.4998 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5076.4999 | 195 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7189.0999 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 25604.8663 | 478 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45001.4999 | 342 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6683.25 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13094.25 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58868.2499 | 315 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40077.15 | 673 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6840 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1740.75 | 165 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9532.1 | 199 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74960.7329 | 668 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3628.8 | 252 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34861.6658 | 1300 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 111923.0215 | 466.67 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 240727.5 | 823 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42009.8666 | 263 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3769.9166 | 95 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22629 | 570 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36200.7662 | 661 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21231.03 | 336.2 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5853.9666 | 122 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45348.75 | 417 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 751.3332 | 161 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72203.2331 | 661 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 104703.3331 | 311 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 5004 | 40 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12014.7498 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 36337.3996 | 597 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10700.8666 | 151 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18474.75 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 642 | 18 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1175.3 | 146 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 861.419 | 128.57 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8401.1165 | 199 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1342.5 | 537 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 224136.6473 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 525.6166 | 61 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2050 | 205 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22720.5 | 510 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 969.5667 | 17 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12878.6666 | 104 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 73485.6665 | 380 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9969.3 | 342 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2719.2 | 41.2 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12799.3332 | 146 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 389.3333 | 160 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 75768.7 | 658 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4660 | 80 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12566.6665 | 325 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 569.2166 | 49 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55887.5 | 850 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3434.25 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1115.3 | 58.7 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10021.3666 | 151 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27206.04 | 152.8 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 55436.5 | 658 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41816.6666 | 260 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 10229.9165 | 455 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3776.25 | 285 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6444.6665 | 280 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1417.7333 | 49 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20392.4997 | 450 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73251.9332 | 253 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21140.9831 | 661 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 36094.9831 | 331.4 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33115.9998 | 255 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161691.1998 | 528 | 1 | 1 | 1040-First superheater | U3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 28013.9999 | 180 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 126.5 | 46 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1689.45 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 2448.3333 | 113 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 800 | Miscellaneous | TRE | Summer | 4496.5 | 115 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1044.05 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 190 | 38 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 280 | 35 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 4860.1998 | 228 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 205 | 41 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 5272.7999 | 117 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2166 | 38 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 470.4 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1539.4167 | 35 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1232.7 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2285.0667 | 44 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 0 | 0 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1407.4667 | 32 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 1426.2266 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2232.58 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2307.095 | 20.3 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2808 | 39 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 400.75 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1886.85 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 10162.4665 | 226 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | TRE | Summer | 7842.3499 | 201 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 985.25 | 21 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 27135.1664 | 361 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1045 | In-bed superheater tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 841.75 | 185 | 1 | 1 | 1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1045 | In-bed superheater tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 6399.7498 | 315 | 1 | 1 | 1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1045 | In-bed superheater tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 83936 | 305 | 1 | 1 | 1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1386.6664 | 800 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 268.2499 | 111 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45237.3331 | 320 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101928.0829 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5492.4999 | 195 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49734.7496 | 585 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424688.3329 | 1300 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 23267.25 | 405 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 39846.7331 | 598 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 76843.4331 | 658 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13818.6666 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26396.3332 | 230 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 81234.7998 | 564 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3476.3832 | 167 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17165.4998 | 330 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 657.3667 | 41 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4229.1332 | 158 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 84325.0332 | 523 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43853.333 | 575 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116831.6332 | 361 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 655.4165 | 357.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 43092.2831 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 298787.3162 | 1331 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72684.1498 | 693 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 35922.9165 | 401 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 26421.3333 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7306.25 | 167 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 250 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5474.8166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9284.6857 | 390.66 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28642.5 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1118.15 | 104.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4740.0166 | 167 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73073 | 511 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 75447 | 747 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3994.55 | 101 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58192.428 | 815.02 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22047.5831 | 395 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 43996.975 | 575.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2403.3331 | 350 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37881.9998 | 705 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2112.11 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1524.6 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1967.7317 | 18.35 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 11588.5 | 98 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29987.6999 | 342 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11997.3333 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 5555.3333 | 40 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12412.8998 | 606 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57053.6999 | 162 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1058.25 | 255 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 868.8 | 32 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17851.3829 | 611 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24458.7 | 613 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1915.76 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 61126.6664 | 692 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43965.5329 | 668 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20073.6 | 123 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.9999 | 240 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4237.5 | 226 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 125982.3331 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12433.6665 | 220 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44400 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 67559.3329 | 620 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15930.6666 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 189909.7662 | 658 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15229.4165 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51874.583 | 575 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 803.25 | 472.5 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 55434.1663 | 595 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34813.57 | 331.4 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35333.7999 | 417 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20501.9996 | 540 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144.9 | 48.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1477 | 211 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67327.8331 | 613 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 129026.3328 | 770 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 357.5192 | 18.35 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11712 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 22743.4997 | 390 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 118766.8 | 388 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3303.8166 | 167 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16572.25 | 151 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 62378.6328 | 738.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 164452.4991 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 53841.6665 | 455 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1300.8666 | 158 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 77215.9664 | 839 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3464.5833 | 125 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 37412.2498 | 747 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 37222.4998 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 9439.4998 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 64347.4996 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 567 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 7017.1332 | 268 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 42125.9999 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2533.77 | 42.3 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57675.8331 | 670 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6014.5 | 523 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15707.4332 | 523 | 1 | 1 | 1055-External superheater link tubing | U3-Forced - Postponed | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 22566.9333 | 136 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 650-Fluidized Bed
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | RFC | Summer | 9928 | 136 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 650-Fluidized Bed
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.3333 | 40 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187.5666 | 34 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 75885.8133 | 146.8 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17342.8 | 152.8 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46450.4162 | 655 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102124.3329 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13986.6833 | 107 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 15483.1498 | 243 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10853.1499 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7783.2 | 184 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2869.9499 | 171 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 315 | 75 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6760 | 104 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27266.25 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39786.5591 | 815.02 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7460.2332 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23511.9496 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 31162.5 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20258.9996 | 540 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 48340.4166 | 275 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 26250.6665 | 184 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9327.9999 | 165 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26419.4666 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 33785.75 | 745 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36167.7162 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3284.3332 | 167 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23971.93 | 495.8 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76813.333 | 560 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6142.6317 | 436.68 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6831 | 198 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22474 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17815.6996 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 34828.425 | 814.7 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16271.1998 | 258 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25342.95 | 107 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35768.1662 | 634 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1501.3265 | 203.8 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48 | 48 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 334.9332 | 128 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 114330 | 1110 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38785.6666 | 115 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12950 | 350 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1686.6666 | 200 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12994.65 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15057.4 | 158 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20387.1496 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27255.1996 | 651 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43485 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 46772.6664 | 680 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 41733.2 | 404 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 9511.3932 | 344.2 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 28580.5333 | 112 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 837071.2 | 536 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30509.2497 | 855 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 0 | 0 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148 | 148 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 336.2665 | 208 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44862.4995 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58837.333 | 560 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110659.9998 | 300 | 2 | 2 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 130.6666 | 80 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2205.4166 | 335 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1286.0831 | 305 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5313.3332 | 400 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 203575.0165 | 611 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14601.9498 | 573 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24688.35 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 52360 | 680 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8431.5 | 231 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11466.2665 | 184 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8190.5665 | 458 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 55676.4998 | 330 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73490.3114 | 736.13 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 363.7083 | 107.5 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 105.9166 | 31 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 179.8333 | 13 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 243.3665 | 298 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40863.3329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85128.3329 | 1300 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91866.6665 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22794.9166 | 115 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35117.2247 | 815.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50166.6665 | 560 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23073.9999 | 417 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4100 | 410 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28762.2991 | 558.13 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.4666 | 58 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.6332 | 158 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11069.9999 | 405 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34202.4497 | 471 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62654.5 | 745 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10885.67 | 216.2 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5296.6332 | 221 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248 | 248 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12647.7331 | 344 | 1 | 1 | 1060-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 24148.6665 | 440 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38437.15 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62940.15 | 339.3 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5399.8 | 196 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 323895.2165 | 533 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 38712.6996 | 582 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 43938.3331 | 410 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40406 | 567.5 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8400 | 350 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24558.3671 | 160.81 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8069.75 | 169 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1386 | 360 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5560.2665 | 232 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60984 | 504 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 259751.6147 | 509.7 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7043.1333 | 116 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29184 | 228 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56723.3329 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89850 | 750 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29579.75 | 661 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14091.5832 | 203 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10698.3331 | 350 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30865.65 | 593 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11429.5997 | 471 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2696.0999 | 198 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9527.75 | 115 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 57256 | 680 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61487.0663 | 616 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107930.95 | 739 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 533.3333 | 50 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48611.919 | 814.27 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16415.4 | 654 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33630.5331 | 401 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11613.4665 | 184 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.3333 | 20 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 243.0333 | 46 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16986.6666 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24624.4998 | 510 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 54867.1662 | 655 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30693.8665 | 494 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88432.6665 | 620 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 26146 | 769 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1060 | First reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 40712.8331 | 419 | 1 | 1 | 1060-First reheater | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2290 | 60 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 756.8 | 22 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45774.8662 | 658 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 199741.5 | 765 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1487.1998 | 312 | 1 | 1 | 1070-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135 | 75 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44771.0332 | 529 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166882.5658 | 1231 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42172.0662 | 694 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 150 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4992.1666 | 110 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 93195.6664 | 770 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 65846.25 | 675 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 181.6667 | 50 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4005.0665 | 184 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 436669.3328 | 785 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.6666 | 50 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14949 | 110 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28161.705 | 815.1 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 58072.4998 | 675 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.8333 | 50 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 84177.333 | 560 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 766.6666 | 200 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 280253.1662 | 658 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97392.1664 | 770 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13986.3833 | 199 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.7913 | 63.16 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 753.8166 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12331.0414 | 392.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11132.0499 | 201 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41902 | 511 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45170.1245 | 815.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47722 | 535 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1462 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1737.2667 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3350.6 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6940.6666 | 290 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 14627.0833 | 175 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 768.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 826 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 574.0264 | 366.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 46039.6498 | 279 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9648.6 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13209 | 595 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 19752.2998 | 459 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146999.2547 | 770.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63526.6306 | 814.27 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36750.7497 | 855 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25653.15 | 523 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44588.25 | 855 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2394.3333 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3998.1333 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 876.2167 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2563.1833 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32933.25 | 595 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1080.405 | 47.7 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 98207.9999 | 432 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 7149.5999 | 81 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15507.2164 | 427 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5628.75 | 285 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8297.6332 | 158 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35605.9996 | 570 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 25082.0798 | 566.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2862.9333 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1185.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 959.6667 | 20 | 1 | 1 | 1080-Economizer | D2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19578.15 | 417 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62314.6665 | 635 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 31038.72 | 566.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 54823.0829 | 605 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32375.9994 | 855 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 7869.1665 | 190 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 48740.7997 | 492 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12683.7497 | 417 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20999.9997 | 450 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21021.25 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 12416.6265 | 426.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33285.2 | 692 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24880.1533 | 146.8 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3591.1497 | 801 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2942.5 | 75 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 796.2533 | 24.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 284.7 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123447.9162 | 625 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 136531.25 | 625 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2255.4 | 108 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3412.7666 | 86 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18104.4 | 564 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2682.4833 | 43 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 511.2 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 65.3066 | 126.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5269.5499 | 201 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24180 | 520 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4410 | 108 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 296.45 | 49 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 305.92 | 9.6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 25504.6666 | 335 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26338.4163 | 565 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 17710.6499 | 243 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1478.9333 | 47.2 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 1707.3333 | 40 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5895 | 524 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 141855.2664 | 836 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4443.3999 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 39034.05 | 577 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136560.6 | 1331 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2139 | 60 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2860.5 | 90 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10038 | 140 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 27237.0831 | 655 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3962.4 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5468.1666 | 86 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21114.1665 | 650 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49996.178 | 814.27 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28447.8332 | 526 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25912.95 | 609 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9812.25 | 105 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 300.475 | 10.1 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 942.3667 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12023.1499 | 201 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80145.8331 | 625 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 134504.9996 | 1350 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5339.2 | 48 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 31173.6665 | 410 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 35560.4798 | 566.4 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 20681.3314 | 406.18 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 778.3998 | 336 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1523.4833 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 647.4167 | 17 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 22957.75 | 655 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32262.75 | 585 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23203.1795 | 815.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 20819.9997 | 450 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 49389.9998 | 330 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 57446.2499 | 225 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 16896 | 256 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 650-Fluidized Bed
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 729 | 27 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 33.8 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1760 | 40 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1701 | 27 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 370.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1384.29 | 24.3 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1247.35 | 30.3 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 305.5 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1248 | 26 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 286 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 364 | 13 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1288 | 28 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 560 | 28 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 157 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 672.4666 | 28 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2962.4999 | 90 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 22498.8664 | 349 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 131153.7497 | 525 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 599.8331 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 78723.7498 | 315 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 61116.9166 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 3146.5831 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 58422.75 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 981.0831 | 305 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1562.7499 | 285 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 134.3332 | 260 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 308.75 | 95 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 14890.5 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 18837 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1012.5 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 6466.3333 | 95 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 26472 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 35213.9999 | 90 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 53600 | 160 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 48 | 48 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14234.6663 | 544 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32766.6664 | 400 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 111356 | 560 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25613.75 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34608.333 | 500 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 48010.7198 | 557.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5933.333 | 500 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64584.1732 | 311.8 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 898.25 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1437.3333 | 16 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31235.3664 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99917.8664 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1093446.7498 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3802.0332 | 167 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35273.5664 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 62015 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10741.4666 | 104 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8239.8665 | 426.2 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 40620 | 400 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197042.1 | 758 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7671.2499 | 255 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266.6666 | 128 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 297.5666 | 158 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60782.6329 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162456.6664 | 650 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61326.3 | 742 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 100608.4498 | 747 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 965.6167 | 22.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 13743.5829 | 605 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 42813.8329 | 605 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1066.6666 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 194.2666 | 188 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 11150.43 | 82.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20800.3096 | 557.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28228.0665 | 458 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56603.7 | 654 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61629.9162 | 677.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 296887.8995 | 762 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 76536.75 | 615 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.9466 | 99.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1374.9999 | 150 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248 | 248 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 162.4999 | 195 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231317.7995 | 762 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42047.75 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 18410 | 75 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 14828.7499 | 75 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 38756.3499 | 183 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 3055.25 | 605 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 22081.6828 | 761 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 54569.9997 | 765 | 1 | 1 | 1090-Other boiler tube leaks | SF-Startup Failure | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82766.6665 | 650 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23850.75 | 245 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 883.75 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21222.5 | 650 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42469.25 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 47569.8331 | 610 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53721.1615 | 307.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40332.0162 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1091.5667 | 22.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 165197.8765 | 650.3 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 244264.5 | 765 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148 | 148 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 727.2 | 16 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3768.3333 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7265 | 100 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16599.8665 | 184 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35354.2081 | 677.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92862 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 24247.4999 | 450 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 896.1333 | 52 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1200.569 | 247.54 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 11771 | 79 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34071.25 | 702.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 28951 | 340 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28275.4165 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13990.3216 | 334.43 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3787.7458 | 18.35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104.4 | 58 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 283.1 | 298 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 250 | 120 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79893 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3852 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30923.7831 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115021.4997 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37165.3331 | 616 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17856.0833 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57176.5 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35675.7 | 654 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161557 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12981.4666 | 167 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21864 | 240 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36044.5165 | 593 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.4333 | 98 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 920.8 | 16 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12395 | 268 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22542.8059 | 206.31 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3881.3333 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1092951.7498 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145043.2497 | 495 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6253.7186 | 77.27 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12928.4997 | 459 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29651.0499 | 363 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32242.5 | 450 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70267.8066 | 234.2 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46436 | 520 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 51321.6662 | 742 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 5.25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.4566 | 144.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 847.3332 | 248 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1844.25 | 45 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 3473.1 | 18 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4042.6666 | 80 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57705.3 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 63756.2662 | 691 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53929 | 677.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36366.0162 | 661 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2051.4583 | 22.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104548.25 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116.53 | 54.2 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1372 | 28 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222018.4828 | 773 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34916.1329 | 614 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55125.7996 | 606 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 49599 | 330 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 45.3333 | 85 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 339.3333 | 40 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 342.9999 | 210 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 59730 | 330 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 287.3333 | 40 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 76614.9998 | 330 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 950.4167 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2996.7 | 21 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 396.5 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 162.1367 | 38.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 565.1333 | 17.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1022.84 | 27.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 231.25 | 25 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2754.5166 | 69.5 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 10893 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 2196 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 6215.9999 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 14890.5 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 485.1 | 18.9 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 3252 | 90 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 32508.25 | 85 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.4166 | 49 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 395.8333 | 25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 501.25 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1828.5 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 8184 | 66 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2689.75 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1386 | 21 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460 | 20 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1162.91 | 314.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 322.9167 | 25 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 4679.9 | 6 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64949.9999 | 450 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16228.3331 | 350 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 364.5833 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 26364.5 | 670 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 577.5 | 330 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 90.39 | 6.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 930.8405 | 6.13 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78301.5332 | 532 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4633.5 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14531.9998 | 504 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29399.4163 | 499 | 1 | 1 | 1100-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18482.6663 | 580 | 1 | 1 | 1100-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.3333 | 40 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.5 | 15 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 915.75 | 366.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19385.05 | 841 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1491 | 30 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 462 | 42 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12987.4995 | 750 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1098.9 | 366.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D2-Forced - Delayed | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 468.4333 | 94 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3994.0833 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 146.6293 | 6.08 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14543.1 | 198 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 12723.6 | 552 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11439.8 | 188 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1202.63 | 5.8 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 28 | 35 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1031.2833 | 43 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1751.45 | 23 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2155.8666 | 46 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2207.2333 | 46 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3311.2333 | 46 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 114.6167 | 23 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 173.3333 | 40 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 40 | 20 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 20 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30 | 10 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1103 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80 | 10 | 1 | 1 | 1103-Steam generating tubes between steam drum and mud drum | D2-Forced - Delayed | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 259.0333 | 19 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 103.1333 | 17 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 136.5 | 26 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71.4 | 28 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 892.3667 | 19 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.8 | 26 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 69.75 | 27 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 460.6167 | 29 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20566 | 280 | 1 | 1 | 1105-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 75.9667 | 2 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 43.3333 | 5 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 574 | 30 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 650-Fluidized Bed
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26545.5 | 510 | 1 | 1 | 1120-Convection pass wall | U1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4842.6666 | 320 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17421.4665 | 193 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1453.062 | 60.84 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11727.6 | 116 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13255.8833 | 193 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1487.4997 | 375 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82726.1665 | 395 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1147.9166 | 25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1513.1 | 6 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1230.98 | 10.09 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1520 | 380 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 507.1 | 22 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 881 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1660 | 25 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 14894.1 | 247 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2034.05 | 17 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 714.1667 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2318.15 | 6.53 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6220.95 | 201 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6516 | 60 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156 | 8 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3760.1667 | 14 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1350 | 150 | 2 | 2 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1585 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2043 | 10 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 471.4667 | 10.4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8169.1999 | 156 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1313.8 | 12 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1474.2 | 210.6 | 2 | 2 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1425 | 20 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 719.4167 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2516.2 | 46 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 459.4 | 229.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 584.1 | 194.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 838.95 | 239.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1540.37 | 57.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3 | 3 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1189.9998 | 600 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4264.9166 | 305 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1198.5 | 102 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 969 | 193.8 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29714.2833 | 151 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 384.25 | 145 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 614.1 | 204.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1937.5 | 310 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21861.1164 | 814.7 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 472.5 | 315 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 615.9166 | 95 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 659.1 | 219.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855.6664 | 340 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2674.95 | 314.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3501.87 | 67.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 221.5 | 30 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 617137.6665 | 620 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 253.1666 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.525 | 164.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 777 | 370 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 838.2165 | 264.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4446.9 | 72.9 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 276 | 138 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304.02 | 11.26 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 187.8 | 36 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1393.1 | 3 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1485 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 899.1 | 299.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1423.4266 | 282.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1968.6333 | 77 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 639.8899 | 314.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38233.4999 | 255.6 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.5333 | 52 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18774.9999 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 482.6082 | 199.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 689.1 | 229.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1528.3333 | 28 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 186 | 31 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1789 | 178.9 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3612.9166 | 145 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.1633 | 27.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68 | 3.4 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 599.1 | 199.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2096.01 | 299.43 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 10.2 | 3.4 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 200.75 | 15 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3241.9999 | 120 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124 | 62 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 370.575 | 164.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3443.9166 | 57.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4924 | 120 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 109.7249 | 119.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1320.8 | 165.1 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6542.9783 | 86.3 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 10 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2355.99 | 336.57 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 4702.5333 | 52 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6671.6833 | 151 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7624.4 | 56 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 989.01 | 299.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1258.8 | 314.7 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 5 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1702.02 | 283.67 | 1 | 1 | 1150-Second superheater | D2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2605.02 | 236.82 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1525 | 305 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1794.9999 | 300 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1750 | 250 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 156021.6658 | 1300 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 542.5 | 310 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 5 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29547 | 245 | 1 | 1 | 1150-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 286 | 13 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 800-Miscellaneous
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29364.66 | 48.06 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.25 | 9 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 554.2 | 51 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1467 | 15 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.5167 | 7 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 615.3333 | 10 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 184.875 | 22.5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3880.8 | 144 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 383.4 | 36 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1047.6 | 194 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2189.6667 | 20 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2574.85 | 23 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2232.6666 | 40 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1224.3833 | 13 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2047.5 | 130 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57541.4 | 644 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 379.9 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10585.7685 | 23.49 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.9867 | 16.4 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10579.2 | 55.1 | 1 | 1 | 1160-First reheater | D3-Forced - Postponed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 784.2 | 12 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 288 | 36 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4830.3666 | 314 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 41461.7 | 427 | 1 | 1 | 1170-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 181.3 | 74 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 309.3999 | 156 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1908.2 | 12 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3545.25 | 435 | 1 | 1 | 1170-Second reheater | D3-Forced - Postponed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 131.7333 | 76 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2322.6 | 126 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5475.3333 | 86 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.1 | 194 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 742.4666 | 172 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 537.6 | 144 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25123.6665 | 226 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1663.9999 | 195 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 640.9333 | 76 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5965.2 | 12 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 177.2165 | 217 | 1 | 1 | 1170-Second reheater | D3-Forced - Postponed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2157.8665 | 289 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2182.3665 | 199 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.7333 | 22 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2215.9333 | 86 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 255.9999 | 96 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1570.7999 | 99 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190.4 | 12 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1067.4333 | 62 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 53411.3663 | 529 | 1 | 1 | 1170-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.0832 | 192.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 275.1665 | 317.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 713.5 | 15 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 151.6666 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 855.8333 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6000 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 50 | 1 | 4 | 1180-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13515.8333 | 50 | 1 | 1 | 1180-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3271.6666 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.3749 | 187.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 420.4666 | 28 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17306 | 340 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.75 | 45 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.8333 | 65 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12283.75 | 75 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1042.1249 | 157.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33.8333 | 58 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.8666 | 92 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 131.9999 | 180 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 378 | 60 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1035.8333 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 261.6667 | 25 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1291.6666 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 344.1667 | 50 | 1 | 1 | 1180-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 22.2 | 37 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 585 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7238.3333 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 148.75 | 297.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 697.5 | 50 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 185.8333 | 50 | 1 | 1 | 1180-Economizer | D3-Forced - Postponed | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212 | 20 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 500 | 100 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1053.3332 | 200 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 761.95 | 21 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2567.25 | 342.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 775.5 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 106 | 53 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 200.75 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 212 | 48 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 422.1 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 680.8666 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 978.9666 | 43 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2075 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 283.3333 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2368.3333 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.04 | 3.46 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1086.92 | 18.74 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 544 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 20 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 176.15 | 39 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 308.75 | 19 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 324.3333 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 514.5833 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2456.25 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3357.3333 | 160 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3016.6665 | 500 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1859.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 380.2667 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 947 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 96.25 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 275 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3474.1166 | 59 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 165 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 13.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 197.7667 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 233.6 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 489.5667 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 668.8633 | 68.02 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2065.5 | 135 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 243.6 | 348 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 681.1 | 97.3 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 812.8333 | 10 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 693.12 | 14.44 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 42.4333 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 44.1 | 49 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 416.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 782.4 | 48.9 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1020 | 90 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9831 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7832.75 | 85 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 329.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 52.8 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 86.25 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 645.5333 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 694.7667 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 821.25 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 48.1666 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4653 | 44 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 463.6666 | 65 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8691.3813 | 91.36 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 960 | 160 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 825.4167 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 970.2 | 107.8 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17.2 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 19.8167 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 939.5333 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 942 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1172.5 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 364.5833 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2184.5833 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4644.5 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 42 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 43.4 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 310.3333 | 14 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 422.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1018.4 | 48 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 121.8333 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 281.4166 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 484.1667 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2002.5 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1832.936 | 17.04 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.0133 | 0.1 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 25.5 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 258.0833 | 19 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 279.3666 | 58 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 287.2 | 48 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 238.3333 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4082.1833 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 8602.9166 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 730.2499 | 172.5 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 408.0133 | 14.2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 55.6 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 189.1 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 70.5667 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 83.25 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 164.6667 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 573.3333 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 673.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 13261.4 | 122 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 27.2 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 588.98 | 12.02 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 24.75 | 27 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 107.9167 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1178.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 43.6 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.5 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 111.1 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 262.5 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 455.1 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 56.3333 | 26 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2030.4166 | 55 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2581 | 60 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1809.7799 | 250.2 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 53.35 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29320.2998 | 606 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 503.8 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 76 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 123.4333 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 179.8 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 324.2667 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 724.8 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 223 | 10 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.1667 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 82.65 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 84 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 539.9166 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 32.5 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 33 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 148.7333 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 696.7333 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 113.3333 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 575.25 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1477.5 | 50 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 870.5358 | 352.92 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 33.3333 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 110.6833 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 17.2 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 58.05 | 43 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1568.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 13.3333 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 15.8333 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 685.4167 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1576.6665 | 236.5 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.7 | 4.2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.2367 | 180.29 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1161.2 | 290.3 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 150.8 | 26 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 183.0333 | 34 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 605.4 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 895.8333 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1092.0833 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 576.0833 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 610.6666 | 40 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1117.5 | 45 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3245 | 44 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 137.02 | 5.27 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 536.9 | 21 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 215.0833 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1506.05 | 21 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1196.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 383.75 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1191 | Bed agglomeration (FBC only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 1616.875 | 37.5 | 1 | 1 | 1191-Bed agglomeration (FBC only) | U2-Forced - Delayed | 650-Fluidized Bed
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182.0332 | 254 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 572.3333 | 34 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17941.5999 | 123 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.1666 | 154 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2736 | 114 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 637.3333 | 160 | 1 | 2 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 536.6666 | 70 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6648.75 | 27 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 27258.8499 | 123 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12748.6333 | 154 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1380.3832 | 277 | 1 | 3 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.2166 | 317 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1986.1165 | 443 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 121.5 | 16.2 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 72 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1385 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.3999 | 228 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3960.2497 | 465 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 252.0933 | 14.6 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1055.9665 | 401 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7823.2666 | 239 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8548.75 | 25 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10506.4 | 184 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22225.8332 | 179 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 610.6666 | 160 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2216 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3078 | 120 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5362.8 | 123 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3490.3333 | 74 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 640 | 160 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 187 | 34 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11873 | 124 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17198.9166 | 179 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 804.6333 | 202 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1657.3832 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1657.3832 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 929.0666 | 104 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 29249.4 | 123 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108143 | 49 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2086.8999 | 123 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 864.1166 | 139 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5236 | 119 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17176.0165 | 259 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 578.6666 | 124 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6670.95 | 99 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 131.5999 | 84 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1041.25 | 119 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7623 | 154 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10523.3333 | 154 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168.3 | 99 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 806 | 124 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5650 | 50 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 8.2 | 8.2 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 206.8333 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 800-Miscellaneous
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 396.3 | 6 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 800-Miscellaneous
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 142.5833 | 5 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 800-Miscellaneous
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 965.6 | 6 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 800-Miscellaneous
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 497.5666 | 149.27 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 771.35 | 154.27 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1540.1866 | 165.02 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 21983.411 | 184.27 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1210 | Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 777.08 | 194.27 | 1 | 1 | 1210-Operation at reduced power to avoid slagging or fouling on waterwalls (Furnace walls) (use codes 1100-1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19451.25 | 585 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2362 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 875.3333 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 377.4 | 68 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 850-Combined Cycle Block
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 249.86 | 161.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 322.3399 | 136.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1008.54 | 86.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 5602.0832 | 125 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 945.01 | 156.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1106.2333 | 86.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1551.6 | 86.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1804.65 | 136.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 408375.3733 | 86.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 163.0933 | 111.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 207.4 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 635.1 | 58 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1820.2333 | 58 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2501 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 443.1 | 63 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 6651.09 | 30.15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1150.8 | 63 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2402.3833 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1484.6666 | 68 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 374 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 424 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 347.0333 | 58 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 773.75 | 15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1590.3 | 62 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1238.25 | 65 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1627.4579 | 702.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 236.3 | 17 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1800.25 | 57 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 328.65 | 63 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 386.3333 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99.1666 | 59.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 333.6666 | 55 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9162.7332 | 167 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5149.9165 | 426.2 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 83.4166 | 65 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 584 | 60 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.5333 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 913.5 | 63 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1181.625 | 57.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348 | 58 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 201.5 | 62 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 453.3333 | 64 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2940.2 | 61 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657 | 54 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1340.0166 | 37 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44152.2711 | 897.1 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.9833 | 59 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 912.3 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2170.8 | 30.15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 559.8667 | 26 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 128.9866 | 138.2 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 87.7333 | 94 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33932 | 680 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 160 | 80 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 394.6666 | 80 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 482.1666 | 263 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 705.4667 | 26 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 423 | 30 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2138.4999 | 390 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 17575.1 | 362 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12037.0163 | 487 | 1 | 1 | 1360-Boiler drains system | U3-Forced - Postponed | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6353.3165 | 497 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 17261.9996 | 540 | 1 | 1 | 1360-Boiler drains system | U2-Forced - Delayed | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1251.25 | 32.5 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 650-Fluidized Bed
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 4452.6531 | 607.18 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 24259.1999 | 342 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 4144.7466 | 277.55 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 188.408 | 452.18 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Summer | 618 | 72 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 619.7333 | 166 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 4446 | 152 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 4450.6 | 154 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 648 | 72 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 414 | 46 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 386.25 | 45 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 173.9999 | 180 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1419 | 33 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 4721.5666 | 163 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 852-CC steam units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 960.0333 | 83 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 860-Co-generator Block
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178.6666 | 160 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 226.1333 | 53 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1759.5998 | 498 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20266.6666 | 200 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3 | 1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.6667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 366.6667 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 651 | 9.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 800.1 | 12.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2765.8966 | 60.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16.7 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 44221.8333 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 20078.9999 | 108 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4600 | 400 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 29 | 14.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3527.211 | 379.27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23 | 11.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1675.7333 | 32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4228.6833 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4248.5 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 57.6 | 48 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 275 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 462.4 | 102 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 758.4 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2542.8 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 94026.2498 | 321 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 95507.1333 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 64.6667 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 92.0833 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 52602 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3879.7167 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 956.7998 | 552 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 252 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 146535.3332 | 146 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 192739.2 | 544 | 1 | 1 | 1400-Forced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24.99 | 8.33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.9333 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96 | 45 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285.1667 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 942.3555 | 29.13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1605.8333 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35275.6332 | 257.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1058 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 108012.9166 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 182.7167 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 315.6333 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21723.7666 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 562.1 | 42 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 370.4999 | 90 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 135340 | 536 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 58.9928 | 75.31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61 | 15.25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.8 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 398.3333 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1035 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1634.15 | 14.21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3899.5833 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7981.1667 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14880 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 13956.0166 | 49 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.75 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.4 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2805 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 218.4 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9072.5 | 190 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209.95 | 39 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 402.7333 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 517 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2794 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 158.08 | 8.32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1085 | 70 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3150.9333 | 211 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 249.1667 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 91723.0999 | 294 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 986.4 | 108 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.2666 | 64 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1690.02 | 187.78 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.9945 | 30.69 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 139.3333 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 649.8333 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 50230 | 60 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63.7333 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 111.15 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 136.4 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 189 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 72.9166 | 87.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 144791.2 | 48 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2175.3332 | 502 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11269.5 | 33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48 | 16 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 46 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 367.2 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 561.5667 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1363.4833 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2462.447 | 18.42 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4653 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2637.74 | 317.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16524.2 | 58 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 70800 | 200 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.8 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 323.6 | 404.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 38858.333 | 500 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 181.5839 | 209.52 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 41854.1498 | 741 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 466.65 | 183 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 998.483 | 431 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.7333 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 713 | 31 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1404.5307 | 29.18 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2645.2833 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5837.6665 | 422 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 115.9667 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 186102.9333 | 32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5507.5666 | 127 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 30017.5 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5696.585 | 897.1 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5979.8525 | 25.05 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 596.9165 | 247 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 892.2666 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 791.7 | 63 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 856.4166 | 43 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.4966 | 141.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335.25 | 45 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.1 | 39 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2068.0075 | 29.55 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13486.5 | 37 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 62.8333 | 130 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 73.2 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 18.0833 | 77.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 390.45 | 57 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9273.5 | 34 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 115550.7665 | 479 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4880.7 | 33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1 | 1 | 1 | 2 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 1 | 1 | 2 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.9993 | 36.92 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95.8 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.95 | 7.93 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480.0833 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855 | 54 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 959.7845 | 28.41 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1192.8667 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2043.8 | 44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3074 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1672.3997 | 444 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1952.4998 | 330 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2846.9331 | 628 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1863.1733 | 17.44 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 110.75 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3.8667 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17.6333 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 340 | 34 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 477.45 | 27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 47410.1667 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4330.3175 | 208.69 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41 | 8.2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.5 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 747.5233 | 22.04 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 761.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 45455.3 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1584.8 | 113.2 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5216.4 | 552 | 1 | 1 | 1400-Forced draft fans | SF-Startup Failure | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 487.2 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5362.9333 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3137.2 | 506 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21210 | 60 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33590 | 60 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 37 | 7.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2160 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 57916.86 | 222.8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16090.8 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 39333.3333 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 78.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 199.3333 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 1330.1999 | 108 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 975 | 78 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.5 | 94 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120.6 | 54 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793.9167 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 802.7879 | 379.27 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 233503.3666 | 62 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 35 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60.4 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 232302.5331 | 284 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5715 | 635 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1105.0666 | 112 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2 | 1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.4 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 594.8166 | 89 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.97 | 7.11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 562 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1344 | 56 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1449.5833 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1723.3333 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4060 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6843.6 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8645 | 60 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27533 | 60 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 165 | 55 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 116664.5333 | 88 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.95 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 75.6 | 8 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 201.6 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 983.916 | 32.58 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1306.5 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1706.6666 | 320 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.2815 | 13.73 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.9833 | 17.05 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128 | 6.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 154.8333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1499.9999 | 180 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 680 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 38.1333 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 518.3166 | 227 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2501.6666 | 76 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1022.2667 | 44 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 41.5333 | 14 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 20.4 | 18 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 650-Fluidized Bed
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 330.3667 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1116 | 62 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 272.1333 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1991.175 | 69.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 107.6666 | 85 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 25.8332 | 310 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 650.44 | 70.7 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 20.5333 | 7 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4458.5331 | 562 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1449.6 | 64 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 63.0667 | 8 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.25 | 15 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1107 | 246 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.85 | 91.4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1704.3 | 437 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20.75 | 3 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 525 | 28 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 18.318 | 8.52 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.3333 | 65 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1809.5 | 55 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 606.7466 | 74.6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 145.0333 | 229 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18616.4997 | 405 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 453.8366 | 78.7 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1021.883 | 461 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2143.7499 | 105 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 988 | 520 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 466.6666 | 80 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11818.75 | 75 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 64.2667 | 8 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4092 | 341 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8005.3333 | 76 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.85 | 41.4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 125.0667 | 4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6123.333 | 440 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 368.375 | 52.5 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1049.9999 | 180 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 829.25 | 107 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1154.6666 | 80 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 514.4333 | 61 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57.8667 | 16 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 994.5 | 221 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1831.3332 | 268 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2124.9997 | 510 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1045.3333 | 40 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 872.083 | 455 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5243.3332 | 520 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30.9 | 6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1093.3333 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 47.9833 | 1 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 76.7467 | 3.2 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1115 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 413.6666 | 85 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 262.5 | 35 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 2156.7 | 182 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1056.6666 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 460 | 40 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | NULL | NULL | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 3617.94 | 61.2 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 861-CoG GT units
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18362.4999 | 390 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22284.1332 | 194 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 300 | 125 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 123.75 | 275 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 804.6 | 298 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1600.56 | 307.8 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2255 | 410 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 38.4583 | 32.5 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 650-Fluidized Bed
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8223.6 | 308 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1371.2 | 96 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37945.4833 | 91 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 564455.2665 | 322 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4978.4 | 48 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 388.1333 | 41 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 740.3499 | 201 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 177461.4999 | 291 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21960 | 800 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138112.7998 | 504 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 796.0332 | 167 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9844.5332 | 152 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 33723.7 | 56.3 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 55836 | 88 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 88.2166 | 67 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 710.6733 | 176.2 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7199.25 | 87 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7080 | 400 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264.5833 | 127 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1845.5333 | 38 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 540.4167 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 81 | 15 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1967.0998 | 747 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 62867.85 | 321 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 263.8998 | 226.2 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 15555.1498 | 351 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 748.6333 | 37 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 837.9 | 114 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6639.7333 | 56 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1652.6666 | 134 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3424.8 | 48 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8878.55 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64981.35 | 757.8 | 1 | 1 | 1410-Forced draft fan motors | U3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1644 | 240 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 23782.9332 | 152 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1334.4 | 278 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1377.6 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23145.75 | 127 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 683.3333 | 125 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 39432.1666 | 146 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14095.4166 | 25 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 67.5 | 18 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2480.4999 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3720.4332 | 239 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5065.77 | 257.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7341.3665 | 431 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 14.4666 | 31 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15433.7666 | 46 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 348.5 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2457.95 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31669.5833 | 52.6 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 384188.1333 | 232 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 65682.6332 | 322 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10381.5125 | 18.35 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 116.5333 | 46 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 110573.7664 | 433 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5106.2497 | 375 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2999.25 | 67.5 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4862.6 | 123 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1192.5 | 90 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 46.1665 | 277 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1733.3331 | 320 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2108.333 | 500 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4626.8 | 53.8 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 42 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65033.6664 | 370 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 98.6666 | 80 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 70084.7 | 98 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122 | 61 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2226.9997 | 510 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 353.4999 | 105 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2248.5 | 90 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 39 | 90 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5957.4999 | 150 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1476.96 | 86.88 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1552.4999 | 405 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13384.7499 | 277.5 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 516.25 | 175 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 295.9999 | 222 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.4 | 35.48 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 993.2999 | 198 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 454 | 90.8 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 618.2999 | 162 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5645.7 | 123 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3393.4 | 361 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9463.9999 | 312 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 176439.2 | 343 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2944.1331 | 568 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1248 | 104 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 293.75 | 15 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7205.9164 | 385 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2501.3332 | 448 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 182 | 91 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1662.733 | 509 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 306.7916 | 92.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 903.6 | 72 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7058.1331 | 832 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1727.1664 | 430 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 133372.4998 | 450 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 274 | 24 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 30494.9406 | 148.78 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4711.4664 | 448 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10798.5249 | 91.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2085.5666 | 74 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 27645 | 285 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1318.5 | 90 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1167.1166 | 293 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 957.6 | 72 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 556.6666 | 200 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28326.25 | 425 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3015.1333 | 91 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12924.1665 | 650 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 395.6333 | 215.8 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1154.1833 | 91 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8084.2661 | 832 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 5770.1332 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2908.3332 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1291.3 | 349 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 644.9999 | 180 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 25315.8331 | 850 | 1 | 1 | 1413-Forced draft fan couplings | U1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 72450 | 525 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 106.75 | 21 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 779.1332 | 150.8 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3116.6333 | 38 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 750.8333 | 85 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2747.3999 | 342 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 867.1665 | 605 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10660 | 520 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 238.3332 | 260 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3840.48 | 604.8 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 475.9333 | 118 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.9999 | 153 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26.15 | 3 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86.1665 | 235 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 129.8 | 118 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3997.7445 | 178.87 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.5 | 370 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3463.1998 | 351 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 403.0997 | 417 | 1 | 1 | 1415-Forced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 223.7666 | 98 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 268.2748 | 328.5 | 1 | 1 | 1415-Forced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 896.4832 | 361 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 558.1333 | 208 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 30 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10348.5 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1050 | 750 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9272.9497 | 490.2 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 49.4666 | 28 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2235.9 | 58 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.5665 | 262 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.9 | 134 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1976.92 | 89.86 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7429.3331 | 320 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 192 | 32 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257 | 128.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.0933 | 40.1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.285 | 14.1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 153.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1726.5 | 115.1 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.7995 | 73.41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61598 | 38 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5444.45 | 209 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 460.7165 | 359 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 903.8333 | 85 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 52.5 | 30 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 552 | 184 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10296 | 198 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21371.028 | 59.43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 322.7666 | 46 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1151.2 | 48 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47199.75 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 61.6666 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 151.6667 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23.3333 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4606.1333 | 46 | 1 | 1 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1444.8 | 51.6 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4847.9164 | 325 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7915.8053 | 10.64 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 383.3999 | 324 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2236.4997 | 378 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 709.0666 | 106.36 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2789.44 | 15.16 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 155 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7427.0832 | 155 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 163.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2042.6999 | 198 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1753.2664 | 442 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5401.5 | 554 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2060.5 | 65 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 70.5 | 141 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 230.3333 | 20 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1335.9 | 438 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 60.9166 | 85 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 938.7164 | 373 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1897.4999 | 198 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1795.8332 | 250 | 1 | 1 | 1420-Other forced draft fan problems | SF-Startup Failure | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3138.0065 | 14.01 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1940.4 | 198 | 1 | 1 | 1420-Other forced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 705 | 50 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1750 | 35 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 426.8332 | 394 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 84.4905 | 18.17 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 15991.6663 | 505 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1434.86 | 22.16 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Off-Peak | 184.5332 | 173 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Summer | 891.6667 | 20 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 638 | 11 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 2184 | 26 | 1 | 1 | 1421-Secondary air fans/blowers | D3-Forced - Postponed | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 650 | Fluidized Bed | TRE | Off-Peak | 2820.9999 | 105 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 650 | Fluidized Bed | TRE | Summer | 2099.5 | 130 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 8.73 | 2.91 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 97.5 | 25 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 483.6 | 24 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 271.25 | 25 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39279.3332 | 332.5 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 125.32 | 19.28 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 1.2907 | 0.64 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 650-Fluidized Bed
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1094.35 | 43 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 800-Miscellaneous
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 87.4 | 23 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 800-Miscellaneous
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 1002.5 | 50 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 248 | 31 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 800-Miscellaneous
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 210 | 35 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 800-Miscellaneous
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 363 | 33 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 800-Miscellaneous
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1696 | 32 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 800-Miscellaneous
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 4217.0333 | 22 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112 | 60 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1062.815 | 51.22 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.9333 | 86 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 373.89 | 72.6 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 22385.3 | 566 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 19240 | 65 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 585 | 78 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 21890 | 110 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 39266.7733 | 46.4 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 220 | 110 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 203856 | 274 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1409.0133 | 46.4 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 651.192 | 271.33 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 254589 | 339 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1401.6 | 128 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 410.1666 | 107 | 1 | 1 | 1431-Air supply dampers from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1564.5 | 90 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 8591.4665 | 362 | 1 | 1 | 1432-Air supply duct expansion joints | SF-Startup Failure | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 7269.4998 | 465 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 19612.5 | 750 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2145.7333 | 76 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13141.4166 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 2815.8332 | 155 | 1 | 1 | 1432-Air supply duct expansion joints | U2-Forced - Delayed | 650-Fluidized Bed
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 127.5066 | 58.4 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 345.5332 | 292 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 70 | 200 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 607.6999 | 177 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 148.1667 | 35 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 914.9332 | 292 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 263.9333 | 107 | 1 | 1 | 1440-Air supply dampers | U1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196 | 49 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 443.2 | 277 | 1 | 1 | 1440-Air supply dampers | D2-Forced - Delayed | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 30832.1067 | 47.6 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 35.9955 | 37.89 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.97 | 14.2 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1533.1333 | 58 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 813 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 69462.5666 | 74 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 110666.6 | 34 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 743.4 | 531 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564 | 72 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 148.1667 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.8333 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 358 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2162.3333 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 87762.1333 | 64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 110.3617 | 2.3 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 110.8333 | 175 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.75 | 45 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 195.7066 | 32.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 620.4 | 52.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2755 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 80.3833 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 402.5 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15896.5333 | 64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.75 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 414.54 | 37.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1671.18 | 82.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87725.8664 | 379 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 67.15 | 17 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 185.15 | 2.3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178.94 | 77.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 180.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.6666 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1744 | 32 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2361.7 | 57 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 190383.6 | 36 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.9 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3034.75 | 61 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.7333 | 57.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 707.3333 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 731.28 | 52.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 811.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 36.8 | 16 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8848.4333 | 31 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 47.65 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16733.8666 | 64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 512.5 | 12.5 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.75 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 285.3333 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 420.6666 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 863.6249 | 157.5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 44.95 | 29 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 8500.8 | 16 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1012.5 | 405 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242.5 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 345 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 26 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 191.9333 | 4 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.3333 | 71 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.5466 | 47.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2093.1166 | 107.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 322 | 4 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 199206 | 62 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 785.4 | 11.9 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 854.4 | 9.6 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 160 | 20 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 255.7333 | 56 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 880 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 9458.7999 | 204 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16.25 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 91.8667 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 243 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 84881.0667 | 32 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 248.7666 | 87.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 143.95 | 3 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 460.1996 | 531 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.1667 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 199.5 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1094.9667 | 42.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 452.4 | 7.8 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8.05 | 23 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23 | 60 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 276.6866 | 107.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 105.3 | 1.3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32767.2 | 738 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49 | 30 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 503.9 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 162 | 2 | 2 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3.7973 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 167 | 16.7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.032 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 0.72533 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 2.2933 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 20.5547 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 118.6666 | 40 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.21333 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.29867 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.512 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 0.864 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1820 | 35 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.4333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 113.125 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 565 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1018 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2106 | 162 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3294.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8325.9 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9054.975 | 47.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31898.475 | 47.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.0417 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.9167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.0167 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.4917 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 219.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 237.5 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 424.8 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 547.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 549.2667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1060 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1133.2 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1431.4767 | 6.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2024.583 | 18.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2102.1 | 100.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2855.4333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3021.3 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28608.3 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 56982.092 | 190.48 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14.6667 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 15.4417 | 10.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 108.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.2 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 303.4083 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1526.25 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5168.3331 | 350 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8175.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 562.25 | 19.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 287.5 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798.2832 | 227 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 280 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 360 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 600 | 200 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 842.5666 | 157 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1608 | 67 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11905.8331 | 350 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 832.9999 | 420 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4285.8833 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48981.8333 | 37 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.15 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 109.6333 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 324.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.1 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 219.6333 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 394.45 | 21 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 413.6 | 44 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2119.3332 | 340 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 229.1666 | 110 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2570 | 200 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2572.9165 | 247 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.3417 | 40.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4.5 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.625 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 212.5 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 227.55 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 484.7917 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 720.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4489 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4968.2497 | 501 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 10935.4666 | 233 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.7505 | 18.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.08 | 4.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36.3 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.2333 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.1 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.59 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.4965 | 19.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 159 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.55 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 194.3166 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.4 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 335.9167 | 14.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 353.8333 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 651.2 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 856 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 890.7 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1268.2 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2436.4882 | 22.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4160.8333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12559.1666 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64061.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 297.5 | 350 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1122.4999 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1406.3 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3377.3333 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 797.8667 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4986 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.5 | 42 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 932.4166 | 167 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.8667 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 472.6833 | 79 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 62.05 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 152.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 269.7 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1481.35 | 39 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.9 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 139.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 144.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 181.7833 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 249.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 395.45 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 630 | 30 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2419.2832 | 379 | 1 | 1 | 1455-Induced draft fans | SF-Startup Failure | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.3999 | 162 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51435.7994 | 876 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 654.1664 | 785 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1703.52 | 608.4 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6.75 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.65 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 108.3333 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128.3333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 426.6167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2468.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4635.9998 | 570 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.9 | 9.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.1555 | 18.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 38.9583 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.98 | 0.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.4 | 4.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 152.95 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.0733 | 9.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.45 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 346.2666 | 53 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 399.9667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 468 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 520 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 589.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 698.4 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1082.7667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2376 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 77148.8333 | 73 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1231.95 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8407.35 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1505.2665 | 268 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 27861.75 | 304.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 28899.7916 | 237.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 21739.0731 | 330.8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.45 | 3 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 519.9166 | 85 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 924 | 72 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 219.6333 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 293.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 958 | 120 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5326.9999 | 420 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.2 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31.9333 | 4 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 614.7166 | 77 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2130.1833 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 30 | 1 | 2 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.5 | 30 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1685.9328 | 836 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 858.75 | 75 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1.0583 | 0.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 159.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 230.9583 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7799.1833 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.13 | 0.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.71 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45.0667 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 46.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.4999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.2466 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 97.9333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 121.365 | 8.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 161.7 | 23.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189.63 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 205.92 | 35.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 244 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 260 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 300.8 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 372.8833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 396 | 132 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 525 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 772.9166 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1132.0933 | 43.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11620.355 | 47.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 96.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 190.35 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 283.4166 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 335.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1450.4 | 98 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2493.1833 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 133877.3333 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 2608.97 | 13.16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 774.2 | 196 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 332.5 | 42 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2413.3333 | 160 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.5 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 266.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 466.32 | 19.43 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 477.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 672 | 28 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 727.5 | 97 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 821.5 | 53 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 843.7333 | 32 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1222.4333 | 62 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 147.2167 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 328.2167 | 47 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.2 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 271.4333 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1863.25 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1900 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119.6 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 333.3333 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 682.7328 | 836 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 795.8333 | 50 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7749.2499 | 417 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 74.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.8333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 200 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 615 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 617.05 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1280.25 | 135 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4456.6666 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1.2133 | 5.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.7933 | 10.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.675 | 18.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.3 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.5 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 185.115 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 223.8667 | 9.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 355.6667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 630.1333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1100.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2134.8 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9222.543 | 18.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63.6333 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1237.5 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 310.5 | 27 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1552.5 | 270 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 602.7 | 147 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 379.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 439.4667 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 768.5 | 87 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 55.4 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.4 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 114.2333 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.7 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 359.4 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 599.5 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 599.5833 | 25 | 1 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1315.4 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24113.1 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 149.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 237.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7295.1664 | 370 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210 | 30 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.4 | 30.1 | 1 | 3 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 238.0746 | 63.77 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 258.5 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 286 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 294.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 313.2666 | 74 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 345.3667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5187.5 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7472 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9005.0667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9631.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10707.65 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15434.25 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20520.5 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 181223.4666 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.0467 | 17.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.6 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.1 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.25 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215.15 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 232.8667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.4333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 269.775 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 271.3333 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 271.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 334.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 340.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 343.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 346.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 373.6733 | 9.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 735 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 883.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1330 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1391.985 | 8.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24749.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 41.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 48.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 85.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 268.8666 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 603.7499 | 207 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 511.2 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 194.9999 | 117 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1050 | 300 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.9 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 885.1333 | 71 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1474.6333 | 82 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 19.1667 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.8333 | 10 | 1 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.95 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 181.7 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 248 | 32 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 259.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16515.7494 | 855 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13.0667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.7833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 92.7333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 233.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2187.7333 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2548.3331 | 275 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3505.8333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44226.6 | 99 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5767 | 2.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 78.2167 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.1 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 91.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.225 | 8.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.3833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 126.5333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 147.95 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.0017 | 20.3 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.5333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 181.5667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196.7 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 221.94 | 8.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 261.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 286.4583 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 405.5333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1114.4632 | 241.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1613.7499 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3554.4 | 14.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42490 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.1525 | 145.83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 178 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5486.25 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 12977.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 188550 | 72 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 24663.5 | 535 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.6667 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 647.04 | 26.96 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2322.45 | 117 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16615.8 | 204 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 17.85 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 56.4 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.8667 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1315.2 | 72 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9948.9333 | 58 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49.8 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.7 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 801.6667 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3311.6167 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 80.25 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 403.5166 | 31 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 764.6664 | 370 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1081.3 | 11 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 268.3916 | 30.1 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 379.9998 | 300 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15769.5497 | 417 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155.9999 | 180 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 524.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17484.1 | 58 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.5883 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.6183 | 25.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.9 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.195 | 40.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.8 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 128.7 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 161.9333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 195 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 195.5699 | 221.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225.9833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 473.8933 | 5.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 739.9582 | 147.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2516.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 579.05 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 746.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1365.1 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 73.4164 | 440.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 485.4 | 404.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.5833 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 168 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 220 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 264 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 724.5833 | 47 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2028.24 | 14.4 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.5833 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 197.7 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.2667 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 160.6167 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 96.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 97.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 152.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 505 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.95 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 694.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1680 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3460 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11596 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10.686 | 17.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.3333 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.3333 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 217 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.9 | 30.1 | 1 | 2 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 368.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1072.3999 | 84 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1479.7666 | 103 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4285.4 | 42 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9967.924 | 181.51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28079.35 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.55 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105.9917 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 138.55 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1926.1 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1983.3333 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 188 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 275 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 432 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 474 | 19.75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1795.5833 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2313.8999 | 162 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246.6833 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 582.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1175.0667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4974.4666 | 332 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8539.8 | 43 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 44.75 | 15 | 1 | 2 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 170.6833 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.5667 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 129.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 167.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 238.8167 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2387.35 | 359 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3825.1331 | 634 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12863.76 | 638.4 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30010.6664 | 680 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.6665 | 190 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.5 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 190.8 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 227 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 818.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1590 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1801.1 | 83 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3269.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 45570.9333 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.36 | 4.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.25 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.7 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 95.8333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121.8667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 137.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.8333 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.4333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 216.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 258.43 | 60.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 461.2666 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 498.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1059 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5614.5 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5790 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208412.1666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.4833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 73 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 235 | 94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1050.8333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 437.233 | 504.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1441.0914 | 434.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1559.3666 | 287 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 753.95 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 139.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 684.6333 | 47 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 815.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1154.65 | 21 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1465.1666 | 149 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 174.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 274.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3583.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 742.7833 | 41 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 807.8 | 21 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2027.9333 | 38 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18869.1998 | 552 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 554.9999 | 450 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.3167 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 539.6 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2460 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3152.4999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.36 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.5983 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50.4083 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.4917 | 25.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 167.13 | 8.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 168 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.8 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 243.1 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 504.0833 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 734.9333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3393.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6898.6666 | 260 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.875 | 11.25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 812.5833 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 891.4667 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1142.4833 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1643.28 | 5.01 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6017.3667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47899 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 95346.9499 | 177 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1471.8666 | 133 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49.5 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 943.5 | 222 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1656 | 207 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3661.8 | 204 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70.6 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 162.8 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 632.4 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 153.0667 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 192.6666 | 68 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 337.5667 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 820 | 410 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 620 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 828.0998 | 507 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6773.5 | 190 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 625.8333 | 50 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 311.9999 | 117 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1153.1666 | 37 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2629.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7923.005 | 47.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.0467 | 0.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.45 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.07 | 4.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.6 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.7167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 112.45 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 131.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.5833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 276.5 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 333.585 | 247.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342.7667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 383.125 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 395.25 | 22.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 430.3833 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 526.6666 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6317.2567 | 13.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 12 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 122.4667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 144 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3489.6667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 188.5999 | 276 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 649.75 | 69 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1479.6665 | 193 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.5 | 75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 118.5 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 761.25 | 87 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17300 | 200 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1168.4 | 69 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 91.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 101.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 199.4667 | 32 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2674 | 28 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10953.6 | 163 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 597.1333 | 52 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 791.1665 | 235 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1225.4667 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3761.3333 | 80 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10507.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15786.6 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.7083 | 40.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 53.2 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.6167 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119.7 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 138.125 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.91 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 186.875 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 241.2667 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 265.3 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 295.1665 | 253 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 322.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1010.85 | 69 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4343.0123 | 19.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7738.605 | 43.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15717 | 39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45496.245 | 47.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62901.1666 | 305 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1239.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2822.82 | 10.01 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19469.3998 | 333 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 65.7065 | 358.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.4333 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 327.5 | 131 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 371.28 | 15.47 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 513 | 171 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 815.8333 | 110 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 990 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1228.5 | 117 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 166 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 558.45 | 73 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4539.95 | 101 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1297.8666 | 248 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5920.8 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9902.2666 | 46 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 131.1 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 240.3333 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 241.6333 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1198.3333 | 100 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16223.8798 | 635.4 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 120.1001 | 63.77 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.0833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.135 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 195.8666 | 104 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 206.8332 | 170 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 240 | 160 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 250.5833 | 97 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2502.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2553.7166 | 49 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5058.1333 | 237.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12469.5 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 16608.6666 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.1667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.8933 | 9.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.9666 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.6333 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.0667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.675 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71.7333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 82.0667 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 139.7917 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320.8333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 405 | 270 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 427.4999 | 270 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 556.65 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.1 | 30.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 860 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17231.38 | 43.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21607.95 | 63 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2.2 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.0917 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 214.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1050.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2407.9999 | 168 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8918 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 702 | 130 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 488.25 | 217 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9480.0332 | 262 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.75 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 296.25 | 75 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 321.5333 | 106 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1085 | 70 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.9 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 81.0333 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1099.5833 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10033.75 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 16.6 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 181.5667 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 229.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.9 | 30.1 | 1 | 2 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 717.5 | 410 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15249.5748 | 723.3 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1077.2499 | 417 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5933.3999 | 198 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1087.5832 | 155 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 427.5 | 450 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18.125 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.105 | 20.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19567.3333 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.8783 | 0.1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26.75 | 107 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.375 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 88.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 98.75 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108.5 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.2833 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 380.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 438.7167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.3333 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2724.063 | 15.81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10668.6666 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11847.95 | 87 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0.91667 | 1 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17.5667 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1849.65 | 177 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2040 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2190.75 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1170 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 342 | 57 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 652.5166 | 49 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 255 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1581 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 709.2 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1308.9999 | 132 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 45.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 132.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.25 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7180.9999 | 258 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 154 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1329.6333 | 113 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1671.2667 | 44 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74816.6666 | 134 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 964.8 | 20.1 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2052.8742 | 183.02 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 715.8666 | 118 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 191.25 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 8.7 | 1.45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 39.4333 | 7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1.0667 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 529.55 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 128 | 32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 26.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 454 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 48.0667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 71.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 113 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 196.0167 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2065.5 | 459 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 234 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1431.5831 | 419 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3688.75 | 39 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 74 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1654.5833 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 643.8664 | 439 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 73920 | 120 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 6.3333 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 14.25 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 61.4333 | 19 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2195 | 439 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 28196.6662 | 769 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 53.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1243.8332 | 439 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 88.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 184.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 322.4667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1815.3332 | 140 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4050 | 810 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1640.175 | 575.5 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 893.9999 | 180 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 120 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1528.7999 | 144 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1964.25 | 135 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2742.9331 | 278 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1088 | 272 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10214.1666 | 50 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1437.4165 | 235 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5015.9994 | 855 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4089.6 | 568 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 435 | 20 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.1666 | 62 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1812.5 | 30 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 316 | 60 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 573.9999 | 246 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1973.3332 | 400 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1980.15 | 307 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3265.9999 | 276 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3378.55 | 147 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 885.6 | 432 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5106.75 | 619 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27819 | 330 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9897.7663 | 502 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 28086.75 | 855 | 1 | 1 | 1456-Induced draft fan dampers | U2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 821.3333 | 64 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2183.3332 | 131 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7788.45 | 137 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2205 | 450 | 1 | 1 | 1456-Induced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 146.25 | 135 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3066 | 146 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20457.8 | 51 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7100 | 25 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 258.3332 | 310 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4596.5 | 290 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 489.125 | 150.5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7447.9164 | 325 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 748.15 | 575.5 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1383.4333 | 154 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4224.3333 | 145 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 367.5 | 147 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 460.4 | 575.5 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3094.6666 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62799.4164 | 457 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2458.7499 | 105 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14143.75 | 155 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35537.25 | 147 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 237.1167 | 41 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 381.3332 | 260 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 78.5833 | 41 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1516.6666 | 65 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 286.4583 | 137.5 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7715.1999 | 96 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 396.6666 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 434 | 31 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 800-Miscellaneous
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3263.4 | 444 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1786 | 94 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 62.5332 | 469 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1154.4 | 74 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 1306.4166 | 257 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 1654.5 | 90 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 5719.35 | 419 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4324 | 94 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 4745.6663 | 619 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 414 | 184 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 264.0666 | 68 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1015.65 | 111 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4763 | 220 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6150.3897 | 790.2 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85121.9998 | 540 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7018.3994 | 849 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19615.1398 | 637.2 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29550.6664 | 370 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 707.6 | 61 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.1333 | 32 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 113.3332 | 200 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1846.9742 | 189.11 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1206.6666 | 80 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 293 | 293 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 745.8333 | 125 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 231.2299 | 365.1 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117 | 39 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1421 | 49 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 912.5 | 30 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1462.5 | 50 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510.8833 | 29 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30992.5 | 350 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1358.3333 | 100 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1074.5 | 14 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.9167 | 25 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2192 | 64 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.5 | 54 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1124.2666 | 248 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1972.8 | 96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3221.3665 | 241 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.25 | 92.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 274.16 | 44.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1658.8831 | 413 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93602.4999 | 150 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 304.308 | 12.84 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 599.1667 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 604.9521 | 209.81 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1961.4833 | 205.75 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 46.6666 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3769.2666 | 164 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3155.4332 | 523 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7883.85 | 507 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16715.8664 | 354.4 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2530 | 138 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2721.9666 | 37 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 59.6667 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 178.5 | 22.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 189.0333 | 106 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 379.9 | 262 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 143.8 | 14.38 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5217.6882 | 211.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 439.03 | 204.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5320.1446 | 209.18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 984.6666 | 140 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 151.2 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 198.45 | 63 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.75 | 227 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14772.0833 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60.75 | 15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114.75 | 17 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 460.41 | 44.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 509.8332 | 266 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 632.2917 | 12.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18500.3 | 266 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 576.05 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3921.8713 | 182.98 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 319.0425 | 15.45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1554.9013 | 33.13 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3546.9373 | 17.36 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 34.3 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1510.4 | 64 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2303.3333 | 100 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45038.6666 | 272 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2138 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82279.1665 | 350 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.1573 | 3.68 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.75 | 5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 18.0833 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 68344.4065 | 209.86 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 849.2 | 212.3 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1141.25 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 235.45 | 17 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1899.75 | 255 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2720 | 544 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27808.6665 | 280 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1776.6666 | 164 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2335.3332 | 248 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 8.7433 | 6.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 324.18 | 36.02 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 384 | 16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 677.52 | 28.23 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1048.334 | 29.08 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1604.6333 | 20.93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1395.3332 | 140 | 1 | 2 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 632.4 | 27.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1329.2916 | 261.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 148.4665 | 262 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2571.9665 | 262 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 235.41 | 24.78 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 859.56 | 18.72 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1215.2 | 248 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1698.5 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 42927.4331 | 562 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.135 | 44.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 343.0666 | 166 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 569.6667 | 20 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.9666 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 459.4823 | 13.37 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1046.5432 | 22.37 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 391.5 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34147.575 | 207.9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 232.54 | 211.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 336.24 | 18.68 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 33614.9999 | 201.69 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18608.3331 | 580 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4548.8996 | 531 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1323.2 | 96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 59355.2958 | 467.61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 443.3333 | 95 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17565.3185 | 129.49 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 295.05 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2889.579 | 250.18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4041.7166 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112070 | 350 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.396 | 14.64 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 210 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 389.8425 | 26.43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 418.4093 | 19.12 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2786.6666 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 9299.6666 | 230 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 63257 | 61 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6041.25 | 225 | 1 | 1 | 1470-Induced draft fan motors and drives | SF-Startup Failure | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 47.95 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4961.1998 | 471 | 1 | 1 | 1470-Induced draft fan motors and drives | U2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 27.1667 | 5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 613.8 | 55.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 718.3333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1194.4933 | 16.16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31.5735 | 6.51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3155.568 | 202.28 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2630 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2192.6666 | 130 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 63.8 | 132 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 500.25 | 87 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 157 | 15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 411.4 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1254.96 | 224.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8107 | 67 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 173.25 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 11.0833 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 594.928 | 18.24 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2497.8145 | 210.49 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12133.3333 | 100 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2037.25 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D3-Forced - Postponed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1729.5999 | 96 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2783 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5950 | 280 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2768.1499 | 231 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30.8333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4997.2865 | 211.6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 206.9632 | 214.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6559.9725 | 203.41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 64680 | 280 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 547.2 | 72 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2116.4666 | 212 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 81.55 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56330.6333 | 238 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 148549.6833 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.6667 | 10 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.988 | 59.56 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 374.7331 | 308 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 590 | 150 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4453.2799 | 128.46 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 132.0825 | 16.01 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 20342.4 | 208.64 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1432.0833 | 175 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1216.6666 | 146 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 111.75 | 45 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1292.0833 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.75 | 65 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.107 | 15.79 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54.45 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3927 | 140 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3973.6333 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 796.1666 | 281 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90025.8331 | 350 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.9487 | 5.72 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 83.3333 | 50 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 851.76 | 16.38 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 48.3333 | 100 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 224.2933 | 64.7 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 484.0832 | 185 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2259.2999 | 306 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3378.6665 | 362 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 237.5 | 62.5 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1870.3333 | 124 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6716.41 | 19.93 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 189 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 963.1999 | 206.4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11730 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7770.5999 | 162 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2475.0499 | 177 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 40.25 | 105 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 203.4616 | 73.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 305.805 | 10.73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 77.0833 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 337.4948 | 16.37 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 640.9366 | 32.59 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14497.9166 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 96.95 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Off-Peak | 6521.9999 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2829.9999 | 150 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 613448.3332 | 230 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 276450 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3318.6665 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1159.2331 | 419 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3414.85 | 419 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 2482.0833 | 175 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15252 | 328 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 655.4166 | 275 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.5998 | 678 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369.4982 | 209.15 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 217.0666 | 148 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3678 | 45 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 98.8833 | 17 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 420 | 120 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1891.6666 | 125 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.01 | 90.67 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810.75 | 141 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.3333 | 100 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3851.65 | 700.3 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 68879.2 | 208 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.3517 | 20.3 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 252.6796 | 91.33 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 234.9999 | 141 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7256.5832 | 265 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 950 | 50 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 4458.6665 | 220 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3052.5 | 275 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.3999 | 192 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4154.5496 | 283.91 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 415.2 | 346 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 216.6 | 19 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2122.9996 | 660 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3262.4999 | 270 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 233.3099 | 181.8 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1350 | 200 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282228.9165 | 455 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13420.4999 | 90 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U3-Forced - Postponed | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2418.7166 | 79 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.3501 | 122.39 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 390.8332 | 134 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2905.8331 | 634 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1302.4 | 148 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 469 | 140 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 817.4 | 61 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2421 | 135 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3057.6331 | 682 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2951.4163 | 535 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 307.6999 | 102 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 3423.7 | 42 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 13769 | 42 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 532.0999 | 102 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 594.3 | 42 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D2-Forced - Delayed | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 18217.15 | 7 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 591.6 | 102 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 650-Fluidized Bed
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 508.9331 | 347 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 664.0499 | 171 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22389.3331 | 320 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114174.4999 | 330 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 4411.25 | 75 | 1 | 1 | 1472-Inducted draft fan coupling | U1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1508.1499 | 325.5 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3337.5 | 75 | 1 | 1 | 1472-Inducted draft fan coupling | SF-Startup Failure | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 168.5332 | 128 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19552.5999 | 177 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.1667 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 235.8 | 108 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 402.5 | 105 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 656.25 | 525 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 222.9 | 18 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5362.9998 | 465 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.3333 | 19 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 458.1499 | 147 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 487.2167 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1735.3666 | 158 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 55.0999 | 174 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 164.8 | 12 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 12 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 625.4 | 118 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 688.5 | 170 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1562.0833 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 104.3 | 14 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 276.4166 | 107 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 67.8333 | 110 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.5833 | 35 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 394.45 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 683.3333 | 25 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1982.9 | 158 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2629.85 | 149 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 492.8 | 88 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3592.7999 | 108 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5171.6 | 42 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 66.4999 | 210 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 602.6667 | 20 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 607.2 | 16 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2021.2498 | 495 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 23621.5 | 595 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56 | 32 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.5 | 18 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.2833 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 186.4833 | 67 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 338.4833 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 637.2 | 108 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 152.3166 | 37 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 155.1 | 66 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 519.65 | 19 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20200.5 | 90 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 493.0666 | 172 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 734.25 | 165 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 798.1499 | 153 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1777.5 | 395 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2566.5 | 147.5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 12 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1408.75 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 267.75 | 153 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 501.4999 | 177 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21690.6664 | 415 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 681.4998 | 282 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.4333 | 17 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2061.8667 | 16 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5109.7666 | 122 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7425.6332 | 367 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 534.2 | 12 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1564.6332 | 146 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52 | 13 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 236.8 | 148 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1359.3 | 197 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 920.3332 | 502 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 237.3 | 21 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 307 | 15 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.1667 | 5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 373.9332 | 158 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 746.1999 | 156 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 575.4666 | 332 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.9333 | 7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6816.9333 | 172 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 663.2332 | 197 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2627 | 142 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.1667 | 19 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1558.3331 | 374 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 69.4166 | 85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 38 | 7.6 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7908.75 | 855 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.3333 | 80 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 342 | 152 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20636.5831 | 595 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158 | 158 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.25 | 42.5 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 434.1333 | 88 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 664.4 | 66 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9197.1 | 66 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 518.9331 | 278 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.6667 | 20 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3282.0667 | 14 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 328.6663 | 493 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53093.368 | 897.1 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.6 | 7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 155.1666 | 98 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.8 | 24 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 725 | 60 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 741.2899 | 175.8 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1174.9832 | 493 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1654.5297 | 757.8 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 96.4 | 48.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 0.10667 | 0.64 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 0.23467 | 0.64 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 13320.45 | 429 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 650-Fluidized Bed
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 570 | 30 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 25.2 | 6 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 86.7866 | 28.3 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 337.1665 | 238 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1128.4999 | 111 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 218 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12296.5332 | 352 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 102.3333 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 189.6667 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55350 | 150 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 193.4633 | 45.7 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 210.3333 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5212.4332 | 502 | 1 | 1 | 1476-Induced draft fan speed changer | U1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1188.1 | 109 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1179.7498 | 495 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 162.3333 | 20 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 290.5 | 35 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5755.2083 | 42.5 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 869.75 | 245 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1960.9998 | 318 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15786.3333 | 26 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.7333 | 68 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 10.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.8 | 7.2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 221.3333 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1405.3 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3706 | 102 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 180 | 15 | 1 | 6 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.7013 | 17.63 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.3333 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147.6 | 4.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 395.2 | 5.2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 629.7996 | 564 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2192.7333 | 31 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 1.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 65.7 | 54 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112.2 | 5.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203 | 58 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 265.1639 | 418.68 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2723.3331 | 380 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24975 | 675 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1405.4833 | 49 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7131.25 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 62.7 | 38 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 63.75 | 255 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250 | 25 | 2 | 2 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 900 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31 | 3.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.8 | 3.2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.9 | 2.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 12.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 295 | 25 | 2 | 2 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282.9 | 94.3 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246.9666 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 184.1667 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 260 | 20 | 1 | 2 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 504.9999 | 300 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 514.8 | 28.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.86 | 5.72 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.8666 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 9.8 | 1 | 2 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.8 | 2.9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.4167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.2 | 8.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3650 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4078.6666 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22406.5333 | 56 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4108.0166 | 31 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 99.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 238.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 350 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8404.9998 | 492 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 19 | 38 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 436.8 | 4.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 595 | 60 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52338 | 36 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.6 | 2.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 47.25 | 21 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1718.3833 | 11 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27193.2 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1433.7998 | 321 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 832.9999 | 420 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 297.5 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100 | 4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5017.2 | 111 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.2 | 2.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203.7 | 9.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 294.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2169.0666 | 56 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2989.3331 | 380 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4350 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.5 | 5.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4682.5333 | 232 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.6 | 3.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 6.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65.4167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.5 | 4.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130 | 6.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 330 | 7.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.5833 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15379.3333 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15402.6666 | 76 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20831.5333 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162750 | 310 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 127.5 | 85 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1342.4333 | 34 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 669.1999 | 168 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2592 | 324 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325 | 25 | 2 | 23 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 1 | 2 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.1 | 1.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 125 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3549.9999 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30822.2333 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3039.6666 | 110 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 30569.4 | 108 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 786.9 | 258 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4071.5 | 170 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.5 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 200 | 25 | 1 | 2 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 316.25 | 25 | 2 | 2 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 550 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 30531.303 | 897.1 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1554 | 259 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1717.1166 | 269 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1.1667 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.5 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.3333 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.7 | 8.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 827.9167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1674.85 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7717.8 | 76 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 117.6 | 4.9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2083.3333 | 250 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 855 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3218.9999 | 90 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 102.2666 | 104 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.8333 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 143.75 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.9167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 319.1667 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 323.75 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.9 | 3.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 1 | 2 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.7 | 5.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.9 | 74 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1003.3333 | 56 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1357.2333 | 19 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5523 | 21 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.75 | 45 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.25 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44113.3329 | 650 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23.2 | 17.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6444.6 | 276 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 211900.5833 | 145 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231.2 | 13.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 351.6 | 36 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 834 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3460.5 | 18 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20847.6 | 36 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192.4 | 7.4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 880 | 352 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 175 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56609.9998 | 540 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 551 | 580 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 516.2665 | 256 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 511.3032 | 257.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 87.9167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111.9333 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 264 | 12 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1922.4 | 8.9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25085.5 | 66 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.3333 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1760.9167 | 11 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5783.3332 | 250 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7748.3333 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1387.7499 | 273 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11931.4 | 169 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.5 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 190 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.8 | 6.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 248.4333 | 102.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 282.5 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.1 | 5.7 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.6 | 1.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 75 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.4 | 2.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2508 | 76 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31693.1 | 350.2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55150 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284.5833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 925.4167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500.8166 | 151 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10756.2333 | 151 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5192.5 | 670 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27 | 0.9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 4 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 179.4 | 46 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 255.2 | 11.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 454.3 | 66 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.24999 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.5 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.4167 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.1667 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 182.75 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 195 | 15 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 375 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 791.9996 | 540 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 745.6165 | 539 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 330 | 110 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5674.2 | 36 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 268.6666 | 130 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1002.45 | 9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3815 | 140 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6567.5 | 37 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 347.5832 | 215 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.16666 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 371.1666 | 85 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2.44 | 1.22 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1145.58 | 24.4 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3541.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2713.5 | 90 | 1 | 1 | 1480-Other induced draft fan problems | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 110.4167 | 5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25295.4333 | 34 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 203.5 | 111 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 56.85 | 9 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53647.05 | 417 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3228.6663 | 580 | 1 | 1 | 1487-Air heater (tubular) | U2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 403.35 | 3 | 1 | 1 | 1487-Air heater (tubular) | D3-Forced - Postponed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 874.8331 | 362 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 842.45 | 203 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1396.7 | 3 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 164209.5 | 409.5 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18132.5499 | 417 | 1 | 1 | 1487-Air heater (tubular) | U2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 113.8333 | 10 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 650-Fluidized Bed
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 47.25 | 15 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 650-Fluidized Bed
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1468.1 | 277 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6382.8765 | 467.61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8549.5832 | 355 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.2 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46810.6662 | 655 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8297.91 | 757.8 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 272.3333 | 86 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 21 | 28 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 26 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.7 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 41.65 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 342.2 | 58 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203.94 | 11.33 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.9333 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 25.2 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 32.9333 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 36.85 | 33 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.7 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8.0167 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.4 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 147 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1252.8 | 432 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9689.75 | 245 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4626.4 | 231.32 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5263.2531 | 402.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406 | 58 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 63.5166 | 37 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.1333 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.7 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 341.25 | 455 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 824 | 103 | 2 | 2 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5412 | 328 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.2 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.1333 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3144.528 | 461.3 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1637.9964 | 407.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 9296 | 105 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2023.92 | 112.44 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 15.6 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.8 | 64 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 47.3 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.7667 | 41 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 250.1333 | 28 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1355.1999 | 132 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 773 | 154.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1798.2 | 54 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.8 | 43.2 | 2 | 2 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.9167 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.1333 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 40.7 | 37 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.2 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30.8 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 32.3 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.8 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 10.7667 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 14.9833 | 31 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.3 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17196.3333 | 115 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1103.0832 | 427 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 65418.7496 | 675 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30142.5 | 150 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 981 | 180 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2070 | 230 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6.2 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14.2333 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.4 | 16 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 77 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 975 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10748.9496 | 537 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 17615.1996 | 582 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 35553.4495 | 757.8 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 299.4833 | 151 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1825.7916 | 151.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18699.9 | 249 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 940.13 | 22.93 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5.3167 | 11 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 27.1333 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8.5 | 34 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13.6 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.9 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30315 | 300 | 2 | 2 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176.6666 | 212 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4420.88 | 552.61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10.4833 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.2 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40.2333 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 13.4 | 12 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 37.7667 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1472.4998 | 285 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 664.5833 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 682.5 | 195 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1987.83 | 662.61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19672.4997 | 450 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 632.7 | 281.2 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6.8 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13268.2666 | 112 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102292.1 | 758 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 315.12 | 8.08 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1318.68 | 11.88 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.2 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.5 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 18.6333 | 26 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.5333 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.9 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23 | 23 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 374.5 | 42 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8008 | 77 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8944.8331 | 410 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 826.4665 | 539 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 2588.3999 | 108 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 8622 | 108 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1898.3999 | 252 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12656.25 | 375 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 679.6664 | 407.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1300.0065 | 357.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 134.4 | 112 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1312.3332 | 254 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29.05 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.75 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 177.75 | 79 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 178.2 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4330.5828 | 785 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 29968.9998 | 690 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12791.4332 | 361 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2071 | 103.55 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2215.83 | 738.61 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 911.8665 | 195.4 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 147481.2999 | 282 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.3667 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 18.7 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2614.15 | 539 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10191.0664 | 427 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 864.1666 | 85 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 136164 | 84 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 421.8833 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.3667 | 17 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.5 | 15 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10478.8 | 268 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84988.2 | 652 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 944.0665 | 476 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 12.5 | 150 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 25647.3498 | 237 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 646.8 | 132 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79939.1665 | 650 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 956.1667 | 5 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2138.4 | 528 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 54 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5500 | 20 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 59175.3497 | 507 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U2-Forced - Delayed | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2546.4998 | 330 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 734.4666 | 46 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 441 | 54 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2089.4 | 124 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45668.4497 | 417 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 454.5 | 54 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5344.5665 | 446 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50837.5 | 415 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U3-Forced - Postponed | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 611.6666 | 100 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1330.2 | 54 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6157.8 | 44 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100 | 75 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480.9 | 63 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 450 | 25 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 974.5833 | 25 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 568.75 | 25 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 719.75 | 15 | 1 | 1 | 1492-Air heater fouling (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 3438.125 | 37.5 | 1 | 1 | 1492-Air heater fouling (tubular) | U2-Forced - Delayed | 650-Fluidized Bed
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 23.9833 | 1 | 1 | 2 | 1492-Air heater fouling (tubular) | D2-Forced - Delayed | 650-Fluidized Bed
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 1333.25 | 15 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 233.3333 | 10 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 774.9167 | 5 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 109.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.5 | 9.5 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 973.4 | 15.7 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 979.2 | 10.2 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 218.4 | 18.2 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 224.7 | 10.7 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.8 | 4.3 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 517.7 | 31 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3275.4 | 10.3 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 616.1 | 10.1 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46789.5333 | 113 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1770 | 100 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 447.5 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43 | 4.3 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 149.9 | 6 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 286.9 | 15.1 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 672 | 28 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345.4 | 15.7 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 742.5 | 9.9 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5178.5325 | 28.89 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 210891.3666 | 101 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1975.05 | 81 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5346 | 19.8 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 38447.2 | 102 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 338.3 | 19.9 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1800 | 20 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8382.5 | 47.9 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 101 | 10.1 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1058.2 | 111 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4085.9583 | 17.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1679.2833 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 838.35 | 81 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.8 | 4.1 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1692.6 | 27.3 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9136.8333 | 26 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.2 | 2.7 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 12.8 | 2 | 2 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 784.35 | 83 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 160 | 120 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90552 | 392 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3092.7497 | 417 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | U2-Forced - Delayed | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1909.3831 | 293 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D2-Forced - Delayed | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7575 | 303 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 931.6666 | 65 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 580.4999 | 162 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4277.3498 | 303 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 842.4 | 312 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75274.3831 | 401 | 1 | 1 | 1500-Air heater soot blowers | U1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 561.6666 | 100 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 170.6667 | 32 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1641.6666 | 50 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1031.0666 | 296 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | WECC | Off-Peak | 1516.775 | 25.35 | 1 | 1 | 1500-Air heater soot blowers | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2278360 | 824 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 956.75 | 15 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9848.3333 | 190 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 311.7833 | 13 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 124.6665 | 220 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 106.1667 | 13 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 123.9333 | 13 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3259.4499 | 219 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 581.25 | 125 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.6667 | 8 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122640 | 14 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 131.1999 | 123 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 261.9 | 81 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 641.4333 | 14 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5175.9167 | 19 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5481.9165 | 419 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6205.3166 | 67 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1890 | 420 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3462.9835 | 32.43 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10845.9997 | 510 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1893.7093 | 100.64 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 650-Fluidized Bed
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4837.5 | 258 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5868.3 | 31 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17813.0666 | 67 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.1665 | 250 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 214.0666 | 76 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1109.7333 | 56 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 14244.9998 | 330 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2374.2833 | 47 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4090.9047 | 510.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3923.2466 | 44.65 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5742.9333 | 16 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24357 | 46 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 164.8 | 4 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 612.8999 | 81 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 8211.4999 | 330 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 103747.6 | 68 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.4916 | 50.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 638.73 | 45.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.42 | 0.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2228.59 | 40.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5582.9167 | 25 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 62449.65 | 81 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 115.1867 | 5.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 274.365 | 60.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 608.85 | 297 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1203.415 | 30.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 799.5 | 205 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3171.9999 | 183 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4082.4 | 510.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 53670 | 30 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 880.4783 | 10.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1273.9998 | 273 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3977.0533 | 50.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1317.5 | 25 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 77315 | 35 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4927.3333 | 20 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.3417 | 35.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1380.05 | 21 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 12050.0333 | 2 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4833.45 | 27 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1897.44 | 566.4 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.69 | 0.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.0267 | 6.08 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.54 | 5.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.99 | 0.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72 | 4 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.405 | 0.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 174809.0666 | 83 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2776.05 | 199 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6186.6666 | 80 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 384.9999 | 165 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15566.4 | 552 | 1 | 1 | 1535-Flue gas recirculating fan | U1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2235.6 | 552 | 1 | 1 | 1535-Flue gas recirculating fan | SF-Startup Failure | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2270.3333 | 69.5 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1536 | Flue gas recirculating fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2297.75 | 455 | 1 | 1 | 1536-Flue gas recirculating fan dampers | SF-Startup Failure | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 237504 | 96 | 1 | 1 | 1550-Flue gas recirculation fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9760.1 | 21 | 1 | 1 | 1550-Flue gas recirculation fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1560 | Other flue gas recirculation fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1954.6495 | 747 | 1 | 1 | 1560-Other flue gas recirculation fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 13543.44 | 178.87 | 1 | 1 | 1570-Flue gas recirculation ducts | SF-Startup Failure | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 965.0332 | 262 | 1 | 1 | 1570-Flue gas recirculation ducts | D1-Forced - Immediate | 100-Fossil-Steam
1572 | Flue gas recirculation duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 492.821 | 214.27 | 1 | 1 | 1572-Flue gas recirculation duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 195.25 | 71 | 1 | 1 | 1580-Flue gas recirculation dampers | D2-Forced - Delayed | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 358.8 | 46 | 1 | 1 | 1580-Flue gas recirculation dampers | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 341.28 | 4.74 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D2-Forced - Delayed | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 93.6472 | 165.26 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | U1-Forced - Immediate | 851-CC GT units
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 85.3842 | 165.26 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | U1-Forced - Immediate | 851-CC GT units
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 57.841 | 165.26 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | U1-Forced - Immediate | 851-CC GT units
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 66.1332 | 128 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 852-CC steam units
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 72.5332 | 128 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 852-CC steam units
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 44.8 | 128 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3428.6664 | 370 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 100-Fossil-Steam
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4642.5666 | 158 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 264.9165 | 187 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 241.9999 | 165 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 1203.755 | 147.7 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 183.0966 | 37.24 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 729.56 | 146.4 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 679.1666 | 163 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 2324.3666 | 206 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 186.2916 | 131.5 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 153.9999 | 105 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 487.4999 | 117 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 852-CC steam units
1591 | Stack damper and linkage | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | SERC | Winter | 51.6666 | 100 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 861-CoG GT units
1592 | Stack damper linkage motors | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 72.5333 | 32 | 1 | 1 | 1592-Stack damper linkage motors | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2394 | 76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1038.8333 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4996 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 517.4333 | 19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 116 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.96 | 6.72 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.05 | 4.55 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.96 | 5.58 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.05 | 3.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.9 | 4.45 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 12.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.96 | 4.48 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 418.2 | 6.97 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.84 | 8.13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 744.04 | 8.36 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 776.82 | 11.77 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2616.24 | 29.73 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 184.45 | 5.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 273.06 | 6.66 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23238.9 | 342 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1033.9999 | 330 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.08 | 4.96 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.96 | 5.82 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60 | 3.75 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.05 | 4.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.02 | 11.06 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 303.03 | 8.19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 74.69 | 6.79 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.02 | 5.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123 | 8.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 407 | 7.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.1661 | 160.81 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1026.8665 | 422 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.2666 | 116 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 476.9333 | 196 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 294 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.08 | 2.08 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.09 | 7.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 173.91 | 5.27 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.98 | 11.94 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 250.88 | 5.12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 335.16 | 5.32 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 735.84 | 15.33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1207.14 | 20.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 93.92 | 5.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103.32 | 4.92 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140.04 | 7.78 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 183.2 | 4.58 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 392.88 | 16.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1922.6662 | 721 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 649.65 | 183 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 128.05 | 39 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12604 | 46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4053.5999 | 216 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3238 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114.96 | 14.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.9 | 4.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 249.76 | 4.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 278.08 | 12.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 441 | 12.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138 | 6.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232 | 11.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 572.85 | 8.55 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1098.24 | 16.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80.04 | 3.48 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 168.96 | 7.04 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285.39 | 4.53 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1671.2 | 20.89 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.3333 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1445.55 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 772.85 | 87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.96 | 5.08 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.98 | 8.07 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 196.08 | 32.68 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 519.8333 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 879.2 | 12.56 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 324 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 519.84 | 6.84 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 973.08 | 14.31 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1898.16 | 28.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.88 | 8.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 347.2 | 217 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3604 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 366 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 117329.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 32 | 8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6291.9 | 54 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 188.02 | 5.53 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.04 | 4.69 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 3.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 407.16 | 7.83 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.98 | 83.33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 727.76 | 8.27 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 778.65 | 8.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1626.88 | 39.68 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.05 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56 | 5.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 195.84 | 5.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 326.3 | 5.02 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 502.09 | 13.57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.8 | 48 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108 | 120 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 182.75 | 73.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 923.7997 | 447 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.1 | 86 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1974.55 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 231.55 | 33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 46.4 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.07 | 8.13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 416.84 | 6.13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.31 | 11.93 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 983.88 | 9.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 986.85 | 11.61 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1804.31 | 26.93 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50.96 | 6.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.08 | 2.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63 | 4.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 86.8 | 2.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 26 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8073.6 | 232 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.0666 | 28 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84.3733 | 6.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304.8 | 48 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2645.4999 | 222 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 148.2 | 156 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4770.5 | 30 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 294.6666 | 104 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 470.1667 | 14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55.98 | 3.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108.12 | 3.18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164 | 20.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 753.74 | 4.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306.96 | 12.79 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 545 | 27.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 552.96 | 11.52 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 793.32 | 12.02 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1974.72 | 22.44 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3418.25 | 30.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62 | 3.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.62 | 5.59 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.9 | 6.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 475.3332 | 248 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3234 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 2.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.97 | 5.41 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 272.88 | 11.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3211.12 | 36.49 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 68 | 6.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75.01 | 5.77 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.07 | 5.71 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 101.15 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 112.8 | 18.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | RFC | Off-Peak | 203.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2017.3333 | 17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 488.75 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 63 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 157.92 | 3.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.96 | 4.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108.92 | 3.89 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 472.96 | 7.39 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 546.72 | 8.04 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1734 | 25.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.92 | 3.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.04 | 10.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.86 | 14.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 477.0999 | 78 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 209.3 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1034.6167 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1391.5 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1788.6333 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4866.8 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1032 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.03 | 3.37 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64.98 | 3.42 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.05 | 3.03 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 31.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 93.96 | 3.24 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106.04 | 9.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118 | 23.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 556.8 | 6.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1008 | 14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1840.76 | 27.07 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 73.98 | 4.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 78.98 | 7.18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 452.4 | 6.96 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.7333 | 23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 4358.9333 | 16 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 354.2 | 3.22 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 625.24 | 4.06 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1091.88 | 20.22 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 2.75 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.04 | 3.69 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.04 | 6.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.9 | 3.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 483.84 | 15.12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 744.8 | 15.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1104.4 | 12.55 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1890.24 | 21.48 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56.95 | 3.35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63 | 6.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76.96 | 4.81 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140.01 | 3.59 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 560 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3943 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.01 | 7.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.04 | 5.86 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 209.92 | 6.56 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 219 | 10.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51.03 | 5.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.16 | 4.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 170.89 | 7.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 328.08 | 13.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 555.06 | 6.38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148.59 | 3.81 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 149.96 | 6.52 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 947.85 | 10.65 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1731.125 | 629.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 231.8 | 61 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 428.76 | 7.94 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55.93 | 3.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61 | 6.1 | 2 | 2 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 420.81 | 10.79 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 522.74 | 8.86 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 665.26 | 8.99 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 103 | 5.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 443.3 | 78 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 673.2 | 132 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 704.04 | 58.67 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10723.6665 | 265 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 125 | 12.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.89 | 4.41 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 213.92 | 7.64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75.06 | 4.17 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.89 | 5.43 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 285 | 9.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 57.92 | 3.62 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 139.1 | 5.35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 954.8 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 140.4 | 156 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 126.5833 | 217 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 155.5165 | 217 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2199.3 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 805.3333 | 160 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 35.75 | 33 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 53.0833 | 49 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 261.7998 | 285.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 168.7 | 241 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 116.2666 | 109 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 11586.24 | 28.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 263.04 | 123.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 207 | 69 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 560.9816 | 82.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 4304.61 | 10.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 198.7666 | 26.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 862-CoG steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16090.6665 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87600 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 12.5 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 877.92 | 566.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 351.4999 | 285 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1258.1332 | 337 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 13.25 | 265 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 1097.1 | 23 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 805.7999 | 153 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 161.4 | 18 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 418.1999 | 153 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 144300 | 1110 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 859.8332 | 385 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.2499 | 135 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1987.5831 | 305 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1017.9 | 351 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1058.9162 | 655 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 705.6663 | 580 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 311.1 | 10.2 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1006.6666 | 302 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 3.8332 | 230 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 72.2499 | 255 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.12 | 5.16 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1360.6664 | 785 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1053.6663 | 580 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1914.3832 | 427 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3209.3332 | 415 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 46873.2 | 536 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 25.3333 | 16 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 39.6666 | 28 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8854.6663 | 580 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9379.9998 | 600 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 9744 | 448 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 101.7666 | 142 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 35.5831 | 305 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 27.5 | 275 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2937.1879 | 650.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 485.1665 | 410 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 1608.8332 | 245 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1755.2499 | 255 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1246.08 | 566.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 134.42 | 42.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1066.4166 | 335 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5310 | 900 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14952 | 7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 27164.25 | 9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 32.9165 | 395 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 378.5666 | 82 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6480.8328 | 770 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1601.8833 | 223 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1947.5 | 410 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 116.3332 | 349 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87.4 | 46 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.1665 | 178 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 34.5 | 230 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 4.6666 | 28 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 852.5333 | 184 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 861.8 | 124 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27462.5 | 650 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 977.1665 | 410 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 766.6664 | 400 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 608 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 6.4166 | 55 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 7.8 | 36 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 119.5833 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2755 | 580 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3408.1005 | 159.63 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3856.2333 | 26 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14226.25 | 599 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35816.6665 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1236.4166 | 185 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 111.1666 | 115 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 127.0833 | 125 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 45.75 | 305 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 527.6329 | 347.89 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5406.3329 | 662 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1146.6664 | 400 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1624 | 560 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29302 | 245 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1642.1665 | 590 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90 | 360 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 32 | 320 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 607.9996 | 570 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1857.333 | 560 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4671.3215 | 650.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 433.0666 | 203 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 238.81 | 42.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 37.5 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 175.5 | 175.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1848.7695 | 720.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 367.0332 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1440 | 600 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4601.2496 | 675 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 142 | 12 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 255.6665 | 590 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 739.9998 | 600 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3528.6166 | 104.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 856.8 | 504 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 122.0833 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 191.8333 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 696.75 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 904.9167 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 932.1666 | 85 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 180.3333 | 20 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 7831.4999 | 90 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 864 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 35.8333 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 184.3333 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2457.0833 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1093.3333 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 3911.0497 | 429 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 938.1667 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1330 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 313.75 | 5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 425 | 50 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 940 | 20 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 15.24 | 3.81 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 2252.4366 | 25.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 800 | Miscellaneous | TRE | Off-Peak | 1179.75 | 121 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2425.535 | 25.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | TRE | Off-Peak | 1452 | 220 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15.5466 | 42.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 833.0382 | 125.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 82.7999 | 216 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 1981.4666 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 279.3 | 294 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1601.7 | 562 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 120.1933 | 59.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 958.2999 | 222 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 6868.4663 | 538 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 809.8333 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 8.36 | 22.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 67.1775 | 103.35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 73.396 | 74.64 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1578.1 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1341.8666 | 272 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 980.5582 | 281.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2855.0012 | 274.96 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 3306.3499 | 267 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 300.3332 | 265 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 6082.1832 | 259 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 772.2548 | 487.74 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2385.1332 | 538 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 197.9999 | 216 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 402.7666 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 580.8 | 363 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 401.0333 | 53 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 924.6665 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2831.895 | 190.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 38.1333 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 6352.3333 | 190 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 14032.2057 | 221.27 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 203.9999 | 180 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 402.9666 | 157 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1200.4166 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 11920.8 | 144 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 387 | 258 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 770.4666 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 62.1 | 138 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 1843.7 | 358 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 141.2666 | 163 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 204.75 | 195 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 343.6533 | 210.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 458.6666 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 31.911 | 106.37 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 152 | 190 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 744.1665 | 190 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 943.6665 | 190 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 9029.9999 | 126 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 2973.95 | 203 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 119 | 30 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 4132.2665 | 208 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 943.3666 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 324.9999 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 7586.4 | 58 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 41933.1 | 194 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 685.2 | 72 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 72.4999 | 75 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 157.7333 | 169 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 1316.7 | 77 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 1092.1999 | 258 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 783.8499 | 183 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1446.2499 | 195 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 37.3333 | 35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 81.25 | 75 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 815.7499 | 195 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 10767 | 194 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1058.3499 | 183 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 1387.4759 | 187.92 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 97.2885 | 73.89 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 161.1999 | 186 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 421.5732 | 158.09 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 1007.0666 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 3175.9 | 182 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 29174.3666 | 194 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 38573.6 | 208 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 24.1667 | 50 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 576.7999 | 168 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 59.8 | 138 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 625.2166 | 161 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 24.99 | 23.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 7 | 12 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 28.5166 | 59 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 596 | 12 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 752.5333 | 136 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 81.6666 | 70 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 244.5 | 163 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 375 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 879.3749 | 157.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1237.4166 | 155 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1251.8332 | 259 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 4023.7833 | 127 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2334.6666 | 136 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 172.6666 | 148 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1246.6666 | 200 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 690.0333 | 163 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | TRE | Winter | 221.1132 | 156.08 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 555.3333 | 136 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 91.35 | 261 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 37944.45 | 243 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 70.85 | 109 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 263.9999 | 99 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 888.1458 | 119.75 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 117 | 260 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 80.64 | 76.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 13317.4999 | 210 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 208.8 | 261 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 106.5999 | 123 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 335.9999 | 157.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1168.4 | 254 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 402.0666 | 148 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 129.1649 | 98.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 120.8998 | 234 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 88.6666 | 95 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 444.5 | 254 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 167.6998 | 234 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 619.2333 | 26 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 680 | 136 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 7381.5 | 133 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 4.6666 | 140 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 9560.05 | 263 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 70.2 | 234 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1821.05 | 301 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 63.2666 | 73 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 231.28 | 141.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 4335.8333 | 60.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 66.6499 | 129 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 60.8999 | 261 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 9.9333 | 74.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 1201.6999 | 183 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 860-Co-generator Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | WECC | Summer | 182.525 | 74.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 860-Co-generator Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7675.5 | 35 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1713.8998 | 522 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26627.6664 | 370 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9.6 | 32 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 261.0665 | 178 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1170.7666 | 341 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 0.62333 | 1.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 122.9166 | 125 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29 | 29 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3918.8605 | 174.43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11769.6665 | 620 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 27298.3747 | 417.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 57557.9732 | 442.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 9.5667 | 41 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | RFC | Winter | 1045.4167 | 13 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 598.9498 | 297 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1148.45 | 223 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 376.6666 | 200 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 132.7717 | 19.43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 25.3 | 66 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18812.5 | 625 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7922.9994 | 855 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 248.2666 | 56 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 239.1666 | 82 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1035 | 92 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5482.0833 | 223 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2728.4995 | 765 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.7166 | 73 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3205.7451 | 815.02 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1984.9662 | 658 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3624.5999 | 126 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 43809.3333 | 40 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6960.7332 | 263 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5414.9997 | 855 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 183960 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 184 | 115 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 72.631 | 14.43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 921.4996 | 570 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1297.4998 | 450 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 11.1 | 37 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 158.922 | 29.43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 45.8999 | 81 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 308 | 11 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90894.7495 | 765 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.6 | 3.6 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4.2 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 5.2 | 5.2 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16.4 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 29.7 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 872.2 | 124.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.6 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 30.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.2 | 3.1 | 2 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.4 | 3.2 | 2 | 4 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 20.4 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.2 | 3.2 | 2 | 7 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.6 | 3.6 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.2 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.2 | 6.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 56 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 4 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 29670 | 92 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.4 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.6 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14.8 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.8 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 22.2 | 3.7 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.8 | 4.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16.5 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 18 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 129.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4.1 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18 | 4.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 42.9 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4.3 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.2 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.5 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 12.6 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 8.2 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 48.1 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.1 | 3.1 | 2 | 4 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.2 | 3.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.6 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 9.9 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 16.4 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 17.5 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 22.8 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.5 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.7 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4.8 | 4.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 5.1 | 5.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.7 | 6.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.8 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.4 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 16 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 7.8 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14.4 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28.8 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 35.2 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 44.4 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 64.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.4 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 11.7 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 15.6 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 5.1667 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.2 | 6.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.8 | 3.4 | 2 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 23.4 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3 | 3 | 2 | 5 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.1 | 3.1 | 2 | 6 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.4 | 3.4 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 12.4 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 7 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 11.4 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3 | 3 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.1 | 3.1 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 12.8 | 6.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14.4 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3 | 3 | 2 | 5 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 19.8 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 18.5 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 72.5333 | 64 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U2-Forced - Delayed | 800-Miscellaneous
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 554.6666 | 64 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U2-Forced - Delayed | 800-Miscellaneous
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9.7643 | 53.26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 17.499 | 55.26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 3207.3799 | 286.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10.8896 | 50.26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 58.1566 | 47.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 225.54 | 37.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 69.1727 | 48.26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1019.1 | 258 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1514.7999 | 168 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 2242.0666 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1517.5999 | 168 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 144.0333 | 29 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 422.1 | 67 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 3609.1 | 193 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 144 | 27 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 7.7 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 138.6667 | 26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 146 | 73 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 643.85 | 163 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 66 | 22 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 167.5 | 75 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 83.3 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 19.4666 | 73 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Winter | 367.4866 | 79.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 861-CoG GT units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1827.3498 | 483 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 84 | 3 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 241.3333 | 181 | 1 | 1 | 1720-Desuperheater/attemperator controls | D2-Forced - Delayed | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2375 | 95 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.8 | 56 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 104.1667 | 50 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30 | 20 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 77.4 | 27 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77801.7499 | 195 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 311.6666 | 275 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 586.5 | 170 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1672.9166 | 275 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30362 | 235 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17683.2499 | 195 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5716.9666 | 79 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 458.25 | 65 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1158.6666 | 40 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 119.9 | 66 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 297.9166 | 275 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 347.2831 | 311 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 632.8 | 56 | 1 | 1 | 1720-Desuperheater/attemperator controls | U2-Forced - Delayed | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5800 | 120 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1690 | 50 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1662 | 120 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7804.4166 | 85 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6984 | 240 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 101.2833 | 59 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 385 | 275 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3778.3333 | 100 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23389.1665 | 650 | 1 | 1 | 1720-Desuperheater/attemperator controls | U3-Forced - Postponed | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13142.9999 | 180 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31080 | 120 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 279.9333 | 247 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D3 | Forced - Postponed | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 328.4 | 12 | 1 | 1 | 1720-Desuperheater/attemperator controls | D3-Forced - Postponed | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2310 | 600 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 40.64 | 38.1 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 124.695 | 146.7 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 154.9333 | 166 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 121.68 | 152.1 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 8598.6 | 153 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 415.2499 | 165 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 476.775 | 146.7 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 2787.8666 | 203 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 9 | 180 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 729.75 | 45 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 5268.8 | 148 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 477.05 | 203 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 114.915 | 146.7 | 1 | 2 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1891.5 | 242.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 920.3832 | 171.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 887.05 | 157 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 1008.2666 | 152 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 348 | 240 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 43.815 | 38.1 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 610 | 200 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 841.7499 | 195 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2351.0999 | 153 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 3773.6 | 106 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 67.3666 | 86 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 264.2499 | 105 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 808.75 | 75 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 87.4333 | 86 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 219.6 | 72 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 8317.75 | 147 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 5.204 | 104.08 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 347.0833 | 87.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 522.3166 | 121 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1959.7665 | 259 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 1950 | 250 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 706.25 | 75 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2342.2 | 147 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 341.25 | 175 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | TRE | Off-Peak | 3988.5333 | 8 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 860-Co-generator Block
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 853.4164 | 385 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1396.95 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 988.6333 | 223 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 795.2666 | 158 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 855 | 285 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 892.5 | 85 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 387.9167 | 9.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1151.933 | 467 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 196 | 112 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 84 | 280 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4018 | 410 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 465.4996 | 570 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1444.6665 | 440 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10847.833 | 485 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 92.5331 | 347 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 245.3 | 66 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3129.4165 | 235 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1418.083 | 455 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 186.6666 | 112 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2761.0666 | 248 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 930 | 310 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330.7497 | 405 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 519.7499 | 405 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 590.9966 | 331.4 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 644.25 | 859 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1542.9 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1848 | 336 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 479.2499 | 405 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 12.8067 | 11.3 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1410.8499 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 138.0166 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 627 | 380 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1224.1664 | 325 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 61.7498 | 285 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 739.4165 | 467 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 541.6665 | 325 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1237.0997 | 417 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.8331 | 350 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 89.9999 | 270 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 97.3332 | 292 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 303.75 | 405 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 594.3166 | 169 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2012.5 | 575 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 154.77 | 9.9 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 49.9333 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 446.5532 | 273.4 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 121.6333 | 178 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 156 | 26 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 40928 | 64 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U2-Forced - Delayed | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 926.55 | 213 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 295.4666 | 64 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 3107.4999 | 150 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1794.4981 | 388.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 39.37 | 393.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 729.625 | 583.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 429.1666 | 206 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 3593.9333 | 148 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 87.4299 | 374.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 46 | 46 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 70 | 70 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 440.5831 | 311 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 227.9333 | 210.4 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 366.1832 | 173 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 149.625 | 157.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 4385.7664 | 349 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 405.1332 | 206 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 870.1666 | 115 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Summer | 18.6333 | 86 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 237.15 | 93 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 84.9333 | 26 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 157.9332 | 206 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 213.6 | 267 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 154.6381 | 299.3 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 153.4 | 141.6 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 12.1333 | 91 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 86.45 | 91 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | TRE | Winter | 3311.7 | 166 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 781.9166 | 55 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 237.1833 | 66.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 11861.2333 | 47 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 661.4999 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 92.7333 | 107 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5.7333 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 66.6666 | 80 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 361.0013 | 208.27 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 126.9427 | 19.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 70 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 200.9 | 82 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 116.1333 | 67 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2164 | 80 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20135.7998 | 498 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 44.4333 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 806.8666 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 9261.2665 | 292 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 357.6883 | 133.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 288.86 | 55.55 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 87.5 | 175 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88.9 | 127 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 64.5 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 182.9333 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 285.0166 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 653.5846 | 585.3 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 134.9 | 71 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 883.93 | 23.89 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 53.3333 | 80 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 95.55 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57.1666 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 6127.383 | 431 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15048 | 627 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 102.6666 | 80 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 553.4997 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 154.8 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 298.6999 | 174 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 57.475 | 104.5 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1695.2666 | 236 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 315.3331 | 344 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3374.4666 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 47.886 | 239.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2026.6666 | 80 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 274.7333 | 52 | 1 | 1 | 1750-Burner management system | D2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236.2499 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 167.25 | 223 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 665.0199 | 243.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 635.8666 | 152 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1161 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 400.8326 | 304.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29178.9332 | 354.4 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3504.2497 | 393 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 235.125 | 104.5 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1001.3 | 57 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 265.2822 | 274.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 836.9997 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 980 | 150 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 480.2269 | 96.69 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 125.1726 | 144.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3799.9999 | 150 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 320 | 80 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4224.9656 | 334.43 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2188.75 | 515 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 56 | 105 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10.2 | 76.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 40.85 | 57 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 174.5833 | 25 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 246.8012 | 264.43 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4851.63 | 770.1 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 398.2499 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1880.5331 | 344 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 49.8166 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 249.3333 | 80 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 202.2064 | 433.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 15892.8633 | 95.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 164.9 | 194 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 24.15 | 69 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 746.1999 | 78 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 5256 | 292 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 303.8666 | 344 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 27.3 | 26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3361.5 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1270.6666 | 80 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5308.4831 | 739 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 733.333 | 500 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 150.2833 | 71 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 473.2 | 24 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 4733.7 | 62 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2131.6 | 292 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 6766.6336 | 334.43 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 232.3331 | 410 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 44.25 | 177 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 969.3333 | 80 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 180.0665 | 292 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 1516.5332 | 376 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2664.55 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 330.7497 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31785.7499 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 42754.4997 | 405 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 56.35 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1.225 | 10.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 14963.6666 | 308 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 64.3333 | 10 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 21.63 | 43.26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 27.6 | 184 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1.925 | 10.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 292 | 146 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 5.25 | 10.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 534.5331 | 422 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 8.3333 | 12.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 240.8832 | 149 | 1 | 1 | 1750-Burner management system | U2-Forced - Delayed | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 16.6667 | 20 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 240 | 100 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 5.0667 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 353.0666 | 64 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 103.85 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 413.8666 | 64 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 4.6667 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 7.1333 | 1 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 79.3333 | 35 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 191.8833 | 29 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 818.1333 | 52 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1207.45 | 57 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 68.5833 | 5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 75.9333 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 102.4 | 64 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 7.75 | 15 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 222.3667 | 14 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 357.1167 | 7 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 253.0666 | 146 | 1 | 1 | 1750-Burner management system | U2-Forced - Delayed | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 123.05 | 23 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1804.1666 | 25 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 120.8333 | 145 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3815.9996 | 540 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 887.7499 | 201 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2987.1329 | 692 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1648.2332 | 502 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 40.25 | 21 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 275.3333 | 118 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1718.1666 | 169 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44.4 | 444 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1292.375 | 738.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | SF-Startup Failure | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2084.0829 | 702.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5362.4164 | 702.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 777.8499 | 141 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18424.875 | 701.9 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3407.5666 | 151 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 30.9333 | 64 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 698.7165 | 371 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 899.8666 | 136 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 11154 | 429 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 650-Fluidized Bed
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 3560.7 | 429 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 650-Fluidized Bed
1760 | Feedwater instrumentation (not local controls) | NULL | NULL | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 512 | 32 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 800-Miscellaneous
1760 | Feedwater instrumentation (not local controls) | NULL | NULL | U1 | Forced - Immediate | 2022 | Other | BM | 800 | Miscellaneous | SERC | Winter | 174.85 | 19.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 800-Miscellaneous
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 16830.05 | 463 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1559.985 | 24.9 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D2-Forced - Delayed | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2587.5933 | 194.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 694.1332 | 274 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 147.5616 | 62.35 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 103.84 | 70.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 555.3332 | 170 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 1081.9 | 349 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 632.925 | 145.5 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 12.1333 | 104 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 110.4546 | 75.31 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 779.7833 | 59 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 604.9332 | 349 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 654.48 | 161.6 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 383.5892 | 162.08 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 291.3333 | 184 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 435 | 100 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 405.0666 | 124 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 6.5333 | 56 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1920.8332 | 250 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1123.3332 | 200 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 744.5 | 6 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1277.9499 | 183 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2828 | 30 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 496.8 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1747.9996 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1030.3996 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | SF-Startup Failure | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 959 | 274 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D2-Forced - Delayed | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 386.4 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 837.25 | 51 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 859 | 859 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 643.9996 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4367.45 | 773 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 496.8 | 552 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | NULL | NULL | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 463.05 | 21 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 800-Miscellaneous
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 148.8667 | 7 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 39.9 | 6 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60.4 | 8 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4065 | 12 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4311.7333 | 19 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7945.9999 | 120 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 2296.6311 | 649.99 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 1086.55 | 93 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 160.55 | 169 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7773.4666 | 173 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 511.4164 | 361 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 205.6166 | 169 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 115.5833 | 95 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4108.8333 | 89 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 288.3499 | 219 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 256.4999 | 405 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Summer | 141.75 | 405 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 302.4 | 126 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.68 | 49.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 74.8 | 24 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.7166 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123938.2824 | 1331 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2342.3 | 397 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.6633 | 21.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.5533 | 14.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 206.6666 | 248 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 401.6667 | 10 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35.6666 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1373.75 | 785 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2713.1999 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10715.6665 | 620 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 177.3333 | 95 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 2654.6291 | 28.57 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 91.2 | 114 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 0 | 0 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1591.3328 | 770 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 373.7045 | 723.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3351.5764 | 841.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.3333 | 130 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3960 | 900 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 564.3 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2267.3663 | 502 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5015.9998 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26732.4996 | 1110 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 732.3333 | 169 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | OG | 100 | Fossil-Steam | RFC | Summer | 701.6667 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85.0667 | 16 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 712.13 | 241.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1556.3 | 197 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.72 | 79.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 454.75 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 84.8 | 16 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 108.7833 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 123.05 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5495.45 | 839 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1538.8733 | 333.33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 485.9433 | 91.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 283.6664 | 370 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12162.6666 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137 | 34.25 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7378.4662 | 652 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9831.6661 | 850 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29.48 | 26.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.2 | 22 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3663.9998 | 480 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 559.9666 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1936.3328 | 785 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 445.0333 | 169 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 650 | 325 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 392.89 | 77.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2821.3333 | 115 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.99 | 24.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13.1667 | 2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.7666 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 130.1833 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 940.7 | 818 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2850.1329 | 668 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 662.4 | 552 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 832.5 | 90 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2608.5332 | 292 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2434.1332 | 448 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2193 | 51 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.69 | 67.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4167.9998 | 480 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 86.1666 | 110 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 282.3333 | 110 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1543.5 | 49 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 336.05 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6666 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 295.5 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1170 | 72 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 441982.5 | 465 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 106.1667 | 26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 135.45 | 27 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 98.7 | 14 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 4184.5833 | 25 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 74586.6667 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 249.7497 | 405 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 734.7333 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9267.0332 | 346 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 164.45 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 927.5 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.6 | 12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.6 | 12 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 586.15 | 19 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 34.2 | 76 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7954 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 15306.5 | 23 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 217.5666 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5781.8663 | 586 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 52.7066 | 53.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 325.3333 | 80 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4471.2 | 552 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 448.9333 | 104 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2938.6665 | 380 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 9.5475 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.2 | 16.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 903.6 | 72 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 771.7499 | 189 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4561.6661 | 850 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2292.1496 | 531 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 269060.85 | 1257 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4846.0999 | 258 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 127.4999 | 90 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 14 | 4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 471.3333 | 70 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 94.75 | 379 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 170.3332 | 292 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.28 | 7.29 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 73.1166 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3846.15 | 297 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.9333 | 17 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 87.954 | 293.18 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 309 | 51.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15363.95 | 627.1 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 141.1332 | 292 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 762 | 508 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2362.5 | 90 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 153.3333 | 92 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2870.9165 | 235 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 805.3333 | 160 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.7 | 16.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.18 | 64.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2517 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 294 | 280 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.48 | 4.66 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 410.0499 | 417 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 369.15 | 107 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 928.9164 | 785 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3838.3 | 586 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3442.7998 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 268285.4162 | 1265 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1222.8832 | 239 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Summer | 725.085 | 161.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 254.6 | 13.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 5037.5535 | 420.38 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 76.6667 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 800-Miscellaneous
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 57822 | 419 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 7.2 | 4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 38.3833 | 49 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 88.4145 | 378.92 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 182.2333 | 14 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 429.3434 | 172.89 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1029 | 367.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Winter | 71.2833 | 91 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 950.2998 | 663 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 654.1732 | 130.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 230 | 230 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 2074.4966 | 127.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1482.8 | 674 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 2496.9 | 246 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1273.7082 | 192.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1169.35 | 257 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 489.9149 | 153.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 290.005 | 112.26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 201.6 | 192 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 4859 | 215 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 1560 | 160 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 203.3865 | 210.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 409.9333 | 172 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 1475.8 | 157 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 1508.5832 | 215 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 116.002 | 112.26 | 3 | 3 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 8321 | 157 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 808.52 | 278.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Summer | 890.3 | 122.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 1411.2 | 196 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 462.9333 | 124 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 117 | 195 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 663.75 | 177 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 873.824 | 273.07 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 2035.4666 | 272 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 142.9999 | 195 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 178.2666 | 152.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Winter | 187.8332 | 161 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 266.875 | 152.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 2269.1666 | 272.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 84.3332 | 230 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 804.4166 | 197 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 360.536 | 212.08 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 29.4666 | 110.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 201.1664 | 355 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1286.1333 | 52 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 752.9166 | 173.75 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Winter | 587.7166 | 197 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 50.5666 | 37 | 2 | 2 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 1316.4666 | 52 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 209.5519 | 112.26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 155.7333 | 64 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | SERC | Summer | 206.25 | 275 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 3017.3333 | 124 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 203.9389 | 112.26 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Summer | 112.4164 | 355 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 354.9332 | 484 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1776.3333 | 73 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 842.248 | 191.42 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 816.2 | 33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 7950 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Winter | 1712.0665 | 244 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1289.2832 | 301 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 57.06 | 285.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 171.6676 | 166.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 45118.3333 | 115 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 813.6 | 113 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Summer | 122.25 | 163 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 519.35 | 119.85 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 123.9 | 118 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 264.9999 | 150 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 11263.9999 | 330 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 337.1166 | 113 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 50.1667 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 108.5599 | 141.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 14.2666 | 53.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 8046.5 | 133 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 7108.2965 | 321.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 49.5 | 90 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 66.3 | 110.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 18.0433 | 54.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 272.5333 | 73 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 770.1 | 102 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 4995.0916 | 160.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 387.375 | 103.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 11153.3333 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 376.5612 | 166.13 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 461.4166 | 113 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 411.3665 | 301 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 43.2666 | 118 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Winter | 48.7166 | 37 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 99.7667 | 41 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 835.45 | 33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 354.144 | 208.32 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 1255.3332 | 140 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 3.4165 | 205 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 350.8166 | 135.8 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 420.75 | 165 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2022 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 681.9999 | 165 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | SERC | Winter | 1883.8666 | 142 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2022 | Gas | GG | 861 | CoG GT units | SERC | Winter | 1178.6 | 142 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 162426.3662 | 1331 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38554.5 | 30 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 28244.6667 | 20 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 7124 | 26 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 552 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47211.475 | 84.9 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 2475 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U3 | Forced - Postponed | 2022 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 12478.6666 | 40 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U3-Forced - Postponed | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1347 | 18 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4760.1 | 86 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6942.6833 | 47 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 274.048 | 0.64 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 650-Fluidized Bed
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1064 | 56 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1107 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 616 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 459.6167 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 768 | 32 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 30.8 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 4021.745 | 27.3 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 6015.1 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 3102.4 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 3281.6667 | 20 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 985.6 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1060.4166 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2707.25 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 114 | 57 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 6490 | 55 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1290 | 30 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1525 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1740 | 29 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 644 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 560.35 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1595.65 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 917.15 | 51 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 580 | 29 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 256.9 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 924 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 702 | 26 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1721.55 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 650 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1786 | 38 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 650 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3434.8662 | 769 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 744.9999 | 300 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1175 | 47 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.6665 | 190 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 810.1333 | 217 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Winter | 2570 | 200 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 851-CC GT units
1811 | Boiler Inspections - problem identification/investigative | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 925.2 | 72 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 852-CC steam units
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 37879.9999 | 240 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 5148.3646 | 63.77 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1043.1 | 18 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 650-Fluidized Bed
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 34933.5833 | 85 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 650-Fluidized Bed
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 157.2 | 18 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 650-Fluidized Bed
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 22692.8333 | 106 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 850-Combined Cycle Block
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Winter | 4132.5916 | 240.5 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1627.6333 | 193 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2247 | 214 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10160 | 254 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 644.8667 | 17 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5042.9166 | 245 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2023.5 | 213 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8614.2165 | 229 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 177.3 | 197 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 692 | 692 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 684.3999 | 177 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2804.3165 | 301 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 159.9 | 53.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 262.9666 | 46 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1739.9999 | 180 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 45.4 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 335.5 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1794 | 117 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 188.7 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 309.8666 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 32.6833 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 81 | 81 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 627.0833 | 175 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1454.9332 | 128 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 366 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 939.9999 | 150 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7114.6665 | 184 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 136.2333 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 219.1333 | 76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 231.9166 | 121 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4839.9998 | 480 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 8813.6 | 92 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 25675.3331 | 380 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 146.74 | 95.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1445.25 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1779.6999 | 222 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 816 | 204 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2449.5 | 213 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1262.488 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 224.5833 | 25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 166.75 | 667 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3213 | 340 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.8333 | 50 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 524.3332 | 260 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2493.4332 | 254 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 237.405 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1002.6666 | 64 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9421.7499 | 195 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16919.8332 | 242 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3908.0833 | 115 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 145.5999 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 364 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 480.9999 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 153.4 | 767 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 555.5 | 110 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D3-Forced - Postponed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 107133.4993 | 1110 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.25 | 41 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 18 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2915.5 | 238 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 681.6159 | 180.96 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2363 | 139 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2627.2999 | 258 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5166.3832 | 239 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 226.0999 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1826.6833 | 127 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 133.75 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 250.85 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 76.2499 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 1477.25 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 286.25 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 273060 | 1110 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 240.25 | 155 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1225 | 140 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1538.5 | 181 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4754.1665 | 350 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2032.9332 | 158 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5403.6 | 237 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 815 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1496.5333 | 244 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 522.1999 | 84 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3583.6833 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 129.2499 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 69.5833 | 25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 294.8 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 71.4666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 171.0999 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 12200.5331 | 817 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41026.0662 | 661 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 10379.5833 | 145 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 226.3429 | 617.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4801.3665 | 229 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 63.2333 | 14 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3936.2499 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 682.5 | 90 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2332.35 | 73 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.875 | 37.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.8383 | 30.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 508 | 127 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 913.4666 | 104 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1504.8 | 114 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1665 | 185 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1433.8832 | 227 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 459.8 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2347.3998 | 291 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1966.5 | 171 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.5999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176.66 | 80.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1423.5 | 146 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3912.1 | 57 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1469.4165 | 229 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2160.9 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 815.5 | 70 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 4738.6 | 817 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 198.3999 | 96 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 967.1333 | 163 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3980 | 199 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4304.7833 | 181 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 77.9 | 123 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 248.71 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1178.941 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2394 | 266 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9916.6666 | 170 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9224.8 | 208 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 730.7333 | 113 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1556.1333 | 88 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 279.1666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 297.4999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 500.5 | 65 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 834 | 278 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1126.2498 | 255 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 30 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34329.8332 | 370 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 43886.9666 | 254 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 13371.6833 | 193 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1027.3666 | 37 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2840 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 62.5333 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.45 | 39 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2962.4999 | 225 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3526.3665 | 238 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6278.6666 | 170 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11602.2 | 244 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 844.8 | 26.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1110.8656 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4241.5333 | 244 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 3.6 | 36 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 742 | 742 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.75 | 27 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18423.34 | 240.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66784.7664 | 662 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.99996 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1195.8333 | 205 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 413.6 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1347.4999 | 210 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1496.9499 | 273 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43.65 | 27 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1794.985 | 370.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 93.3332 | 200 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 24.1667 | 25 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 116 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 667 | 667 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 876.3749 | 110.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18073.0664 | 412 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4595.5 | 202 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1430 | 143 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2086.8 | 74 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 500.5166 | 59 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1504.5333 | 217 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3793.5 | 135 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 77.5 | 31 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 602.4 | 25.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 1399.7333 | 232 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 611.31 | 8.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 526.785 | 6.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 20.2267 | 8.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 693 | 33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2337.6667 | 20 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1798.3333 | 52 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 527 | 31 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 429 | 33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 84 | 28 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 972 | 27 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 210.5833 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2022 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 315 | 35 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 42.3133 | 115.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 269.7799 | 197.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 17.1849 | 147.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 10.1566 | 55.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 32.4333 | 97.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 243.3366 | 197.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 20.6533 | 154.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 128.2366 | 124.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 71.485 | 84.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 256.125 | 204.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 36.5466 | 274.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 299.2382 | 197.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 22584.5666 | 302 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 13.4017 | 47.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 21.285 | 47.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 95.935 | 274.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 279.855 | 207.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 14.775 | 59.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 23.31 | 155.4 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 45.2766 | 79.9 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 131.11 | 187.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 25.9466 | 97.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 32.82 | 164.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 513.6515 | 204.1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U2 | Forced - Delayed | 2022 | Gas | GG | 851 | CC GT units | WECC | Summer | 189.8333 | 34 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U2-Forced - Delayed | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 10038.0833 | 163 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Winter | 1978.375 | 142.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 578.2633 | 61.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 10099.6666 | 164 | 2 | 2 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 23094.3999 | 168 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6766.2832 | 167 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 150.19 | 65.3 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 15611.7166 | 167 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6120.7999 | 168 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6885.9666 | 167 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | SF | Startup Failure | 2022 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1469.1832 | 171.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 132.9166 | 145 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 18906.0832 | 307 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | SF | Startup Failure | 2022 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 370.4166 | 87.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 665 | 190 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 436.8 | 117 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 72.5833 | 13 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 11010.3332 | 268 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2022 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 25044.6 | 268 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2022 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 603.2 | 208 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 852-CC steam units
1900 | Improper balance between tube sections not due to fouling or plugging | Boiler | Boiler Design Limitations | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 951.4666 | 64 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | U1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 35 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 52.9117 | 5.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 57.9617 | 8.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 39.9333 | 4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 83 | 8.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 59.9333 | 4 | 1 | 2 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 254.4 | 5.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1584 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 446.856 | 15.48 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 41.9 | 6 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.8675 | 32.85 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.1988 | 14.33 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180584.8166 | 31 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 21.2 | 5.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 143 | 13 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 512.2 | 2.6 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 204.3373 | 37.04 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 122003.35 | 21 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144850.4166 | 25 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180415.35 | 31 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 84 | 12 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 192 | 4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 91.3 | 8.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 79.4117 | 5.3 | 1 | 2 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75 | 15 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D2-Forced - Delayed | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.6326 | 42.07 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139131.6 | 24 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0.4 | 2 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 130 | 13 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 37.1 | 5.3 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.4455 | 31.83 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 144579.5833 | 25 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 97.7667 | 14 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 179.8 | 12 | 1 | 2 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 66 | 6 | 1 | 2 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 176 | 44 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.7333 | 56 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 434.6666 | 160 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 437.75 | 85 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1329.8332 | 505 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 514.5833 | 125 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 227.9 | 53 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1012 | 176 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 610.3998 | 336 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 21.84 | 7.28 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 650-Fluidized Bed
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 56.3333 | 169 | 1 | 1 | 1980-Boiler safety valve test | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20 | 60 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 559 | 172 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 573.7497 | 405 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2204.1667 | 23 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.6666 | 28 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 171.1667 | 13 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 281.8666 | 28 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 84 | 36 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45.7333 | 98 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 153.6 | 48 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 364.1667 | 38 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 487.3 | 33 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14.19 | 4.73 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 542.0332 | 161 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1366.2 | 207 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 309.0665 | 304 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 331.2 | 46 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 163.2 | 204 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 895.9331 | 302 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1103.2 | 48 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4029.4333 | 98 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20761.0665 | 268 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 475.2 | 48 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1708.4333 | 214 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 194.6665 | 365 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1143.4833 | 23 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1234.7167 | 23 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1594.6 | 28 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21260.8999 | 321 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4 | 16 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.1666 | 62 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.0333 | 13 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 919.7333 | 16 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2185 | 230 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | U3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10132.3994 | 876 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | U3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 124.5833 | 13 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 911.75 | 35 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 276 | 24 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.4165 | 217 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 85.8 | 13 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 248.7333 | 28 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 257.9833 | 23 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 24 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153 | 60 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 533 | 260 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 875.7831 | 281 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 48 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60.8 | 38 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1011.1833 | 13 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1885.0332 | 194 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 51.3667 | 23 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.8166 | 161 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 45.0427 | 10.64 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.16 | 0.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3085.1333 | 120.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2374.9 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 126.1167 | 9.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1236.75 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 5476.5 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 3 | 10 | 20 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.8 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.02 | 2.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.8 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.8 | 4.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.96 | 2.12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.97 | 3.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.8 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2206 | 120 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 6 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 3 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.1 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.07 | 2.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.7 | 0.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.4 | 0.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.4 | 1.2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1 | 5 | 10 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1.5 | 8 | 18 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 2 | 6 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.2 | 0.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.01 | 1.67 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 2 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.99 | 2.33 | 2 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.3 | 8.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.5 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.48 | 1.58 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.1 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 2.4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.4 | 2.48 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.08 | 4.02 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.3 | 8.15 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17 | 8.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28.98 | 2.07 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.87 | 6.41 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3775 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5850 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7560 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3373.4 | 167 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5087.9332 | 167 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 35 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 74.1333 | 139 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 188.7 | 102 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2660 | 380 | 2 | 2 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2000 | 400 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.4 | 0.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.638 | 26.07 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 179.75 | 7.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 558.25 | 223.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 640.5033 | 8.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 99.5037 | 12.49 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 566.6666 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1530 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 639.1667 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1026.6667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 2783.5 | 19 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 0 | 0 | 1 | 2 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 645.5167 | 11 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2393.7166 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.99 | 1.33 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 8 | 19 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.1 | 1.7 | 3 | 7 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 3 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.8 | 2.2 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 4.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 2.2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.01 | 3.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 3.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.99 | 2.11 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20 | 4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.99 | 7.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39 | 3.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 7 | 17 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 3 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 1.6 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.02 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.8 | 3.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.05 | 2.47 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.96 | 5.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.8 | 0.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 5 | 14 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 2.5 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 3 | 4 | 6 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.9 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 1.8 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 2.25 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.88 | 2.72 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.99 | 6.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.38 | 3.34 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3787.7499 | 417 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105264 | 765 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 67.4667 | 44 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10171.973 | 426.2 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 0 | 0 | 1 | 3 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 260.9333 | 10.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3895.7333 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1920.45 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 1 | 9 | 26 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.8 | 1.2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5 | 2.5 | 4 | 7 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.99 | 2.33 | 1 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.01 | 2.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 2 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.2 | 6.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.98 | 2.61 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.96 | 6.12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.4 | 3.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.8 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.8 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.02 | 2.17 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.04 | 2.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.7 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8.88 | 1.48 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.38 | 1.34 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.03 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.98 | 2.83 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 37.06 | 2.18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 956.6666 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2700 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6165 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 210.33 | 77.9 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3330.6666 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 185.5999 | 174 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 411.04 | 18.35 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 958.0632 | 180.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4045.5 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 360.9667 | 11.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 3 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1321.45 | 5.35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 43303.25 | 85 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.2 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9 | 2.25 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 2.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.99 | 4.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.6 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29 | 7.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.01 | 4.89 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1.5 | 5 | 10 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 2 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 11 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 2.5 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.01 | 8.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41 | 8.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.04 | 2.28 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 8.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.4 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9 | 1.3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.2 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 1.5 | 4 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.33 | 1.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21.8 | 10.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40.15 | 3.65 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 425.4433 | 90.2 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1940 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23648.3333 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43399.2998 | 357 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3289.5 | 765 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 124.55 | 141 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 127.4166 | 139 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.62 | 5.62 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1412.8333 | 70 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 220.5683 | 58.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20839.75 | 155 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 194.7877 | 10.27 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 205.4167 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1689.5 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.01 | 4.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.4 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16 | 1.6 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18 | 3.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.2 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 10.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.5 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.9 | 1.3 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 1.8 | 4 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23.01 | 1.77 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.5 | 1.5 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2.3 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7.89 | 2.63 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30.06 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64.02 | 5.82 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1063.2332 | 167 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | SERC | Winter | 305683.4028 | 787.1 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13.086 | 21.81 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 49.5833 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2223.75 | 75 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.74 | 0.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.3267 | 14.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11957.7 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 201.2949 | 95.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 824.419 | 210.49 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7201.6666 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15800 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 89.18 | 9.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 116.2 | 8.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 282.4333 | 22.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 363.7333 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 207.1 | 21.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 257.2667 | 22.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1530.0832 | 215 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.9 | 1.3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.9 | 2.3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.1 | 2.7 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.1 | 5.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.9 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 20.4 | 1.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37.7 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45 | 2.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 3 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.01 | 1.67 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.5 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 3.5 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.98 | 1.83 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 5.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 3 | 3 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.02 | 2.78 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.8 | 4.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.4 | 1.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.3 | 3.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.4 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.01 | 3.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12.9 | 4.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24.99 | 8.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 34.96 | 4.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 288.4008 | 18.35 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 236.3 | 139 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.975 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.99 | 15.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.9 | 15.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 877.5 | 78 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1614.6967 | 10.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15733.25 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25382 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 282 | 47 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 91.14 | 9.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1129.05 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 104.9667 | 9.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 125.6666 | 52 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.5 | 1.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7 | 3.5 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.55 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.02 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12.1 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.2 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.96 | 1.87 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.01 | 5.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.2 | 1.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.96 | 2.37 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.6 | 2.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.04 | 2.08 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.99 | 1.33 | 4 | 4 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 5 | 7 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 1.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.35 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12 | 12 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 7.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.02 | 2.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.97 | 2.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 5.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.6 | 0.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.3 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7 | 1.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.1 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9.6 | 1.92 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11 | 2.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19 | 4.75 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22 | 5.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 42 | 5.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.01 | 3.91 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 43.2 | 14.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.06 | 3.62 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 115.92 | 5.52 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 985 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2216.6666 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5175 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16575 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1463.19 | 770.1 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11900 | 850 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 88389.9 | 342 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3286.9133 | 22.9 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2022 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 10201.05 | 453.38 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32.775 | 17.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 532.6667 | 47 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.6 | 20.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 621.0717 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 82.6667 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 858.3333 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2300 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9369.6785 | 335.23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11094 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15666.6666 | 100 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2022 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 241.2067 | 9.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam