## Instructions
Cause Code Report
The Cause Code report is an export from NERC's GADS data
Cause Codes are identified for each Event
Each Event has an attributed capacity in Megawatts, as well as duration where generation loss in Megawatt hours can be calculated.
The Report includes different types of Forced Outages and Deratings: Forced Immediate (U1, D1), Forced Delay (U2, D2), Force Postponed (U3, D3) and Startup Failure (SF).
Excluded are Planned Outages and Deratings, Maintenance Outages and Deratings, Reserve Shutowns, and any other non-forced outages.
The Data page is the aggregated export file.
This export masks the identity of each unit by aggregating data instead of including each confidential data item.
Each Cause Code with similar units are listed on the same row
The Report Page allows different analysis
| Cause Code | The identified cause of an event. For events with multiple cause codes, only the primary cause code is tallied.
| Sum of Distinct Untis | The number of units that were tallied to create the row
| Sum of Event Count | the number of events that were tallied to create the row
| Sum of MW Lost | The sum of MegaWatts lost during the Events in each row
| Sum of MWHrsLost | The sum of MegaWatt Hours lost during the Events in the row
Pre-populated Filters allow ease of use to go from broad analysis to more granular analysis
|  | Season |  | Summer months are from June - september.Winter Months December -February.
|  |  | Off-Peak |  | Neither Wintor Nor summer months
|  |  | Summer |  | Peak Summer months
|  |  | Winter |  | Peak Winter months
|  | Region code |  | NERC defined regions can give some territorial information.
|  |  | MRO |  | Midwest Reliability Organization
|  |  | NPCC |  | Northeast Power Coordinating Council
|  |  | RF |  | ReliabilityFirst
|  |  | SERC |  | SERC Reliabilty Council
|  |  | TRE |  | Texas Reliability Entity
|  |  | WECC |  | West Electric Coordinating Council
|  | Fuel Category |  | some fuels are used among different unit types
|  |  | Coal | solid coal fuel
|  |  | Gas | air-burned fuel
|  |  | Hydro | Water turbine
|  |  | Nuclear | Nuclear radioactive fuel
|  |  | Oil | Liquid fuel
|  |  | Other | fuel not categorized in other categories
|  |  | Waste Heat | Vented heat from primary fuel source
|  | Unit Type |  | some unit types burn different types of fuel
100- Fossil-Steam
200 - Nuclear
300 - Gas Turbine / Jet Engine
400 - Internal Combustion / Reciprocating Engine
500 - Pumped Storage / Hydro
650 - Fluidized Ben
800 - Miscellaneous
810 - Multi-Boiler / Multi-turbine
850 - Combined Cycle Block
851 - Combined Cycle Gas Turbine
852 - Combined Cycle Steam unit
860 - Cogeneration Block
861 - Cogeneration Gas Turbine
862 - Cogeneration Steam unit
|  | Event Type |  | there are several types of Forced Event Types, Outages remove the full capacity of the unit, Deratings remove partial capacity from the unit.
D1 - Forced immediate Derating
D2 - Forced Delayed Derating
D3 - Forced Postponed Derating
U1 - Forced Immediate Outage
U2 - Forced Delayed Outage
U3 - Forced Postponed Outage
SF - Startup Failure
|  | System Name |  | Cause Codes fall under different Systems of a plant. Some systems apply to all Unit Types, others aply to certain unit types.
Balance of Plant
Boiler
Diesel Engine
External
Gas Turbine
Generator
HRSG Boiler
Hydro Turbine / Pump
Nuclear Reactor
Performance
Personnel Errors
Pollution control Equipment
Regulatory, Safety, Environmental
Steam Turbine
|  | Component Name |  | Components are subsets under the System Name. Each System has a different set of Components
Each cause Code has an associated Component that falls under one of the listed Systems

## Report
Season | - all -
RegionCode | - all -
FuelCategory | - all -
UnitType | - all -
EventType | - all -
SystemName | - all -
ComponentName | - all -
Data
Cause | Count of EVENT_COUNT | Count of DISTINCT_UNITS | Sum of MWLost | Sum of MWHrsLost
0020-Coal car dumpers; shakers; and unloaders | 18 | 18 | 5885 | 216588.6146
0022-Unloading/receiving hopper (train/truck) | 2 | 2 | 43 | 262816.0333
0024-Rotary plow | 1 | 1 | 277 | 4704.3832
0028-Dust collection system | 14 | 14 | 3344.3 | 181657.5845
0030-Coal conveyors and feeders | 230 | 230 | 53090.97 | 649325.892
0035-Metal detector/collector (including magnetic separator) | 2 | 2 | 704 | 8974.8496
0060-Coal crushers including motors | 8 | 8 | 988.67 | 4588.9734
0075-Storage silos/hoppers | 16 | 16 | 2716.68 | 53605.5534
0080-Stackers/reclaimers | 16 | 16 | 2572.47 | 19010.0683
0084-Coal conveyor scales-storage coal pile | 1 | 1 | 458 | 5022.733
0085-Bunker feeder coal scales | 2 | 2 | 67.7 | 405.5
0090-Bunker fires | 3 | 3 | 732.7 | 7700.8998
0095-Bunker flow problems | 43 | 43 | 4205.2 | 53378.2673
0100-Bunker gates | 5 | 5 | 412.6 | 5044.9999
0105-Bunker structures | 6 | 6 | 227 | 85106.9333
0110-Other coal fuel supply problems up through bunkers | 39 | 39 | 8132.31 | 97679.5846
0111-Solid fuel feeder conveyors | 53 | 53 | 651.18 | 21535.5613
0112-Solid fuel feed tanks/hoppers | 2 | 2 | 53.1 | 765.5167
0114-Solid fuel volumetric feeder | 6 | 6 | 145.2 | 1248.2
0115-Solid fuel gravimetric feeder | 9 | 9 | 308.83 | 3765.3228
0116-Solid fuel feeder motors | 1 | 1 | 8.3 | 249.9683
0121-Other solid fuel feed problems | 161 | 161 | 2003.46 | 43301.1419
0125-Coal crusher dryer hammers | 1 | 1 | 287 | 4352.8331
0129-Other coal processing system problems | 11 | 11 | 1925.8 | 8108.8524
0200-Pulverizer exhauster fan (for indirect firing) | 4 | 4 | 614.8 | 17005.11
0205-Pulverizer exhauster fan drive | 7 | 7 | 622 | 18537.9448
0240-Pulverized coal bin | 6 | 6 | 1086.62 | 6799.3458
0250-Pulverizer feeders | 656 | 656 | 70455.99 | 925308.1019
0253-Pulverizer feeder motor | 46 | 46 | 5106.31 | 617836.4437
0255-Pulverizer feeder coal scales | 4 | 4 | 519 | 5383.5999
0256-Seal air system (air to pulverizers) | 18 | 18 | 4538.8 | 240584.2967
0257-Coal Crusher/dryer between feeder and pulverizer | 5 | 5 | 752.66 | 4939.7001
0260-Primary air fan | 156 | 156 | 22225.07 | 719975.7998
0262-Primary air fan lube oil system | 7 | 7 | 1914.12 | 17538.0096
0263-Primary air fan drives | 42 | 42 | 5755.88 | 64266.1948
0264-Other primary air fan problems | 31 | 31 | 6134.83 | 182011.1225
0265-Primary air heater | 10 | 10 | 2678 | 87591.8159
0267-Primary air flow instrumentation | 22 | 22 | 4739.3 | 29517.0479
0270-Primary air duct and dampers | 118 | 118 | 12858.21 | 273044.0588
0280-Pulverizer fires | 24 | 24 | 3851.6 | 143742.3437
0290-Pulverizer reduced capacity due to wear | 6 | 6 | 818 | 304825.4332
0300-Pulverizer motors and drives | 90 | 90 | 8274.21 | 166485.0766
0310-Pulverizer mills | 832 | 832 | 80775.78 | 3306589.9037
0312-Pulverizer mill classifiers | 29 | 29 | 3640 | 39994.7238
0313-Pulverizer mill trunnion seals | 4 | 4 | 483 | 6058.4331
0315-Pulverizer mill coal level controls | 2 | 2 | 179.3 | 465.2799
0320-Foreign object in Pulverizers mill | 68 | 68 | 3204.59 | 16726.8081
0325-Pulverizer skidding | 5 | 5 | 482.54 | 13136.5018
0330-Pulverizer coal leak (pulverizers only) | 74 | 74 | 7764.2 | 159362.4957
0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | 42 | 42 | 4250.5 | 15150.752
0335-Pulverizer lube oil system | 63 | 63 | 7851.29 | 273000.0793
0338-Pulverizer control systems (temperature and pressure) | 36 | 36 | 3043.94 | 15899.1639
0339-Pulverizer System Puff | 12 | 12 | 1762.22 | 12363.4898
0340-Other pulverizer problems | 206 | 206 | 19618.46 | 570136.7027
0342-Pulverizer inert system | 15 | 15 | 2080.74 | 36749.3063
0344-Pulverizer inspection | 26 | 26 | 2455.95 | 47335.4961
0345-Pulverizer overhaul | 34 | 34 | 1318.42 | 142991.2014
0346-Pulverizer pyrite removal system | 94 | 94 | 9789.75 | 91082.7826
0350-Pulverized fuel and air piping (from pulverizer to wind box) | 51 | 51 | 4213.03 | 40696.8716
0358-Oil burner piping and valves | 2 | 2 | 94.2 | 1427.1
0359-Gas burner piping and valves | 127 | 127 | 24029.26 | 669681.4738
0360-Burners | 161 | 161 | 10384.69 | 307279.4895
0370-Burner instruments and controls (except light-off) | 134 | 134 | 19617.28 | 1036239.3493
0380-Light-off (igniter) systems (including fuel supply) | 57 | 57 | 10086.3 | 127746.4555
0385-Igniters | 46 | 46 | 11754.26 | 71098.9241
0390-Burner wind boxes and dampers | 6 | 6 | 890 | 6356.9163
0400-Burner wind box fires | 11 | 11 | 3172 | 758817.4828
0410-Other burner problems | 31 | 31 | 2420.3 | 173597.5392
0415-Cyclone feeders | 100 | 100 | 6739.55 | 87082.4106
0420-Cyclone crusher | 18 | 18 | 513 | 11506.2832
0425-Cyclone dampers | 8 | 8 | 868 | 3740.6162
0426-Cyclone air ducts | 11 | 11 | 417 | 1738.7664
0430-Cyclone furnace | 16 | 16 | 837 | 111069.5331
0435-Other cyclone problems | 55 | 55 | 3242 | 89988.4309
0440-Fuel oil pumps (general) | 7 | 7 | 1815.5 | 29922.7991
0441-Fuel oil pumps (burner supply) | 3 | 3 | 297 | 1479.6665
0450-Fuel oil heaters | 2 | 2 | 445.97 | 1137.2235
0460-Fuel oil atomizers | 2 | 2 | 55 | 4403.3333
0470-Oil and gas fires | 13 | 13 | 1914.7 | 1768285.4826
0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | 45 | 45 | 10801.04 | 103469.7788
0500-Main steam piping up to turbine stop valves | 44 | 44 | 8637.7 | 1610907.1013
0510-Main steam relief/safety valves off superheater | 36 | 36 | 7158.9 | 147513.155
0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | 36 | 36 | 9438.47 | 404186.3461
0530-Other main steam system problems | 35 | 35 | 4177.87 | 233137.2212
0540-Hot reheat steam piping up to turbine stop valves | 29 | 29 | 8584.01 | 893264.3115
0541-Cold reheat steam piping up to boiler | 25 | 25 | 5528.22 | 641117.1384
0550-Reheat steam relief/safety valves | 23 | 23 | 3095.82 | 74201.8105
0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | 41 | 41 | 11609.8 | 218127.9265
0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | 29 | 29 | 6562.57 | 113093.0553
0570-Other reheat steam problems | 31 | 31 | 4130.39 | 127188.1084
0580-Desuperheater/attemperator piping | 7 | 7 | 2544.6 | 57451.4658
0590-Desuperheater/attemperator valves | 49 | 49 | 11189.15 | 541780.0294
0610-Desuperheater/attemperator drums | 1 | 1 | 208.69 | 925.1923
0620-Other desuperheater/attemperator problems | 5 | 5 | 2592.2 | 7130.9912
0630-Startup bypass system piping (including drain lines up to heaters or condenser) | 2 | 2 | 1343 | 61140.3997
0640-Startup bypass system valves | 27 | 27 | 17437 | 659522.2059
0650-Startup bypass tanks or flash tanks | 5 | 5 | 4605.3 | 22444.122
0670-Feedwater piping downstream of feedwater regulating valve | 9 | 9 | 907.7 | 8771.4315
0680-Feedwater valves (not feedwater regulating valve) | 40 | 40 | 6380.1 | 238070.2919
0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | 16 | 16 | 2078.5 | 14960.8745
0700-Blowdown system valves A | 8 | 8 | 2223.03 | 40526.8681
0710-Blowdown system piping B | 15 | 15 | 4005.3 | 446868.0323
0730-Other blowdown system problems | 6 | 6 | 536.6 | 9382.5364
0740-Boiler recirculation pumps | 40 | 40 | 8302.96 | 588598.8812
0741-Boiler recirculation pumps - motors | 22 | 22 | 4394.68 | 537523.2307
0742-Boiler recirculation pumps - motors - cooling system | 11 | 11 | 2301 | 443623.5654
0750-Boiler recirculation piping including downcomers | 3 | 3 | 1212 | 74007.0997
0760-Boiler recirculation valves | 12 | 12 | 2252.51 | 308542.2006
0770-Other boiler recirculation problems | 3 | 3 | 782 | 20959.4496
0775-Economizer piping | 16 | 16 | 2356.3 | 97305.8496
0780-Headers between tube bundles | 5 | 5 | 2868.57 | 339354.9842
0790-Pipe hangers; brackets; supports (general) | 4 | 4 | 1053.92 | 21519.1623
0799-Other miscellaneous piping system problems | 22 | 22 | 4095.7 | 2093076.317
0800-Drums and drum internals (single drum only) | 91 | 91 | 24944.86 | 420198.8829
0801-HP Drum (including drum level trips not attributable to other causes) | 98 | 98 | 15759.61 | 169494.9039
0802-IP Drum (including drum level trips not attributable to other causes) | 68 | 68 | 11079.15 | 72499.046
0803-LP Drum (including drum level trips not attributable to other causes) | 27 | 27 | 4563.6 | 25122.3581
0810-Boiler supports and structures (use code 1320 for tube supports) | 13 | 13 | 1266 | 233926.3165
0820-Casing | 52 | 52 | 7052.33 | 608056.4626
0830-Doors | 20 | 20 | 3306.5 | 93301.4986
0840-Refractory and insulation | 13 | 13 | 2557.8 | 710315.5992
0847-Other expansion joints | 4 | 4 | 742.6 | 90525.5398
0850-Other internal or structural problems | 8 | 8 | 2179.5 | 277156.1575
0855-Drum relief/safety valves (Single drum only) | 26 | 26 | 4198.1 | 98375.3625
0856-HP Drum relief/safety valves | 6 | 6 | 464.6 | 22881.2298
0857-IP Drum relief/safety valves | 1 | 1 | 141 | 2328.8499
0859-Tube external fins/membranes A | 9 | 9 | 1477.75 | 134401.6841
0870-Soot blowers - steam | 31 | 31 | 3126.3 | 131172.5491
0873-Soot blower drives | 1 | 1 | 41.4 | 18.63
0876-Soot blower controls | 28 | 28 | 4711.4 | 30328.8718
0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | 36 | 36 | 4621.54 | 130133.6618
0885-Fly ash Removal System - wet transport | 3 | 3 | 236.04 | 3895.4752
0890-Bottom ash systems (wet or dry) | 78 | 78 | 14114.75 | 493790.8525
0891-Bottom ash hoppers (including gates) | 18 | 18 | 3235.06 | 686083.6923
0892-Bottom ash clinker grinders | 5 | 5 | 1695 | 91338.2331
0893-Bottom ash water pumps and motors | 4 | 4 | 1028.2 | 29450.6865
0894-Bottom ash piping and valves | 3 | 3 | 485.3 | 15572
0895-Ashpit trouble | 10 | 10 | 843.36 | 7776.3855
0897-Bottom ash rotary (drag chain type) conveyor and motor | 72 | 72 | 23436.54 | 516480.2285
0898-Bottom ash pyrite hopper (pulverizer reject) system | 6 | 6 | 1231.78 | 17895.74
0900-Slag-tap (cyclone furnace) | 5 | 5 | 2286.48 | 321259.0128
0920-Other slag and ash removal problems A | 74 | 74 | 8388.79 | 427310.3437
0930-Bed material coolers | 4 | 4 | 130 | 2145
0936-Bed material conveyors B | 1 | 1 | 43 | 622.0666
0950-Other bed material system problems | 4 | 4 | 226.5 | 2864.5333
0989-Other bed solids recirculation problems | 16 | 16 | 555.96 | 40299.1252
0991-Tube leaks | 17 | 17 | 443.72 | 26194.3759
0999-Other heat exchanger problems | 10 | 10 | 37.1 | 219.8
1000-Waterwall (Furnace wall) | 465 | 465 | 142114.56 | 12376767.4126
1003-Steam generating tubes between steam drum and mud drum | 15 | 15 | 3080.5 | 364381.1971
1005-Generating tubes | 19 | 19 | 2086.6 | 112690.8162
1010-Cyclone furnace (in cyclone area only) | 6 | 6 | 2302 | 64147.766
1020-Convection pass wall (water tubes only) | 22 | 22 | 5780.78 | 330370.2732
1030-Boiler screen; wing wall; or slag screen (water tubes only) | 27 | 27 | 9445.9 | 946775.1594
1035-Platen superheater | 37 | 37 | 13459.66 | 1662996.5049
1040-First superheater | 84 | 84 | 23510.78 | 2842627.1063
1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | 1 | 1 | 259 | 49961.1
1050-Second superheater | 91 | 91 | 36921.58 | 4306531.1556
1055-External superheater link tubing | 4 | 4 | 2293 | 226302.1664
1060-First reheater | 100 | 100 | 39536.87 | 3559064.7425
1070-Second reheater | 18 | 18 | 8501.07 | 550753.0503
1075-External reheater link tubing | 2 | 2 | 574 | 25979.2166
1080-Economizer | 73 | 73 | 17919.6 | 1441344.5639
1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | 1 | 1 | 315 | 78849.7498
1090-Other boiler tube leaks | 119 | 119 | 39114.95 | 4712042.4173
1100-Waterwall (Furnace wall) | 30 | 30 | 4299 | 488209.1819
1105-Generating tubes | 4 | 4 | 324.96 | 21098.4999
1110-Cyclone furnace (in cyclone area only) | 8 | 8 | 667 | 16649.3497
1120-Convection pass wall | 4 | 4 | 114.3 | 11390.735
1130-Boiler screen; wing wall; or slag screen (water tubes only) | 3 | 3 | 1233.1 | 45829.6349
1140-First superheater | 19 | 19 | 732.31 | 75786.5135
1150-Second superheater | 23 | 23 | 1986.1 | 159532.2862
1160-First reheater | 17 | 17 | 1339.31 | 84315.4764
1170-Second reheater | 12 | 12 | 334.6 | 8058.5415
1180-Economizer | 7 | 7 | 1292.5 | 22578.4166
1190-Other tube slagging or fouling | 88 | 88 | 6659.35 | 383683.621
1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | 11 | 11 | 2246.9 | 12426.5662
1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | 9 | 9 | 915.71 | 106102.2909
1340-Tube modifications (including addition and removal of tubes) | 4 | 4 | 393.2 | 331686.6
1350-Other miscellaneous boiler tube problems | 54 | 54 | 5008.01 | 663213.1708
1360-Boiler drains system | 10 | 10 | 4046.8 | 116041.5156
1400-Forced draft fans | 169 | 169 | 21147.65 | 2956638.172
1401-Forced draft fan dampers | 47 | 47 | 6012.28 | 83457.2461
1407-Forced draft fan lubrication system | 10 | 10 | 2450.26 | 84402.4369
1410-Forced draft fan motors | 61 | 61 | 12019.88 | 2138517.728
1411-Forced draft fan motors - variable speed | 9 | 9 | 1587.87 | 920891.0494
1412-Forced draft fan drives (other than motor) | 19 | 19 | 6792.78 | 1255406.7325
1413-Forced draft fan couplings | 3 | 3 | 605.9 | 40428.5781
1415-Forced draft fan controls | 34 | 34 | 7349.43 | 59371.2027
1420-Other forced draft fan problems | 34 | 34 | 4926.11 | 738068.7062
1421-Secondary air fans/blowers | 10 | 10 | 1844.62 | 27869.6064
1422-Secondary air fan/blower motors - single speed | 3 | 3 | 431 | 11166.1332
1423-Secondary air fan/blower motors - variable speed | 6 | 6 | 2372.9 | 3089.9217
1424-Secondary air fan/blower controls | 3 | 3 | 509 | 4620.6333
1430-Air supply ducts from FD fan | 10 | 10 | 1187.3 | 121697.438
1431-Air supply dampers from FD fan | 2 | 2 | 379.43 | 5463.8981
1432-Air supply duct expansion joints | 23 | 23 | 868 | 66458.9999
1440-Air supply dampers | 7 | 7 | 779 | 6726.833
1450-Other air supply problems | 74 | 74 | 6045.64 | 1368466.1502
1455-Induced draft fans | 673 | 673 | 48133.92 | 3761705.131
1456-Induced draft fan dampers | 45 | 45 | 7778.8 | 300044.0437
1457-Induced draft fan lubrication systems | 28 | 28 | 9260.99 | 174728.5389
1460-Induced draft fan fouling | 39 | 39 | 4017.93 | 280738.4914
1470-Induced draft fan motors and drives | 145 | 145 | 24233.67 | 2227793.0959
1471-Induced draft fan motors - variable speed | 38 | 38 | 9580.25 | 265339.5166
1472-Inducted draft fan coupling | 3 | 3 | 430 | 232268.9666
1475-Induced draft fan controls | 123 | 123 | 18334.67 | 1094875.1655
1476-Induced draft fan speed changer | 7 | 7 | 1212.4 | 60553.5799
1480-Other induced draft fan problems | 157 | 157 | 23198.48 | 1332415.1382
1487-Air heater (tubular) | 25 | 25 | 2190.4 | 100191.1588
1488-Air heater (regenerative) | 160 | 160 | 29888.63 | 1103640.7164
1489-Air heater (heat pipe; plate-type) | 12 | 12 | 2402.5 | 1352802.7575
1492-Air heater fouling (tubular) | 4 | 4 | 486 | 39898.9331
1493-Air heater fouling (regenerative) | 93 | 93 | 3225.3 | 463526.7771
1495-Other air heater fouling (heat pipe; plate-type) | 13 | 13 | 1692 | 112157.7829
1500-Air heater soot blowers | 2 | 2 | 973 | 32477.6329
1510-Flue gas ducts (except recirculation) | 27 | 27 | 1209 | 255207.5777
1512-Flue gas expansion joints | 8 | 8 | 1660.98 | 213050.5906
1520-Flue gas dampers (except recirculation) | 10 | 10 | 753.7 | 196987.4464
1530-Other flue gas problems | 14 | 14 | 1653.13 | 322962.696
1535-Flue gas recirculating fan | 11 | 11 | 797 | 161271.2997
1550-Flue gas recirculation fan motors | 4 | 4 | 539 | 319943.0666
1570-Flue gas recirculation ducts | 1 | 1 | 146 | 16176.8
1580-Flue gas recirculation dampers | 1 | 1 | 65 | 249.1666
1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | 6 | 6 | 493.21 | 2314.9138
1591-Stack damper and linkage | 6 | 6 | 1658 | 7410.3826
1592-Stack damper linkage motors | 1 | 1 | 195.6 | 648.7399
1599-Other miscellaneous boiler air and gas system problems | 190 | 190 | 10676.57 | 872278.9558
1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | 209 | 209 | 36787.45 | 843698.6731
1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | 216 | 216 | 14844.49 | 586485.066
1720-Desuperheater/attemperator controls | 56 | 56 | 8774.24 | 74246.0651
1740-Boiler drum gage glasses/level indicator | 75 | 75 | 13419.28 | 104197.2407
1750-Burner management system | 135 | 135 | 21864.55 | 414843.8445
1760-Feedwater instrumentation (not local controls) | 33 | 33 | 7986.62 | 133545.5507
1761-Combustion /Steam condition instrumentation (not local controls) | 29 | 29 | 6185.38 | 27055.8543
1762-Desuperheater/attemperator instrumentation (not local controls) | 13 | 13 | 2052 | 17156.8323
1799-Other boiler instrumentation and control problems | 139 | 139 | 34376.95 | 1229086.5973
1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | 2 | 2 | 345 | 48258.9999
1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | 32 | 32 | 1658.75 | 47567.1613
1810-Other boiler inspections | 4 | 4 | 181.85 | 5799.9333
1811-Boiler Inspections - problem identification/investigative | 4 | 4 | 763.25 | 61154.0112
1812-Boiler Inspections - scheduled or routine | 9 | 9 | 1003.11 | 292733.5072
1850-Boiler water condition (not feedwater water quality) | 178 | 178 | 29521.88 | 583223.7445
1900-Improper balance between tube sections not due to fouling or plugging | 1 | 1 | 261.44 | 575.168
1910-Inadequate air not due to equipment problems | 29 | 29 | 869.96 | 131395.3064
1980-Boiler safety valve test | 9 | 9 | 919.5 | 10589.1998
1990-Boiler performance testing (use code 9999 for total unit performance testing) | 32 | 32 | 5496.82 | 76645.6823
1999-Boiler; miscellaneous | 463 | 463 | 30147.01 | 663619.3666
2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | 47 | 47 | 6522.81 | 138404.6107
2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | 3 | 3 | 148.89 | 21395.3266
2062-Other fuel/core related instrumentation problems | 2 | 2 | 1274 | 177856
2070-Normal refueling | 6 | 6 | 6972 | 903074.8643
2140-Control rod drive cooling | 1 | 1 | 17 | 47.6
2151-Control rod drive controls | 1 | 1 | 8 | 130
2155-Control rod testing | 1 | 1 | 47.96 | 455.62
2200-Reactor coolant/recirculating pumps | 20 | 20 | 7969.4 | 842838.8668
2210-Reactor coolant/recirculating pump motors | 3 | 3 | 2042 | 666027.5831
2220-Reactor coolant/recirculating pump MG sets | 2 | 2 | 143 | 302.2832
2270-Power operated relief and safety/relief valves | 4 | 4 | 2529.61 | 120876.7976
2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | 2 | 2 | 1168.84 | 48984.5447
2380-Reactor control system/integrated control system problems | 2 | 2 | 1105 | 57691.4499
2390-Other reactor coolant system instruments and controls | 2 | 2 | 1362 | 137024.8991
2440-Steam generator chemistry (excluding feedwater chemistry) | 8 | 8 | 1418.7 | 202738.5084
2480-Other blowdown | 1 | 1 | 8.71 | 4.5002
2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | 2 | 2 | 20 | 24.6667
2799-Other containment system problems | 12 | 12 | 8037.75 | 187486.5394
2817-Instruments and controls | 1 | 1 | 16 | 318.6667
2819-Other CVCS and RWC problems | 1 | 1 | 52.13 | 329.2878
2820-Nuclear closed cooling water pumps | 1 | 1 | 69.4 | 7517.1766
3110-Condenser tube leaks | 154 | 154 | 36507.81 | 2841399.8715
3111-Condenser tube fouling shell side | 7 | 7 | 117 | 142506.75
3112-Condenser tube fouling tube side | 285 | 285 | 14470.29 | 729230.9253
3113-Condenser tube and water box cleaning (including circulating water flow reversal) | 70 | 70 | 15872.9 | 272524.53
3114-Air-cooled condenser tubes | 7 | 7 | 1173.83 | 119515.8891
3116-Air-cooled condenser fans | 47 | 47 | 3029.4 | 28194.8997
3117-Air-cooled condenser fan motors | 2 | 2 | 3 | 18
3118-Other Air-cooled condenser problems | 215 | 215 | 4893.4 | 44496.6486
3119-Other condenser tube casing or shell and internal problems | 11 | 11 | 561.28 | 869325.415
3120-Tube sheets | 11 | 11 | 2635.5 | 123480.5325
3121-Expansion joint | 3 | 3 | 909 | 129649.9998
3122-Gaskets and seals | 7 | 7 | 1120.78 | 48006.7635
3123-Hot well | 8 | 8 | 2347.2 | 14367.9415
3124-Tube sheet fouling | 12 | 12 | 1011 | 21211.6996
3129-Other condenser casing or shell and internal problems | 16 | 16 | 2088.5 | 55503.9911
3130-Air ejectors | 11 | 11 | 1639.89 | 32973.5805
3131-Air ejector piping and valves | 9 | 9 | 1363.34 | 5767.3297
3132-Inter and after condensers | 4 | 4 | 776 | 14923.783
3133-Vacuum pumps | 101 | 101 | 9842.4 | 79592.3592
3134-Vacuum pump piping and valves | 14 | 14 | 2637.31 | 76912.7856
3135-Vacuum pump motor and auxiliaries | 8 | 8 | 703 | 2696.7665
3139-Other air extraction system problems - general | 12 | 12 | 1812.61 | 25113.8838
3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | 325 | 325 | 35908.24 | 1319037.6838
3150-Hot well level controls | 26 | 26 | 4005 | 53406.9156
3151-Vacuum pump and air ejector controls | 5 | 5 | 793.15 | 1480.4007
3152-Air-cooled condenser controls | 2 | 2 | 287.8 | 442.4432
3159-Other condensing system controls and instruments | 9 | 9 | 1393.51 | 17303.2427
3186-Auxiliary Condenser and Associated Equipment | 32 | 32 | 1324.66 | 29789.8564
3190-Air leakage (for losses not attributable to previously noted equipment related codes) | 23 | 23 | 5053.01 | 430473.3304
3199-Other miscellaneous condensing system problems | 124 | 124 | 9316.08 | 184532.2287
3210-Circulating water pumps | 225 | 225 | 27609.1 | 1799960.3434
3211-Circulating water pump motors | 116 | 116 | 12498.58 | 737473.1074
3220-Circulating water piping | 31 | 31 | 9569.59 | 661469.8405
3221-Circulating water piping fouling | 3 | 3 | 228 | 48439.7
3230-Circulating water valves | 36 | 36 | 6546.1 | 1190663.3389
3231-Waterbox | 24 | 24 | 6307.77 | 150802.3804
3232-Condenser tube cleaning system including debris filter | 19 | 19 | 5007.05 | 90423.823
3235-Cooling tower booster pump | 7 | 7 | 1683.77 | 181669.8114
3238-Cooling tower fan motors | 13 | 13 | 995.39 | 6997.3933
3239-Cooling tower fan motors - variable speed | 3 | 3 | 285.73 | 4432.2532
3240-Cooling tower fans | 66 | 66 | 3549.45 | 249540.2666
3241-Cooling tower efficiency below design | 20 | 20 | 868.85 | 43323.1603
3242-Cooling tower fill damage | 2 | 2 | 95 | 6160.3333
3245-Other cooling tower problems | 30 | 30 | 4441.32 | 858306.0412
3247-Cooling tower instrumentation | 6 | 6 | 1347.38 | 69741.8861
3250-Circulating water system instruments and controls | 10 | 10 | 1432.5 | 7916.1797
3260-Traveling screens | 29 | 29 | 4751.99 | 102508.8173
3261-Traveling screen fouling | 3 | 3 | 285.6 | 674.5833
3269-Circulating water biological conditions (ie; zebra mussels) | 5 | 5 | 1005.95 | 8304.7681
3270-Intake system problems other than traveling screens | 28 | 28 | 4005.54 | 113334.1233
3271-Intake grating fouling | 3 | 3 | 111.5 | 1954.05
3272-Circulating water screenwash system | 3 | 3 | 648 | 17674.6666
3273-Debris in circulating water from outside sources (leaves; mud; etc.) | 29 | 29 | 6128.21 | 164341.1351
3274-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc B | 1 | 1 | 61.8 | 397.58
3280-High circulating water temperature (not due to season; tower efficiency below design; or other listed equipment problem) | 51 | 51 | 5679.48 | 82807.4507
3281-Circulating water tempering system | 4 | 4 | 466 | 11718.4832
3282-Circulating water cooling ponds | 16 | 16 | 459.3 | 19062.0565
3285-Circulating water chemistry | 2 | 2 | 20.15 | 42.9333
3290-Waste water (zero discharge) tanks; pumps and motors | 1 | 1 | 191 | 1034.5832
3299-Other circulating water system problems | 61 | 61 | 9229.19 | 776293.209
3300-Condensate water pre-treatment | 14 | 14 | 2863.7 | 166491.3089
3310-Condensate/hotwell pumps | 119 | 119 | 19713.11 | 429117.0354
3311-Condensate/hotwell pump motor | 47 | 47 | 7435.67 | 643973.9274
3312-Condensate booster pump | 8 | 8 | 1302.2 | 7381.5681
3313-Condensate booster pump motor | 5 | 5 | 258 | 1282.7166
3314-Condensate booster pump motor - variable speed | 4 | 4 | 651 | 7558.7
3320-Condensate piping | 8 | 8 | 2569.44 | 83495.4856
3330-Condensate valves | 40 | 40 | 11594.84 | 197018.9967
3339-LP heater head leaks | 1 | 1 | 151 | 40015
3340-LP heater tube leaks | 8 | 8 | 1639 | 220960.953
3341-Other LP heater - general | 31 | 31 | 4857.09 | 78405.1384
3342-IP heater tube leaks | 5 | 5 | 228.29 | 20511.9593
3343-Other IP heater - general | 7 | 7 | 3175 | 17262.1657
3344-Deaerator (including level control) | 74 | 74 | 11959.9 | 715953.3441
3350-Condensate polishing and filtering systems | 47 | 47 | 5766.2 | 120728.5303
3351-Chemical addition systems | 4 | 4 | 296.12 | 3577.2759
3352-Feedwater chemistry (not specific to condenser; polishers; or chemical addition) | 109 | 109 | 22730.27 | 865745.2104
3360-Condensate makeup and return (including storage tanks) | 23 | 23 | 4321.5 | 94988.148
3370-Condensate system controls and instrumentation (not hotwell level; heater level; or deaerator level controls: see codes 3150-3159; 3344; 3502. | 16 | 16 | 2463.9 | 33436.733
3380-Condensate coolers | 1 | 1 | 50 | 433.3333
3399-Other miscellaneous condensate system problems | 145 | 145 | 15666.36 | 144265.2802
3401-Startup feedwater pump | 20 | 20 | 9936.1 | 1524333.7677
3402-Startup feedwater pump drives - all types | 3 | 3 | 1759 | 89453.2498
3407-Feedwater pump suction screens | 7 | 7 | 1128 | 16001.2995
3408-Feedwater pump drive - local controls | 14 | 14 | 4036.7 | 37344.3321
3409-Feedwater pump drive motor - variable speed | 9 | 9 | 1035.4 | 120704.7621
3410-Feedwater pump | 426 | 426 | 69363.96 | 4822253.4007
3411-Feedwater pump drive - motor | 84 | 84 | 11072.64 | 1119140.5521
3412-Feedwater pump drive - steam turbine | 139 | 139 | 39921.76 | 1845725.0131
3413-Feedwater pump coupling and drive shaft | 23 | 23 | 4974.95 | 483043.8093
3414-Feedwater pump local controls | 39 | 39 | 9843 | 220672.8
3415-Feedwater pump/drive lube oil system | 81 | 81 | 20985.52 | 488539.3759
3416-Other feedwater pump problems | 130 | 130 | 29474.28 | 956555.1855
3417-Feedwater pump drive - main shaft | 4 | 4 | 894.2 | 235960.4997
3418-Feedwater pump drive - other | 10 | 10 | 2219.3 | 343276.6679
3420-Feedwater piping and supports | 24 | 24 | 7840.9 | 325447.0508
3430-Feedwater regulating (boiler level control) valve | 168 | 168 | 33953.68 | 1064835.0352
3431-Other feedwater valves | 118 | 118 | 35532.26 | 1418022.3925
3439-HP heater head leaks | 22 | 22 | 2696.77 | 219173.3784
3440-High pressure heater tube leaks | 166 | 166 | 12309.28 | 842122.9186
3441-Other high pressure heater problems (see condensate system for LP and IP heater codes) | 36 | 36 | 3696.64 | 340439.4213
3454-Feedwater Booster Pump | 4 | 4 | 1256 | 32556.3998
3455-Feedwater Booster Pump Drive - Motor | 6 | 6 | 421.63 | 158070.2432
3458-Feedwater Booster Pump Local Controls | 2 | 2 | 930 | 10020.75
3459-Feedwater Booster Pump/Drive Lube Oil System | 6 | 6 | 1938.7 | 13456.5059
3460-Other Feedwater Booster Pump Problems | 5 | 5 | 426 | 23215.9998
3499-Other feedwater system problems | 91 | 91 | 15059.91 | 936471.3766
3501-Heater drain pumps | 45 | 45 | 9178.18 | 742108.0773
3502-Heater level control | 45 | 45 | 6317.66 | 230987.4295
3503-Heater drain piping | 6 | 6 | 566.45 | 23095.3373
3504-Heater drain valves | 18 | 18 | 2200.15 | 88340.1764
3505-Heater drain pump drive | 3 | 3 | 202 | 86066.6666
3509-Other heater drain system problems | 12 | 12 | 1797.03 | 18779.2865
3520-HP Extraction steam piping | 5 | 5 | 1548.55 | 53691.6473
3521-HP Extraction steam valves | 21 | 21 | 3535.2 | 102197.6287
3522-HP Extraction steam instruments and controls | 2 | 2 | 373.7 | 1611.6881
3529-Other HP extraction steam system problems | 11 | 11 | 2239.8 | 1130567.8761
3531-IP Extraction steam valves | 14 | 14 | 2760.6 | 318586.5724
3532-IP Extraction steam instruments and controls | 1 | 1 | 242 | 1201.9332
3539-Other IP extraction steam system problems | 4 | 4 | 552 | 8805.1998
3540-LP Extraction steam piping | 4 | 4 | 301.8 | 100456.55
3541-LP Extraction steam valves | 3 | 3 | 209.84 | 127.568
3549-Other LP extraction steam system problems | 9 | 9 | 1393.29 | 16875.0855
3600-Switchyard transformers and associated cooling systems - external | 48 | 48 | 6431.18 | 338897.8607
3601-Switchyard transformers and associated cooling systems ? (not outside management control) | 18 | 18 | 1633.2 | 257622.9029
3610-Switchyard circuit breakers - (not outside management control) | 48 | 48 | 9368.99 | 453140.1776
3611-Switchyard circuit breakers - external | 91 | 91 | 18107.92 | 635743.2282
3612-Switchyard system protection devices - external | 102 | 102 | 17591.17 | 241113.5318
3613-Switchyard system protection devices - (not outside management control) | 25 | 25 | 4744.3 | 34233.0997
3618-Other switchyard equipment ? (not outside management control) | 9 | 9 | 1602.7 | 264899.2565
3619-Other switchyard equipment - external | 96 | 96 | 16716.77 | 876351.9441
3620-Main transformer | 412 | 412 | 57346.92 | 13401109.4513
3621-Unit auxiliaries transformer | 115 | 115 | 24789.01 | 1152632.5612
3622-Station service startup transformer | 20 | 20 | 4680.08 | 417863.2344
3623-Auxiliary generators | 5 | 5 | 693.16 | 28046.7458
3624-Generator Voltage Supply System | 6 | 6 | 776.32 | 10154.9044
3629-Other switchyard or high voltage system problems - external | 84 | 84 | 9974.2 | 844520.0091
3630-480-volt transformers | 11 | 11 | 2702.92 | 17379.3927
3631-480-volt circuit breakers | 69 | 69 | 9449.3 | 299220.02
3632-480-volt conductors and buses | 22 | 22 | 4983.45 | 695113.6168
3634-480-volt protection devices | 11 | 11 | 2603.4 | 23531.8959
3639-Other 480-volt problems | 16 | 16 | 2649.1 | 87389.2827
3640-AC instrument power transformers | 4 | 4 | 212.19 | 11392.6056
3641-AC Circuit breakers | 82 | 82 | 11034.65 | 275475.1469
3642-AC Conductors and buses | 13 | 13 | 1093.29 | 61178.262
3643-AC Inverters | 18 | 18 | 2906.04 | 34476.4368
3644-AC Protection devices | 82 | 82 | 7820.23 | 123393.9284
3649-Other AC instrument power problems | 24 | 24 | 4214.13 | 39829.6113
3650-DC instrument power battery chargers | 17 | 17 | 1180.88 | 55244.8565
3651-DC circuit breakers | 10 | 10 | 964.45 | 22942.3136
3652-DC conductors and buses | 7 | 7 | 542.2 | 4435.2015
3653-DC protection devices | 20 | 20 | 1111.64 | 138260.7583
3659-Other DC power problems | 45 | 45 | 3997.62 | 78012.793
3660-4160-volt transformers | 27 | 27 | 5871.59 | 240610.6452
3661-4160-volt circuit breakers | 87 | 87 | 17418.12 | 317343.2506
3662-4160-volt conductors and buses | 20 | 20 | 10045.5 | 288652.172
3664-4160-volt protection devices | 29 | 29 | 8746.5 | 98919.2399
3669-Other 4160-volt problems | 14 | 14 | 2265.15 | 78894.7261
3670-12kV transformers | 23 | 23 | 4401.3 | 62666.2605
3671-12kV circuit breakers | 45 | 45 | 3847.38 | 369893.7821
3672-12kV conductors and buses | 28 | 28 | 4632.18 | 529860.3249
3673-12kV insulators | 3 | 3 | 657.55 | 54427.0222
3674-12kV protection devices | 22 | 22 | 2274.18 | 96836.1245
3679-Other 12kV problems | 9 | 9 | 632.74 | 54497.2979
3680-Other voltage system transformers | 23 | 23 | 6108.56 | 1227036.7748
3681-Other voltage system breakers | 27 | 27 | 4953.86 | 423050.5809
3682-Other voltage system conductors and buses | 26 | 26 | 4053.73 | 798785.734
3683-Other voltage system insulators | 17 | 17 | 2888.24 | 70697.5224
3684-Other voltage system protection devices | 31 | 31 | 3650.21 | 93807.2082
3689-Other Other voltage system problems | 37 | 37 | 4920.61 | 315563.5211
3690-Station Service Power Distribution System; General | 52 | 52 | 8415.99 | 840553.6862
3700-Power Station switchyard (non generating unit equipment) | 62 | 62 | 8100.6 | 917425.8349
3710-Transmission line (connected to powerhouse switchyard to 1st Substation) | 95 | 95 | 6766.95 | 608726.9587
3720-Transmission equipment at the 1st substation) | 22 | 22 | 3474.32 | 131723.2073
3730-Transmission equipment beyond the 1st substation | 69 | 69 | 5910.25 | 673828.6877
3800-Open cooling water pumps and motors | 5 | 5 | 298 | 25728.5499
3801-Open cooling water piping | 2 | 2 | 111.9 | 10715.565
3805-Open cooling water system instrumentation | 5 | 5 | 244.2 | 105.0982
3809-Other open cooling water problems | 5 | 5 | 784.1 | 4662.1829
3810-Service water pumps and motors | 15 | 15 | 1156.35 | 18807.4074
3811-Service water piping | 22 | 22 | 2465.1 | 87414.4793
3812-Service water valves | 6 | 6 | 576.85 | 35252.6353
3813-Service water heat exchangers | 1 | 1 | 40.25 | 16313.9958
3814-Service water system fouling | 6 | 6 | 728.2 | 5093.36
3819-Other service water problems A | 21 | 21 | 4970.56 | 200115.1199
3820-Closed cooling water pumps | 30 | 30 | 4057.75 | 192571.6277
3821-Closed cooling water piping | 19 | 19 | 4830.42 | 117294.462
3822-Closed cooling water valves | 5 | 5 | 1166.5 | 1865.516
3823-Closed cooling water heat exchangers | 39 | 39 | 2382.89 | 53084.7438
3824-Closed cooling water system fouling | 10 | 10 | 332.92 | 3870.9999
3829-Other closed cooling water system problems A | 42 | 42 | 3483.41 | 156453.6891
3830-Auxiliary boiler | 22 | 22 | 7873.72 | 130003.1033
3831-Auxiliary steam piping | 3 | 3 | 795 | 11557.833
3832-Auxiliary steam valves | 15 | 15 | 4327.72 | 79653.2646
3833-Auxiliary steam controls and instruments | 21 | 21 | 4030.1 | 25055.8411
3834-Auxiliary boiler tube leaks | 15 | 15 | 4113.5 | 165782.9491
3835-Auxiliary boiler burner management system | 3 | 3 | 1412 | 3210.9324
3836-Steam Transfer to Other Unit | 88 | 88 | 9215.4 | 138533.3254
3839-Other auxiliary steam problems (also see extraction steam codes 3520 to 3529; startup bypass codes 0630 to 0660; and soot blower steam code 0870) | 22 | 22 | 6141.25 | 126021.4339
3840-Service air compressors | 19 | 19 | 3337.7 | 32379.5741
3841-Service air piping | 3 | 3 | 104 | 61.0333
3843-Service air dryers | 1 | 1 | 198 | 214.4999
3844-Soot blowing air compressor and system | 2 | 2 | 81 | 1195.35
3849-Other service air problems | 13 | 13 | 977.58 | 4917.6927
3850-Instrument air compressors | 64 | 64 | 15344.27 | 90994.8969
3851-Instrument air piping | 18 | 18 | 3801.7 | 141302.8153
3852-Instrument air valves | 15 | 15 | 1935.46 | 4703.1292
3853-Instrument air dryers | 8 | 8 | 1497.4 | 30347.8363
3859-Other instrument air problems | 11 | 11 | 1787.54 | 4704.0131
3861-Fire protection system piping | 4 | 4 | 1204 | 28869.6992
3862-Fire protection system valves | 4 | 4 | 493.51 | 36574.2057
3864-Fire protection system instrumentation and controls | 69 | 69 | 7397.1 | 149108.5339
3869-Other fire protection system problems | 57 | 57 | 6110.41 | 282274.035
3870-Fuel Gas Compressor and Motors | 72 | 72 | 6853.64 | 40070.4619
3871-Fuel Gas Compressor Piping | 3 | 3 | 496 | 4429.6
3872-Fuel Gas Compressor Valves | 44 | 44 | 5705.13 | 34274.3334
3873-Fuel Gas Compressor Heat Exchangers | 12 | 12 | 1015.5 | 24393.6498
3874-Fuel Gas Compressor Controls and Instrumentation | 61 | 61 | 6289.21 | 27510.1199
3875-Fuel Gas Compressor Filters | 8 | 8 | 922.8 | 8588.1547
3876-Fuel Gas Compressor Fire System | 1 | 1 | 81 | 301.0499
3879-Fuel Gas Compressor - other | 55 | 55 | 5654.34 | 202199.7386
3880-Seal air fan | 3 | 3 | 342 | 4237.5
3898-Miscellaneous plant auxiliary process and services instrumentation and controls | 73 | 73 | 10515.39 | 549672.0125
3899-Other miscellaneous auxiliary system problems | 129 | 129 | 11921.47 | 376232.3051
3950-Process computer | 30 | 30 | 3836.44 | 34450.5995
3960-Thermal derating (thermal efficiency losses in balance of plant when specific cause(s) unknown) | 176 | 176 | 3162.7 | 296029.1647
3970-Distributive Control System (DCS) - process computer | 82 | 82 | 8911.85 | 108689.467
3971-DCS - data highway | 25 | 25 | 3673.15 | 13845.4785
3972-DCS - hardware problems (including card failure) | 108 | 108 | 19234.59 | 248030.1925
3973-DCS - internal and termination wiring | 11 | 11 | 1867.4 | 21587.0528
3974-DCS - logic problems | 45 | 45 | 7840.15 | 81731.4559
3975-DCS - upgrades | 29 | 29 | 2905.13 | 40357.9852
3979-Other DCS problems | 57 | 57 | 7593.91 | 79250.4779
3980-Programmable Logic Controller (PLC) | 29 | 29 | 1901.78 | 19075.6265
3981-PLC - data highway | 5 | 5 | 509.9 | 1705.9166
3982-PLC - hardware problems (including card failure) | 39 | 39 | 3892.24 | 155537.3264
3983-PLC - internal and termination wiring | 2 | 2 | 164.89 | 204.0563
3984-PLC - logic problems | 13 | 13 | 2992.54 | 8307.6486
3985-PLC - upgrades | 9 | 9 | 475.7 | 8854.0032
3989-Other PLC problems | 21 | 21 | 1202.14 | 12506.1259
3995-Powerhouse heating and ventilating systems | 12 | 12 | 438.51 | 2359.4506
3996-Air conditioning systems - rooms and areas | 19 | 19 | 1712.44 | 9459.0212
3998-Balance of plant overhaul/outage | 26 | 26 | 1510.54 | 319419.6321
3999-Other miscellaneous balance of plant problems | 533 | 533 | 62285.6 | 7658400.1975
4000-Outer casing A | 2 | 2 | 786 | 11808.3662
4001-Inner casing C | 11 | 11 | 590.15 | 232294.425
4010-Nozzles and nozzle blocks C | 4 | 4 | 214.84 | 154984.61
4012-Buckets or blades A | 5 | 5 | 635.7 | 407954.7929
4020-Shaft seals B | 4 | 4 | 1852.1 | 422341.6193
4030-Rotor shaft C | 7 | 7 | 2422 | 479648.7326
4040-Bearings C | 148 | 148 | 35101.75 | 1051974.6199
4041-HP steam turbine thrust bearings | 21 | 21 | 1997.97 | 481083.6128
4099-Other high pressure turbine problems | 64 | 64 | 15223.94 | 8097098.5809
4100-Outer casing B | 1 | 1 | 280 | 172.6665
4112-Buckets or blades B | 7 | 7 | 1785 | 310904.4994
4130-Rotor shaft B | 4 | 4 | 2488.4 | 3332207.1045
4140-Bearings D | 16 | 16 | 4992.5 | 447243.565
4141-IP steam turbine thrust bearings | 3 | 3 | 270 | 5553
4199-Other intermediate pressure turbine problems | 15 | 15 | 3624 | 74345.9159
4211-Diaphragms C | 5 | 5 | 1935.6 | 67967.5763
4212-Buckets or blades C | 48 | 48 | 7357.66 | 3688001.6191
4220-Shaft seals D | 2 | 2 | 1145.1 | 634230.0714
4230-Rotor shaft A | 5 | 5 | 664 | 98355.9331
4240-Bearings E | 27 | 27 | 9396 | 535105.5045
4250-Other low pressure turbine problems | 40 | 40 | 7739.7 | 950017.6706
4260-Main stop valves | 98 | 98 | 22182.31 | 875787.4085
4261-Control valves | 330 | 330 | 74293.53 | 3475519.3855
4262-Intercept valves | 61 | 61 | 14002.41 | 350867.1648
4263-Reheat stop valves | 33 | 33 | 10528.93 | 1003084.3681
4264-Combined intercept valves | 9 | 9 | 2711.74 | 129038.9466
4265-Miscellaneous drain and vent valves | 44 | 44 | 10739.8 | 353038.8069
4266-Main stop valve testing | 7 | 7 | 1863.5 | 11590.7241
4267-Control valve testing | 27 | 27 | 4278.24 | 5453.5307
4268-Reheat/intercept valve testing | 12 | 12 | 1853.5 | 28073.5328
4269-Other turbine valves (including LP steam admission valves) | 77 | 77 | 12704.9 | 455406.6654
4270-Crossover or under piping | 12 | 12 | 6071.4 | 489404.5574
4279-Miscellaneous turbine piping | 22 | 22 | 9388.1 | 622743.9916
4280-Lube oil pumps A | 18 | 18 | 5845.72 | 231453.802
4281-Lube oil coolers A | 20 | 20 | 5140.5 | 688316.7063
4283-Lube oil system valves and piping | 23 | 23 | 7535.49 | 325352.4646
4284-Lube oil pump drive | 7 | 7 | 1534.75 | 614391.2749
4289-Other lube oil system problems | 55 | 55 | 11221.91 | 546908.5742
4290-Hydraulic system pumps | 49 | 49 | 13564.49 | 460216.6094
4291-Hydraulic system coolers | 3 | 3 | 952.6 | 49076.3496
4292-Hydraulic system filters | 4 | 4 | 1367.5 | 208529.1665
4293-Hydraulic system pipes and valves | 103 | 103 | 27491.66 | 922920.9367
4299-Other hydraulic system problems | 48 | 48 | 14169.75 | 450573.9458
4300-Turbine supervisory system (use codes 4290 to 4299 for hydraulic oil) | 25 | 25 | 4850.33 | 30504.9438
4301-Turbine governing system | 40 | 40 | 8767.83 | 417365.5368
4302-Turbine trip devices (including instruments) | 114 | 114 | 25862.33 | 511054.2907
4303-Exhaust hood and spray controls | 11 | 11 | 2513.72 | 6307.6583
4304-Automatic turbine control systems - mechanical | 14 | 14 | 1577.96 | 807492.5211
4305-Automatic turbine control systems - mechanical - hydraulic | 12 | 12 | 1620.63 | 20247.4005
4306-Automatic turbine control systems - electro-hydraulic - analog | 14 | 14 | 2767.85 | 63452.5096
4307-Automatic turbine control systems - electro-hydraulic - digital | 10 | 10 | 2872.7 | 100032.1162
4308-Automatic turbine control systems - digital control and monitoring | 46 | 46 | 9703.01 | 228123.6536
4309-Other turbine instrument and control problems | 107 | 107 | 22009.3 | 366242.2951
4310-Steam Turbine Control System - data highway | 7 | 7 | 805.48 | 9792.4298
4311-Steam Turbine Control System - hardware problems (including card failure) | 81 | 81 | 12315.42 | 355363.8195
4312-Steam Turbine Control System - internal and termination wiring | 10 | 10 | 1374.85 | 7992.327
4313-Steam Turbine Control System - logic problems | 51 | 51 | 8409.93 | 60227.4745
4314-Steam Turbine Control System - upgrades | 5 | 5 | 2510 | 25029.2494
4400-Major turbine overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 14 | 14 | 2962.64 | 233811.5221
4401-Inspection F | 8 | 8 | 1468.36 | 162276.9166
4402-Minor turbine overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 2 | 2 | 51.03 | 19167.074
4410-Turning gear and motor A | 47 | 47 | 10499.33 | 1065403.8738
4412-Steam turbine clutch (single shaft configuration) | 15 | 15 | 3654 | 2992.165
4420-Vibration of the turbine generator unit that cannot be attributed to a specific cause such as bearings or blades (use this code for balance moves) | 131 | 131 | 30838.79 | 1803715.5918
4430-Gland seal system | 38 | 38 | 7263.69 | 144157.1624
4440-Moisture separator/reheater (nuclear including MSR drains; controls; etc.) | 8 | 8 | 183 | 53938.8333
4450-Water induction | 8 | 8 | 1521.5 | 766622.7281
4460-Turbine overspeed trip test | 5 | 5 | 1062.5 | 50691.4313
4470-Differential expansion | 46 | 46 | 14039.14 | 104943.1224
4490-Turbine performance testing (use code 9999 for total unit performance testing) | 5 | 5 | 791.16 | 12145.2867
4499-Other miscellaneous steam turbine problems | 450 | 450 | 78290.85 | 2119172.9627
4500-Rotor windings (including damper windings and fan blades on hydro units) | 49 | 49 | 5661.69 | 1411528.8654
4510-Rotor collector rings | 27 | 27 | 5798.74 | 438914.8497
4511-Rotor; General | 76 | 76 | 6061.38 | 1792439.7428
4520-Stator windings; bushings; and terminals | 46 | 46 | 8468.49 | 4751692.5991
4530-Stator core iron | 6 | 6 | 921 | 518025.05
4535-Stator; General | 68 | 68 | 6179.51 | 3376514.2975
4540-Brushes and brush rigging | 46 | 46 | 11119.89 | 1127585.3966
4550-Generator bearings and lube oil system (including thrust bearings on hydro units) | 126 | 126 | 8956.77 | 1593126.2504
4551-Generator bearings | 67 | 67 | 9534.58 | 1473566.03
4552-Generator lube oil system | 98 | 98 | 7246.13 | 686512.9348
4555-Bearing cooling system A | 35 | 35 | 4249.95 | 804530.7099
4560-Generator vibration (excluding vibration due to failed bearing and other components) | 156 | 156 | 18157.76 | 2350776.5951
4570-Generator casing | 5 | 5 | 1849.1 | 416723.8879
4580-Generator end bells and bolting | 1 | 1 | 35.5 | 50.2916
4590-Generator brakes | 34 | 34 | 2402.4 | 40538.0503
4600-Exciter drive - motor | 9 | 9 | 1476.07 | 376934.8388
4601-Exciter field rheostat | 6 | 6 | 597.75 | 152757.3
4602-Exciter commutator and brushes | 36 | 36 | 9244.85 | 1262535.812
4603-Solid state exciter element | 25 | 25 | 5237.4 | 120816.5577
4604-Exciter drive - shaft | 1 | 1 | 40.25 | 4736.0833
4605-Exciter transformer | 21 | 21 | 4090.17 | 653416.2921
4609-Other exciter problems | 588 | 588 | 85135.99 | 4757179.0965
4610-Hydrogen cooling system piping and valves | 13 | 13 | 2778.5 | 123502.6439
4611-Hydrogen coolers | 38 | 38 | 3898.7 | 287060.9688
4612-Hydrogen storage system | 1 | 1 | 46 | 713
4613-Hydrogen seals | 7 | 7 | 2294.72 | 248136.2294
4619-Other hydrogen system problems | 111 | 111 | 10771.45 | 641690.932
4620-Air cooling system | 29 | 29 | 3035.86 | 336570.5388
4630-Liquid cooling system | 45 | 45 | 8524.22 | 182052.6882
4640-Seal oil system and seals A | 33 | 33 | 6204.28 | 633839.2281
4650-Other cooling system problems | 59 | 59 | 6559.66 | 216164.7374
4700-Generator voltage control | 146 | 146 | 18007.05 | 522936.842
4710-Generator metering devices | 42 | 42 | 5888.79 | 653029.2785
4720-Generator synchronization equipment | 199 | 199 | 20672.87 | 532487.2824
4730-Generator current and potential transformers | 69 | 69 | 12230.26 | 685536.4959
4740-Emergency generator trip devices | 172 | 172 | 21340.86 | 1195955.6285
4750-Other generator controls and metering problems | 247 | 247 | 28231.43 | 680866.915
4800-Generator main leads | 43 | 43 | 7597.53 | 1612893.6339
4805-Generator Bus Duct Cooling System | 8 | 8 | 2092.19 | 20741.9909
4810-Generator output breaker | 384 | 384 | 33609.47 | 3820608.9837
4830-Major overhaul (720 hrs or longer) (use for non-specific overhaul only; see page B-1) | 3 | 3 | 236 | 6490.6666
4831-Minor overhaul (less than 720 hrs.) (use for non-specific overhaul only; see page B-1) | 1 | 1 | 23.8 | 481.5533
4840-Inspection E | 31 | 31 | 1253.83 | 98483.8101
4842-Reactive and capability testing | 7 | 7 | 653.5 | 3357.6997
4860-Generator Neutral Grounding Equipment | 68 | 68 | 9927.44 | 321097.4125
4899-Other miscellaneous generator problems | 243 | 243 | 28198.57 | 8334882.8869
5000-Inlet air ducts A | 28 | 28 | 3274.99 | 247696.2158
5001-Inlet air vanes / nozzles | 187 | 187 | 24847.71 | 426299.4724
5002-Inlet air filters A | 107 | 107 | 6569.26 | 76984.5505
5003-Inlet cone | 1 | 1 | 2 | 1488
5004-Inlet air chillers B | 235 | 235 | 5155.25 | 139414.0401
5005-Inlet air evaporative coolers B | 35 | 35 | 1155.95 | 58991.5586
5006-Inlet air foggers B | 60 | 60 | 1697 | 41813.8409
5009-Other inlet air problems A | 56 | 56 | 5635.46 | 88429.3527
5010-High pressure shaft D | 1 | 1 | 126.7 | 16.8933
5011-High pressure bearings C | 3 | 3 | 273.5 | 52427.7165
5012-High pressure blades/buckets B | 25 | 25 | 2721.44 | 1963794.5934
5013-Compressor casing and bolts | 5 | 5 | 467.44 | 20865.9165
5014-Compressor diaphragms | 19 | 19 | 3436.6 | 320303.4376
5015-Compressor seals | 66 | 66 | 2989.19 | 29228.308
5016-High pressure compressor bleed valves | 195 | 195 | 24077.83 | 135125.6844
5017-Low pressure compressor bleed valves | 48 | 48 | 6985.05 | 44310.9711
5019-Other high pressure problems A | 22 | 22 | 2129.42 | 742790.5572
5021-Low pressure bearings D | 1 | 1 | 93 | 8184
5022-Low pressure blades/buckets A | 3 | 3 | 423 | 946034.45
5029-Other low pressure problems E | 9 | 9 | 1051.75 | 36558.8662
5035-Compressor Washing | 11 | 11 | 2089.39 | 20646.1993
5036-Compressor shaft & bearings two sft machines | 1 | 1 | 166 | 1203.5
5037-Inlet bleed heat valve | 85 | 85 | 10832.95 | 67657.1865
5039-Other compressor problems | 123 | 123 | 12785.75 | 3748075.4225
5040-Fuel tanks B | 3 | 3 | 306.2 | 2157.7833
5041-Fuel piping and valves A | 672 | 672 | 90282.39 | 2112391.8256
5042-Fuel nozzles/vanes B | 93 | 93 | 11693.68 | 1032207.3908
5043-Fuel filters A | 34 | 34 | 4218.91 | 110350.2865
5044-Liquid fuel oil pump A | 22 | 22 | 998.1 | 62057.1697
5046-Liquid fuel oil transfer/forwarding pump B | 13 | 13 | 1924.7 | 3025.6411
5047-Liquid fuel purge system A | 19 | 19 | 2902.9 | 10875.3325
5048-Gas fuel system B | 629 | 629 | 74849.42 | 1117368.2976
5049-Other fuel system problems B | 263 | 263 | 32792.03 | 623706.3318
5050-Ignition system A | 345 | 345 | 49341.99 | 483475.5821
5051-Pilot fuel piping and valves A | 64 | 64 | 8428.47 | 78608.3142
5052-Pilot fuel nozzles/vanes B | 14 | 14 | 2281.2 | 81346.9025
5053-Pilot fuel filters A | 4 | 4 | 961.4 | 28559.4097
5054-Water Injection System (Gas Turbine) | 164 | 164 | 12270.14 | 87920.511
5060-Atomizing air system B | 52 | 52 | 6288.12 | 499513.5692
5065-NOx water injection system including pumps | 93 | 93 | 7965.32 | 139855.1323
5066-NOx Steam Injection System | 32 | 32 | 2251.74 | 284026.7073
5070-Combustor casing A | 50 | 50 | 5323.88 | 472486.1894
5071-Combustor liner B | 8 | 8 | 771.3 | 206230.7115
5072-Combustor caps B | 2 | 2 | 61.6 | 11492.6667
5073-Flame scanners B | 177 | 177 | 16036.55 | 230400.1349
5074-Flashback including instruments | 83 | 83 | 11159.1 | 337867.0073
5075-Blade Path Temperature Spread A | 317 | 317 | 47796.65 | 653765.1955
5079-Other combustor problems B | 285 | 285 | 38481.09 | 1379158.0895
5080-High pressure shaft C | 9 | 9 | 847.64 | 74539.6163
5081-High pressure bearings D | 22 | 22 | 2394.65 | 92337.85
5082-High pressure blades/buckets A | 19 | 19 | 2749.3 | 3648459.5523
5083-High pressure nozzles/vanes A | 17 | 17 | 1901.3 | 701299.0708
5084-High pressure casing/expansion joints | 8 | 8 | 759.31 | 44275.8628
5085-Interstage gas passages - HP | 2 | 2 | 341 | 1022.6331
5086-High pressure shaft seals A | 6 | 6 | 352.5 | 68476.0999
5087-Thrust Bearing | 13 | 13 | 1871.7 | 38316.4996
5088-Gas turbine cooling steam | 63 | 63 | 11379.4 | 544081.7617
5089-Other high pressure problems B | 19 | 19 | 1864.19 | 59107.5493
5090-Low pressure shaft A | 4 | 4 | 219.2 | 56643.1166
5091-Low pressure bearings A | 8 | 8 | 662.49 | 16227.6005
5092-Low pressure blades/buckets D | 10 | 10 | 826.08 | 919279.6723
5093-Low pressure nozzles/vanes B | 5 | 5 | 180.85 | 132343.3766
5095-Interstage gas passages ? LP | 4 | 4 | 659.2 | 928.7948
5097-Other low pressure problems B | 4 | 4 | 240.5 | 6153.4166
5098-Expansion joints A | 8 | 8 | 1287.54 | 367472.0304
5099-HP to LP coupling | 1 | 1 | 56 | 71.8666
5100-Chamber A | 5 | 5 | 604.4 | 13444.4765
5102-Vanes/nozzles A | 5 | 5 | 759.41 | 7121.5656
5103-Silencer B | 1 | 1 | 185 | 7350.6666
5105-Diverter Dampers B | 27 | 27 | 2700.7 | 782154.3725
5106-Exhaust Stack | 9 | 9 | 948.6 | 563901.5331
5108-High engine exhaust temperature A | 132 | 132 | 15171.07 | 454213.66
5109-Other exhaust problems (including high exhaust system temperature not attributable to a specific problem) | 216 | 216 | 24369.44 | 383441.767
5110-Lube oil system - general | 229 | 229 | 16590.91 | 923069.8105
5111-Lube oil pumps B | 87 | 87 | 8682.15 | 338365.6384
5112-Lube oil coolers B | 44 | 44 | 3877.72 | 230680.9772
5113-Lube oil valves/piping | 27 | 27 | 2951.76 | 45217.9652
5114-Lube oil filters | 27 | 27 | 1724.6 | 13019.336
5115-Oil vapor extractor | 16 | 16 | 1328.9 | 36341.0196
5116-Power Augmentation System Equipment B | 31 | 31 | 2768.82 | 31218.617
5117-Power augmentation piping | 5 | 5 | 115 | 19970.8666
5118-Power augmentation valves | 4 | 4 | 389 | 11637.1
5119-Power augmentation controls | 24 | 24 | 1849.15 | 10541.2074
5120-Hydraulic oil system A | 119 | 119 | 13711.92 | 235773.8357
5121-Hydraulic oil system pumps | 27 | 27 | 3202.54 | 39010.4438
5122-Hydraulic oil system piping/valves | 39 | 39 | 4632.46 | 90856.097
5130-Starting system (including motor) A | 233 | 233 | 30448.02 | 791342.425
5140-Battery and charger system B | 14 | 14 | 883.95 | 18012.2829
5150-Turning gear and motor C | 67 | 67 | 7611.18 | 490873.9468
5151-Load gear compartment B | 3 | 3 | 371 | 903.0165
5160-Cooling and seal air system B | 135 | 135 | 20887.21 | 672300.933
5170-Cooling water system A | 40 | 40 | 3833.34 | 16313.9813
5180-Anti-icing system A | 38 | 38 | 5825.25 | 17156.0287
5190-Other auxiliary system problems A | 129 | 129 | 15503.27 | 313744.7745
5200-Reduction gear B | 3 | 3 | 223.1 | 87258.1882
5201-Load shaft and bearings A | 9 | 9 | 1489.29 | 126579.718
5205-Main coupling between the turbine and generator A | 7 | 7 | 642.6 | 69192.4764
5206-Gas Turbine Clutch | 4 | 4 | 397.1 | 81254.6832
5210-Intercoolers A | 11 | 11 | 1414.81 | 78006.8433
5240-Fire detection and extinguishing system B | 229 | 229 | 31806.48 | 589517.3504
5241-Fire in unit A | 27 | 27 | 2484.6 | 1526210.7228
5245-Gas Turbine Control System - data highway | 32 | 32 | 3773.64 | 33538.0813
5246-Gas Turbine Control System - hardware problems (including card failure) | 211 | 211 | 29876.21 | 337625.734
5247-Gas Turbine Control System - internal and termination wiring | 39 | 39 | 3634.7 | 86463.7704
5248-Gas Turbine Control System - logic problems | 64 | 64 | 9184.6 | 86685.4782
5249-Gas Turbine Control System - upgrades | 9 | 9 | 1714.5 | 305506.9166
5250-Other Controls and instrumentation Problems A | 567 | 567 | 63553.32 | 1266079.9186
5255-Computer | 11 | 11 | 811.6 | 32158.0414
5260-Major overhaul (use for non-specific overhaul only; see page B-1) A | 26 | 26 | 3090.6 | 1126115.969
5261-Gas turbine/compressor washing | 29 | 29 | 2821.38 | 106118.7881
5262-Gas turbine exchange | 3 | 3 | 136.4 | 60894.0899
5269-Combustion inspection (CI) | 1 | 1 | 47.26 | 42068.489
5270-Hot end inspection B | 15 | 15 | 2317.55 | 238702.2244
5272-Boroscope inspection A | 29 | 29 | 3318.2 | 259018.509
5274-General unit inspection A | 17 | 17 | 912.61 | 92562.9197
5280-Vibration (not engine) in unit not attributable to bearings or other components B | 58 | 58 | 4740.56 | 331290.9975
5285-Gas turbine vibration | 246 | 246 | 23771.1 | 2593877.934
5286-Gas Turbine lockout cause by OEM specifications | 9 | 9 | 537.68 | 5736.6865
5290-Gas turbine performance testing - individual engines (use code 9999 for total unit performance testing) | 73 | 73 | 2760.39 | 350248.0362
5295-Synchronous condenser equipment A | 2 | 2 | 132 | 103.6333
5299-Other miscellaneous gas turbine problems | 903 | 903 | 82627.95 | 3970097.6381
5400-Inlet air ducts B | 3 | 3 | 101 | 177.9083
5401-Inlet air vanes/noozles | 18 | 18 | 1446.89 | 19235.9948
5402-Inlet air filters B | 19 | 19 | 491.17 | 780.1765
5404-Inlet air chillers A | 11 | 11 | 91 | 23321.75
5405-Inlet air evaporative coolers A | 5 | 5 | 120.4 | 194.0333
5406-Inlet air foggers A | 1 | 1 | 2 | 5.8333
5409-Other inlet air problems B | 15 | 15 | 818.7 | 46815.2563
5410-High pressure shaft B | 3 | 3 | 195.69 | 161189.1355
5412-High pressure blades/buckets C | 12 | 12 | 746.6 | 560147.7164
5413-Other high pressure problems D | 12 | 12 | 683.1 | 3654.6498
5414-Compressor diaphragms/vanes | 6 | 6 | 270.1 | 2580.4299
5420-Low pressure shaft C | 1 | 1 | 42 | 84
5422-Low pressure blades/buckets C | 2 | 2 | 86 | 20846.6666
5429-Other low pressure problems D | 9 | 9 | 498.75 | 42349.1482
5435-Jet Engine Compressor Washing | 1 | 1 | 42.8 | 144.0933
5439-Jet engine other compressor problems | 48 | 48 | 2148.25 | 106407.7508
5441-Fuel piping and valves B | 85 | 85 | 4707.29 | 86693.1705
5442-Fuel nozzles/vanes A | 2 | 2 | 115.3 | 58897.03
5443-Fuel filters B | 2 | 2 | 95.8 | 745.05
5444-Liquid fuel oil pump B | 3 | 3 | 99.2 | 1381.8433
5445-Liquid fuel oil transfer/forwarding pump A | 4 | 4 | 399 | 158.3498
5446-Liquid fuel purge system B | 13 | 13 | 758.3 | 3782.3398
5447-Gas fuel system A | 115 | 115 | 6124.53 | 47212.2787
5449-Other fuel system problems A | 65 | 65 | 3064.28 | 63346.5473
5450-Ignition system B | 39 | 39 | 1606.15 | 37686.1002
5451-Pilot fuel piping and valves B | 3 | 3 | 419.4 | 651.4366
5454-Water injection system (Jet Engine) | 56 | 56 | 2694.31 | 26931.2576
5455-Fuel nozzle/vane cooling air system | 9 | 9 | 370 | 118497.0165
5460-Atomizing air system A | 1 | 1 | 17 | 36.8333
5471-Combustor liner A | 3 | 3 | 145.16 | 68839.6619
5473-Flame scanners A | 15 | 15 | 711.24 | 5317.8511
5475-Blade Path Temperature Spread B | 88 | 88 | 12309.59 | 63100.047
5479-Other combustor problems A | 52 | 52 | 3689.4 | 76001.2928
5480-High pressure shaft A | 3 | 3 | 76.3 | 119057.315
5481-High pressure bearings A | 10 | 10 | 692.73 | 185432.1858
5482-High pressure blades/buckets D | 3 | 3 | 90 | 143612.1166
5483-High pressure nozzles/vanes B | 6 | 6 | 326 | 130921.0166
5487-Thrust Bearing/jet | 2 | 2 | 87 | 4086.4833
5489-Other high pressure problems C | 15 | 15 | 749.83 | 101856.0261
5490-Low pressure shaft B | 7 | 7 | 326.7 | 698.3717
5491-Low pressure bearings C | 2 | 2 | 87 | 104703.3999
5492-Low pressure blades/buckets B | 1 | 1 | 1 | 2105.4333
5493-Low pressure nozzles/vanes A | 1 | 1 | 35 | 7756.5833
5497-Other low pressure problems C | 23 | 23 | 891.6 | 43862.4722
5505-Diverter Dampers A | 1 | 1 | 78.2 | 11.73
5508-High engine exhaust temperature B | 28 | 28 | 1532 | 7976.1161
5509-Other exhaust problems (including high exhaust temperature not attributable to a specific problem) | 22 | 22 | 1468.5 | 35192.198
5510-Lube oil system A | 184 | 184 | 9165.16 | 990084.7034
5516-Power Augmentation System Equipment A | 12 | 12 | 209.15 | 2194.4824
5520-Hydraulic oil system B | 36 | 36 | 2046.2 | 490223.4828
5530-Starting system (including motor) B | 49 | 49 | 2374.72 | 74444.8937
5540-Battery and charger system A | 7 | 7 | 287.25 | 3052.6424
5550-Turning gear and motor B | 7 | 7 | 546.6 | 91711.3698
5551-Load gear compartment A | 4 | 4 | 133.43 | 12449.6885
5560-Cooling and seal air system A | 32 | 32 | 1543.9 | 15666.7864
5570-Cooling water system B | 14 | 14 | 548.3 | 9986.4699
5580-Anti-icing system B | 27 | 27 | 1278.6 | 23102.1496
5590-Other auxiliary system problems B | 76 | 76 | 3062.6 | 48827.939
5601-Load shaft and bearings B | 1 | 1 | 253.55 | 2273.4982
5605-Main coupling between the turbine and generator B | 2 | 2 | 63 | 6512.8333
5606-Jet Engine Clutch | 2 | 2 | 44 | 34381.65
5610-Intercoolers B | 2 | 2 | 66.8 | 188.0533
5640-Fire detection and extinguishing system A | 41 | 41 | 3282.79 | 43423.6358
5645-Jet Engine Control System - data highway | 8 | 8 | 374.05 | 2582.0832
5646-Jet Engine Control System - hardware problems (including card failure) | 52 | 52 | 2185.87 | 15869.7341
5647-Jet Engine Control System - internal and termination wiring | 6 | 6 | 262.12 | 3069.6033
5648-Jet Engine Control System - logic problems | 10 | 10 | 390.7 | 975.4232
5649-Jet Engine Control System - upgrades | 2 | 2 | 94 | 698.7333
5650-Other Controls and instrumentation Problems B | 162 | 162 | 8355.19 | 99333.6791
5660-Major overhaul (use for non-specific overhaul only; see page B-1) C | 6 | 6 | 260 | 42296.6999
5661-Engine/compressor washing | 2 | 2 | 83.3 | 346.3833
5662-Engine exchange | 1 | 1 | 38 | 9.5
5665-Engine shafts and bearings | 18 | 18 | 579.4 | 523565.2015
5672-Boroscope inspection B | 3 | 3 | 244.35 | 2151.7624
5674-General unit inspection B | 4 | 4 | 119.3 | 46642.5333
5680-Vibration (not engine) in unit not attributable to bearings or other components A | 25 | 25 | 1141.5 | 25240.6497
5685-Engine vibration | 70 | 70 | 3374.09 | 1888930.3895
5686-Jet Engine lockout cause by OEM specifications | 5 | 5 | 151.7 | 87163.6783
5690-Engine performance testing - individual engines (use code 9999 for total unit performance testing) A | 2 | 2 | 77.8 | 15.9633
5699-Other miscellaneous jet engine problems | 83 | 83 | 3281.38 | 225535.4039
5710-Cylinders | 11 | 11 | 109.04 | 11094.5253
5711-Cylinder heads | 26 | 26 | 403.44 | 18373.2313
5730-Intake valves | 7 | 7 | 135 | 6276.25
5731-Exhaust valves | 13 | 13 | 392.07 | 2691.2584
5734-exhaust gas bellow | 16 | 16 | 254.5 | 9195.45
5735-main starting air valve | 1 | 1 | 9.1 | 218.4
5740-Turbo charger | 8 | 8 | 125.08 | 19294.676
5759-waste gate | 6 | 6 | 98.12 | 1628.4433
5799-Other engine problems | 238 | 238 | 6687.59 | 34553.2446
5800-Lube oil system C | 24 | 24 | 580.94 | 5485.072
5805-Cooling system | 62 | 62 | 1487.6 | 27304.3309
5815-Fuel system | 22 | 22 | 376.27 | 7008.6264
5820-Start system | 39 | 39 | 1131.65 | 645.8384
5831-Exhaust gas rapture disc | 9 | 9 | 160.5 | 489.1
5849-Other engine auxiliaries problems | 29 | 29 | 910.05 | 1937.0515
5855-Engine control system | 23 | 23 | 620.52 | 5218.0659
5865-Synchronization system | 3 | 3 | 71.28 | 20.196
5870-Other engine control problems | 26 | 26 | 698.39 | 4258.5429
5873-Gas admission valve | 18 | 18 | 333.5 | 811.7666
5874-Exhaust gas temp sensor | 1 | 1 | 9.1 | 3185
5895-Inspection C | 4 | 4 | 50.5 | 4027.3833
5999-other miscellaneous Internal Combustion/Reciprocating Engines problems | 45 | 45 | 1174.4 | 18163.4671
6000-Heat recovery steam generator to gas turbine connecting equipment. For additional codes; use Fossil Steam Cause Codes 0010 to 1999. | 40 | 40 | 3673.28 | 114792.863
6005-HP Evaporator tubes | 15 | 15 | 2955.5 | 387241.7777
6006-IP Evaporator tubes | 3 | 3 | 467 | 22728.7833
6007-LP Evaporator tubes | 2 | 2 | 324 | 11883.7499
6010-HP superheater | 41 | 41 | 5534.43 | 391986.8004
6011-HP reheater | 11 | 11 | 1772.1 | 115930.9528
6012-HP economizer | 45 | 45 | 5571.08 | 479702.9445
6021-IP reheater | 27 | 27 | 5490.7 | 453871.8041
6022-IP economizer | 4 | 4 | 650.7 | 52202.1998
6032-LP economizer | 14 | 14 | 1798 | 95522.8661
6090-Other HRSG tube Problems | 50 | 50 | 4928.06 | 956922.9052
6110-HP steam piping up to turbine stop valves - Greater than 600 PSIG; (see 0790 for piping supports) | 7 | 7 | 1470.45 | 12314.2047
6111-HP steam relief/safety valves | 4 | 4 | 542.3 | 43478.7547
6112-Other HP steam valves (including vent and drain valves but not including the turbine stop valves) | 35 | 35 | 5637.5 | 54368.2062
6113-Other HP steam system problems | 21 | 21 | 4736.24 | 26556.2092
6114-HP steam isolation/boundary valves | 31 | 31 | 6052 | 209819.064
6121-IP steam relief/safety valves | 6 | 6 | 1335.98 | 21399.686
6122-Other IP steam valves (including vent and drain valves but not including the turbine stop valves) | 12 | 12 | 2658.2 | 17008.5472
6123-Other IP steam system problems | 3 | 3 | 541 | 12127.9163
6124-IP steam isolation/boundary valves | 4 | 4 | 247.5 | 3984.1998
6131-LP steam relief/safety valves | 10 | 10 | 1389.09 | 13882.1818
6132-Other LP steam valves (including vent and drain valves but not including the turbine stop valves) | 3 | 3 | 546 | 19594.5664
6133-Other LP steam system problems | 4 | 4 | 464.5 | 7868.5664
6134-Other main steam valves (including vent and drain valves but not including the turbine stop valves) B | 4 | 4 | 601 | 601.9333
6140-HP Desuperheater/attemperator piping - Greater than 600 PSIG. | 6 | 6 | 733.48 | 31162.3225
6141-HP Desuperheater/attemperator valves | 32 | 32 | 5092.78 | 32378.5497
6142-HP Desuperheater/attemperator spray nozzles | 11 | 11 | 1650.73 | 44783.3368
6144-Other HP desuperheater/attemperator problems | 8 | 8 | 1578.25 | 39897.5492
6145-IP Desuperheater/attemperator piping - Between 200-600 PSIG | 4 | 4 | 561 | 35931.1998
6146-IP Desuperheater/attemperator valves | 17 | 17 | 3042.8 | 23525.4858
6147-IP Desuperheater/attemperator spray nozzles | 4 | 4 | 549 | 18347.025
6148-IP Desuperheater/attemperator drums | 1 | 1 | 147 | 112.6999
6149-Other IP desuperheater/attemperator problems | 2 | 2 | 51.5 | 1220.55
6160-HP Startup bypass system piping (including drain lines up to heaters or condenser)- Greater than 600 PSIG | 11 | 11 | 2756 | 30370.7488
6161-HP Startup bypass system valves | 52 | 52 | 10933.46 | 257941.5912
6163-Other HP startup bypass system problems | 16 | 16 | 3758.97 | 19501.7931
6164-HP Startup bypass instrumentation and controls | 17 | 17 | 3362.6 | 41145.669
6171-IP Startup bypass system valves | 45 | 45 | 9533.15 | 128413.2726
6173-Other IP startup bypass system problems | 7 | 7 | 1632.78 | 6176.3975
6174-IP Startup bypass instrumentation and controls | 6 | 6 | 903 | 10527.2661
6181-LP Startup bypass system valves | 1 | 1 | 259 | 811.5332
6200-Combined cycle instruments and controls. (Report instruments and controls specific to the gas turbine; steam turbine; boiler; generator; or balance of plant using the codes for the appropriate piece of equipment. | 52 | 52 | 8865.65 | 87479.2586
6299-Other combined cycle problems. (Use other gas turbine problem codes; other steam turbine codes; etc. whenever appropriate.) | 12 | 12 | 1573.6 | 396021.911
6399-Other coal gasification equipment problems | 83 | 83 | 7360.66 | 321904.703
6410-Steam wells/steam field piping problems | 62 | 62 | 400 | 5887.6332
6420-Condensate reinjection system | 1 | 1 | 8 | 8
6440-H2S abatement system problems ? general | 3 | 3 | 202 | 10893.2
6499-Geothermal | 6 | 6 | 90 | 1837.4167
7000-Shaft B | 9 | 9 | 1178.52 | 1375289.3864
7001-Shaft packing | 23 | 23 | 1840.06 | 84827.8212
7003-Lube oil system (use code 7007 to report bearing failures due to lube oil problems) | 36 | 36 | 3077.6 | 314620.3477
7007-Bearings A | 33 | 33 | 3061.01 | 1918605.9939
7008-Bearing cooling system B | 50 | 50 | 3904.77 | 93848.1942
7009-Bearing Oil System | 70 | 70 | 5791.84 | 247609.6437
7011-Other runner problems | 19 | 19 | 732.63 | 728094.5711
7012-Casing; wear ring; or liner cavitation damage | 1 | 1 | 22 | 192720
7020-Nozzle assembly | 3 | 3 | 110.25 | 644.5141
7030-Vibration (Only for unbalance; report bearing failure; etc. in appropriate category) | 43 | 43 | 1035.35 | 174673.9296
7050-Turbine governor | 155 | 155 | 9175.99 | 296615.7966
7052-Other turbine control problems (Report specific wicket gate controls; etc. using the code for the appropriate equipment item.) | 53 | 53 | 5833.27 | 45656.3453
7053-Governor Oil System | 99 | 99 | 6256.88 | 144428.2132
7070-Speed Increaser | 2 | 2 | 81.05 | 1152.6308
7099-Other turbine problems | 34 | 34 | 3103.49 | 249287.2583
7100-Upper reservoir dams and dikes | 19 | 19 | 887.67 | 10269.6968
7101-Lower reservoir dams and dikes | 17 | 17 | 583.8 | 14891.1164
7110-Intake channel or flume (including trash racks) | 232 | 232 | 4118.73 | 335800.9184
7111-Intake tunnel | 7 | 7 | 730.5 | 52807.7914
7112-Ice blockages at intake structures including frazil ice; sheets; blocks of ice; etc A | 5 | 5 | 26 | 600.4667
7120-Headgates | 26 | 26 | 1418.87 | 165863.1879
7121-Shutoff valves | 17 | 17 | 2928.74 | 121596.2526
7123-Shutoff valve bypass line and valve | 5 | 5 | 832 | 3374.833
7124-Penstock | 11 | 11 | 481.19 | 14617.3245
7130-Spiral case | 1 | 1 | 29.78 | 1307.342
7140-Wicket gate assembly | 20 | 20 | 2171.69 | 141377.1121
7141-Wicket gate operating mechanism or positioner | 31 | 31 | 3935.58 | 95535.2105
7142-Wicket gate shear pin | 107 | 107 | 6591.01 | 64740.5879
7160-Pressure regulating valve | 9 | 9 | 644.99 | 1776.3656
7161-Pressure regulating valve operator or positioner | 2 | 2 | 48.7 | 763.92
7162-Relief valve and vacuum breakers | 6 | 6 | 203.5 | 18894.5332
7170-Draft tube | 65 | 65 | 3495 | 15162.8987
7180-Tailrace | 38 | 38 | 1365.23 | 59425.5608
7181-Tail water depressing equipment | 11 | 11 | 1483.12 | 5692.0841
7190-Dewatering and rewatering equipment | 9 | 9 | 708.73 | 26521.9022
7191-Equalizing line | 1 | 1 | 270.5 | 29308.675
7199-Other water supply/discharge problems (use for equipment related problems; use codes 9135 or 9320 for lack of water or discharge limit related problems) | 175 | 175 | 4159.93 | 302073.1463
7201-Inspection A | 2 | 2 | 56.9 | 108.6383
7210-Canals (including siphons; radial gates; and spills) | 4 | 4 | 211.81 | 33804.7957
7220-Unit out of service due to common penstock with unit under repair | 2 | 2 | 52 | 915.2
7240-Powerhouse Substructure | 1 | 1 | 25.71 | 141.405
7299-Other miscellaneous hydro turbine/pump problems (use generator codes and balance of plant electrical and auxiliary codes as appropriate) | 28 | 28 | 3247.59 | 371974.6861
7300-Routine Hydro Planned Outage (reoccuring schedule) | 1 | 1 | 61.74 | 1031.058
7800-Couplings | 3 | 3 | 239.5 | 22790.9583
7820-Bearings B | 11 | 11 | 937 | 69394.7831
7830-Blades | 12 | 12 | 421.02 | 52301.7509
7880-Exhaust diffusers | 1 | 1 | 65.9 | 2930.3533
7920-Lube oil system B | 10 | 10 | 763.98 | 481406.4454
7930-Controls and instrumentation A | 13 | 13 | 889.6 | 14046.2448
7960-Other expander turbine problems | 15 | 15 | 477.63 | 29961.5917
8000-Chemical feed storage; mill feeders; and conveyors | 2 | 2 | 290 | 4697.4999
8010-Crushers/mills | 16 | 16 | 6049.3 | 28216.4791
8020-Mill slurry tanks supply problems | 2 | 2 | 200.75 | 1200.0291
8040-Slurry transfer pumps and motors | 5 | 5 | 873.91 | 5925.3722
8099-Other chemical supply problems | 13 | 13 | 1529 | 66716.0827
8100-Scrubber/absorber tower or module | 77 | 77 | 14648.09 | 921474.5409
8110-Spray nozzles | 3 | 3 | 272 | 24146.9
8120-Spray pumps and motors | 12 | 12 | 2268 | 29808.8162
8125-Scrubber recycle (liquid) pumps | 14 | 14 | 3398.1 | 82417.4323
8127-Scrubber recycle (liquid) pump motors | 3 | 3 | 598 | 13231.3333
8130-Recirculation tanks including agitators | 11 | 11 | 3084 | 56863.9495
8140-Reaction tanks including agitators | 1 | 1 | 197 | 413.7
8160-Mist eliminators/demisters and washdown | 20 | 20 | 3425 | 153975.2157
8199-Other scrubber problems | 30 | 30 | 8399.9 | 331106.0018
8200-Piping | 20 | 20 | 3180.16 | 18506.9021
8210-Valves | 11 | 11 | 1323.02 | 17699.6458
8230-Ducting | 8 | 8 | 2175.04 | 228653.7061
8235-Demister | 2 | 2 | 54 | 9.45
8240-Bypass dampers | 1 | 1 | 280 | 1614.6665
8250-Dampers other than bypass | 4 | 4 | 940 | 86890.3833
8260-Scrubber booster I.D. fan (fan specific to the scrubber) | 26 | 26 | 5009.3 | 126290.0487
8261-Scrubber booster I.D. fan drive | 1 | 1 | 250 | 14162.5
8262-Scrubber booster I.D. fan vibration (fan specific to the scrubber) | 11 | 11 | 2853 | 64302.7821
8265-Scrubber ID fan dampers | 1 | 1 | 65 | 606.6666
8270-Scrubber booster F.D. fan (fan specific to the scrubber) | 5 | 5 | 839.25 | 28344.6121
8272-Scrubber booster F.D. fan vibration (fan specific to the scrubber) | 7 | 7 | 1284 | 43479.4996
8274-Scrubber booster F.D. fan blades (fan specific to the scrubber) | 1 | 1 | 279 | 860.2499
8280-Reagent feed piping | 6 | 6 | 510 | 6211.0831
8299-Other piping; ducting; damper; and fan problems | 4 | 4 | 392.5 | 1130
8300-Waste disposal/recovery tanks | 2 | 2 | 791 | 56429.3165
8330-Dewatering equipment (thickener; centrifuge; etc.) | 9 | 9 | 1508.7 | 64619.1833
8340-Centrifuge/vacuum filter | 2 | 2 | 247.3 | 2967.6
8399-Solids conveying and mixing system problems | 1 | 1 | 39 | 553.8
8404-Scrubber gas discharge reheaters - tube leaks | 1 | 1 | 62.2 | 445.7666
8410-Scrubber instruments and controls | 5 | 5 | 1666 | 16604.4327
8415-Liquid level controls | 2 | 2 | 121.85 | 104.0691
8426-Miscellaneous electrical failures | 6 | 6 | 2160 | 374499.9996
8499-Other miscellaneous wet scrubber problems | 23 | 23 | 3348.25 | 843869.0077
8500-Slurry storage and feed tanks | 3 | 3 | 527.5 | 5033.7081
8501-Reagent storage; feed bins; and conveyors | 2 | 2 | 505 | 3219.7498
8502-Weigh feeders | 1 | 1 | 149 | 1527.25
8503-Screw conveyors | 1 | 1 | 37 | 163.4166
8504-Mills/slakers | 7 | 7 | 1397 | 38907.4498
8506-Slurry pipelines | 8 | 8 | 2258.6 | 27559.0662
8507-Reagent uploading and transfer systems | 2 | 2 | 503 | 11258.2498
8510-Slurry mixers and agitators | 5 | 5 | 780 | 28394.3666
8520-Slurry transfer pumps and motors | 10 | 10 | 2349 | 28331.9493
8521-Reagent/slurry problems | 7 | 7 | 1504.38 | 5993.2329
8522-Piping | 2 | 2 | 121.1 | 5831.3716
8523-Valves | 3 | 3 | 1237 | 8441.8329
8526-Dampers | 9 | 9 | 918.9 | 21660.8281
8528-Dry scrubber instruments and controls | 3 | 3 | 204 | 23006.6666
8529-Gas dispersers | 2 | 2 | 108 | 3091.5
8530-Spray towers | 20 | 20 | 2743.38 | 193867.6568
8531-Spray machine/atomizer | 83 | 83 | 9996.69 | 99003.0382
8532-Spray machine/atomizer motors | 18 | 18 | 1872.75 | 173376.5879
8533-Spray machine/atomizer lubrication systems | 15 | 15 | 1271 | 9081.283
8534-Spray machine/atomizer vibration problems | 24 | 24 | 3320 | 56807.6656
8535-Fly ash conveyors | 9 | 9 | 1007.18 | 11303.967
8538-Recycle storage and feed tanks including agitators | 13 | 13 | 4058 | 194972.7657
8539-Recycle slurry transfer pumps | 3 | 3 | 290 | 2072.5666
8540-Waste disposal | 1 | 1 | 448 | 384070.4
8544-Mechanical failures | 2 | 2 | 155 | 12303.9166
8545-Electrical failures | 8 | 8 | 2119.26 | 43271.6359
8547-Inspection | 4 | 4 | 558 | 1620.5166
8549-Other dry scrubber problems | 18 | 18 | 2051.96 | 244447.5594
8550-Electrostatic precipitator fouling | 35 | 35 | 3646 | 276706.0318
8551-Electrostatic precipitator field out of service | 109 | 109 | 20589.65 | 278827.8114
8560-Electrostatic precipitator problems | 46 | 46 | 8436.6 | 365323.1006
8590-Other precipitator problems | 15 | 15 | 4620.1 | 284856.8823
8600-Flue gas additives (furnace injection) | 4 | 4 | 1234.3 | 27259.3649
8601-SO3 mitigation | 12 | 12 | 4837.87 | 20571.403
8620-Mercury Abatement | 27 | 27 | 4866.53 | 336288.3246
8650-Baghouse systems; general | 341 | 341 | 23448.65 | 946508.947
8651-Bag failures and rebagging | 93 | 93 | 4176.38 | 103151.2614
8653-Inflation and deflation fans and motors | 22 | 22 | 601 | 23970.1831
8654-Baghouse booster fans and motors | 21 | 21 | 1616 | 34391.3328
8655-Structural duct work and dampers | 3 | 3 | 215.94 | 12647.4866
8656-Controls and instrumentation B | 69 | 69 | 4554.28 | 66116.9856
8657-Ash handling system and hoppers | 28 | 28 | 4101.45 | 276339.0349
8670-Emission monitors (other than CEMS) A | 3 | 3 | 24 | 1162.7167
8699-Other miscellaneous pollution control equipment problems | 36 | 36 | 5319.5 | 326588.9717
8700-CEMS Certification and Recertification | 29 | 29 | 2976.7 | 54845.456
8710-SO2 analyzer problems | 1 | 1 | 100 | 608.3333
8720-NOx analyzer problems | 68 | 68 | 5630.68 | 116089.3429
8730-CO analyzer problems | 27 | 27 | 3011.33 | 34757.4239
8740-CO2 analyzer problems | 4 | 4 | 346.1 | 7050.1332
8750-O2 analyzer problems | 19 | 19 | 1809.14 | 19750.8543
8760-Opacity monitor problems | 14 | 14 | 1707.5 | 7137.766
8770-Flow monitor problems | 5 | 5 | 604.2 | 6540.7733
8780-Data acquisition system problems | 10 | 10 | 887.95 | 49780.1221
8790-Miscellaneous CEMS problems | 131 | 131 | 12060.95 | 218039.2925
8802-SNCR NOx Control system | 11 | 11 | 1299 | 9632.558
8809-Other SNCR NOx problems | 15 | 15 | 1141.76 | 8458.9306
8810-SCR NOx Reactor | 3 | 3 | 276.6 | 181.9165
8811-SCR NOx Reagent | 10 | 10 | 693.29 | 5888.9619
8812-SCR NOxCatalyst | 46 | 46 | 2488.88 | 101877.1517
8813-SCR NOx Injection grid piping/valves | 22 | 22 | 1751.53 | 91093.3914
8814-SCR NOx Catalyst support material | 1 | 1 | 65 | 6986.4166
8815-SCR NOx Soot blowers | 2 | 2 | 781.1 | 927572.0966
8816-SCR NOx Plugging | 77 | 77 | 8639.16 | 1078569.0406
8817-SCR NOx Control system | 41 | 41 | 2993.39 | 99906.5675
8820-SCR NOx Ammonia injection grid piping/valves | 45 | 45 | 6621.89 | 70008.7637
8821-SCR NOx Ammonia tanks; piping and valves (not injection) | 34 | 34 | 5120.75 | 62034.2342
8822-SCR NOx Ammonia air blowers | 35 | 35 | 3664.49 | 69580.484
8823-SCR NOx Other ammonia system problems | 94 | 94 | 9769.73 | 140183.6297
8825-Other SCR NOx problems | 87 | 87 | 4229.51 | 62834.046
8840-CO Active catalyst | 33 | 33 | 1471.09 | 139943.2966
8841-CO Support materials | 6 | 6 | 1086.4 | 121603.9513
8842-CO Plugging | 3 | 3 | 163 | 5784.65
8845-Other CO reduction problems | 90 | 90 | 6473.53 | 22382.0494
9000-Flood | 27 | 27 | 3450.22 | 111467.6305
9001-Drought | 18 | 18 | 2434.84 | 403241.1942
9010-Fire; not related to a specific component | 20 | 20 | 1841.45 | 455557.8487
9020-Lightning | 177 | 177 | 34793.47 | 577278.2922
9030-Earthquake | 12 | 12 | 504.8 | 1940.3516
9031-Tornado | 13 | 13 | 2002 | 488068.5996
9035-Hurricane | 15 | 15 | 566.48 | 571751.0332
9036-Storms (ice; snow; etc) | 177 | 177 | 14071.79 | 365432.5022
9040-Other catastrophe | 9 | 9 | 622.8 | 3450.6227
9110-Core coastdown (nuclear) | 6 | 6 | 352.32 | 58549.8508
9130-Lack of fuel: Physical failures of fuel supply or delivery/transportation of fuel | 278 | 278 | 34385.61 | 1673800.3802
9131-Lack of fuel: Contract or Tariff allows for interruption | 385 | 385 | 44302.22 | 1374309.9704
9132-Wet Fuel - Biomass | 284 | 284 | 1761.9 | 26534.167
9134-Fuel conservation | 64 | 64 | 8431.08 | 67603.6221
9135-Lack of water (hydro) | 2654 | 2654 | 116394.22 | 2043909.9653
9136-Problems with Primary Fuel for Units with Secondary Fuel Operation | 4 | 4 | 951.4 | 5287.3032
9137-Ground water or other water supply problems | 89 | 89 | 9157.29 | 86807.0611
9138-High Water Level in Tailrace (too much water) | 15 | 15 | 1119.6 | 128638.9887
9140-Plant modifications to burn different fuel (not regulatory mandated) | 1 | 1 | 25 | 8399.5833
9160-Other economic problems | 12 | 12 | 1506.76 | 218512.0096
9180-Economic (for internal use at plants only) | 1 | 1 | 237 | 738.6498
9181-Economic (for internal use at plants only) | 4 | 4 | 2408 | 3802.1829
9182-Economic (for internal use at plants only) | 33 | 33 | 16428 | 38952.895
9191-Economic (for internal use at plants only) | 1 | 1 | 20 | 254.3333
9200-High ash content | 324 | 324 | 10368.5 | 250409.4646
9201-High ash content ? (not outside management control) | 1 | 1 | 6.39 | 207.5685
9205-Poor quality natural gas fuel; low heat content | 30 | 30 | 642.22 | 7379.3215
9220-High sulfur content | 31 | 31 | 7878 | 76160.4981
9250-Low Btu coal due to low BTU vane of coal not expected (Outside Management Control) | 195 | 195 | 4357.64 | 231912.8908
9251-Low Btu Coal From Contract For Low Btu Coal | 32 | 32 | 793.67 | 26487.6614
9270-Wet coal | 302 | 302 | 35491.84 | 393296.6309
9271-Wet coal (not outside management control) | 114 | 114 | 13341.57 | 361178.0386
9272-Wet Fuel (other than coal) | 2 | 2 | 0.36 | 71.034
9280-Frozen coal | 1 | 1 | 15.1 | 2028.9367
9290-Other fuel quality problems | 379 | 379 | 23384.53 | 747678.5584
9291-Other fuel quality problems (not outside management control) | 104 | 104 | 2068.06 | 74301.5776
9300-Transmission system problems other than catastrophes (do not include switchyard problems in this category; see codes 3600 to 3629) | 610 | 610 | 67069.52 | 3905406.0927
9305-Ash disposal problem | 3 | 3 | 855.2 | 64591.1597
9320-Other miscellaneous external problems | 487 | 487 | 45775.05 | 2629224.9485
9340-Synchronous Condenser Operation | 2 | 2 | 101.5 | 123.1167
9350-Public Safety/River Rescue | 1 | 1 | 54 | 10.8
9510-Plant modifications strictly for compliance with new or changed regulatory requirements (scrubbers; cooling towers; etc.) | 3 | 3 | 176.63 | 94850.9566
9590-Miscellaneous regulatory (this code is primarily intended for use with event contribution code 2 to indicate that a regulatory-related factor contributed to the primary cause of the event) | 45 | 45 | 3385.84 | 143223.6922
9600-SO2 stack emissions (fossil) | 228 | 228 | 25185.64 | 221978.1941
9610-NOx stack emissions (fossil) | 50 | 50 | 4058.07 | 230707.9971
9613-NOx stack emissions (gas turbine) | 125 | 125 | 10246.78 | 132327.6694
9614-NOx stack emissions (jet engines) | 43 | 43 | 1849.05 | 14853.0215
9615-NOx stack emissions (Internal Combustion/Reciprocating Engines) | 2 | 2 | 31.04 | 58.216
9616-CO stack emissions | 86 | 86 | 5447.86 | 34360.9393
9620-Particulate stack emissions (fossil) | 54 | 54 | 8126.9 | 146587.5184
9623-Particulate stack emissions (gas turbine) | 9 | 9 | 1207.1 | 144427.0264
9630-Opacity (fossil) | 519 | 519 | 56440.44 | 682247.3916
9650-Other stack or exhaust emissions (fossil) | 50 | 50 | 7368.68 | 356089.2978
9653-Other stack or exhaust emissions (gas turbine) | 34 | 34 | 3843.2 | 22914.4838
9654-Other stack or exhaust emissions (jet engines) | 3 | 3 | 143.4 | 937.85
9656-Other stack or exhaust emissions testing - fossil | 13 | 13 | 2177.04 | 19395.5864
9657-Other stack or exhaust emissions testing - gas turbine | 8 | 8 | 751.7 | 14968.4215
9660-Thermal discharge limits (fossil and nuclear) | 86 | 86 | 5150.2 | 107644.1087
9663-Thermal discharge limits (gas turbine) | 2 | 2 | 41 | 643.8167
9690-Other miscellaneous operational environmental limits (fossil and nuclear) | 96 | 96 | 8814.47 | 753185.753
9693-Other miscellaneous operational environmental limits (gas turbines) | 23 | 23 | 2440.02 | 588039.66
9694-Other miscellaneous operational environmental limits (jet engines) | 17 | 17 | 538.08 | 3642.2116
9695-Other miscellaneous operational environmental limits (Internal Combustion/Reciprocating Engines) | 1 | 1 | 29.04 | 5756.696
9696-Other miscellaneous operational environmental limits (hydro and PS) | 142 | 142 | 5761.55 | 401867.8398
9700-OSHA-related retrofit or inspection | 2 | 2 | 1427.7 | 28047.4831
9720-Other safety problems | 35 | 35 | 3413.8 | 1887176.6173
9900-Operator error | 335 | 335 | 73889.96 | 1715034.768
9910-Maintenance personnel error | 86 | 86 | 14795 | 67261.8169
9920-Contractor error | 38 | 38 | 7954.62 | 1068406.0271
9930-Operating procedure error | 38 | 38 | 7304.49 | 28545.6034
9940-Maintenance procdure error | 13 | 13 | 1306.24 | 17812.2271
9950-Contractor procedure error | 12 | 12 | 1401.2 | 4973.2909
9960-Staff shortage | 29 | 29 | 1525.3 | 94882.526
9997-NERC Reliability Standards requirements | 6 | 6 | 1057 | 202493.8997
9998-Black Start testing | 10 | 10 | 932.61 | 10841.6
9999-Total unit performance testing (use appropriate codes for individual component testing) | 223 | 223 | 8172.62 | 9351984.6516
0000-Reserve shutdown | 6 | 6 | 445.62 | 87313.357
0113-Solid fuel tank/hopper fires | 5 | 5 | 58.8 | 1867.485
0127-Other coal crusher dryer problems (see code 0106) | 1 | 1 | 72 | 418.8
0156-Other sorbent feed problems | 1 | 1 | 87 | 787.35
0163-Bed material feeders | 1 | 1 | 0.64 | 5.728
0164-Bed material feeder motors | 1 | 1 | 16 | 18.4
0361-Burner orfices | 1 | 1 | 16 | 184.5333
0720-Blowdown system controls / instrumentation | 1 | 1 | 171 | 555.75
0848-Inlet panel | 1 | 1 | 52 | 130.8666
0910-Slag-tap (other than cyclone furnace) | 1 | 1 | 198 | 13232.9999
0933-Bed material fans/blowers | 1 | 1 | 24 | 467.2
0952-Char reinjection piping/valves | 1 | 1 | 4.8 | 275.52
0982-High pressure loop seal recirculation fan/blower controls | 1 | 1 | 30.1 | 73.745
0990-Refractory | 5 | 5 | 829 | 155269.8996
1300-Water side fouling | 1 | 1 | 72 | 5827.2
1330-Slag fall damage | 5 | 5 | 651.8 | 49699.9066
1451-Fluidized Air Fan | 2 | 2 | 290.3 | 2514.7466
1555-Flue gas recirculation fan controls | 2 | 2 | 805 | 1360.8332
1820-Chemical cleaning/steam blows | 1 | 1 | 65 | 80.1666
2071-Refueling equipment problems | 1 | 1 | 966 | 268998.7994
2112-Control rod hydraulic drives | 2 | 2 | 49 | 98.8833
2150-Control rod instrumentation | 1 | 1 | 484.6 | 37936.1032
2160-Other control rod drive problems | 2 | 2 | 675.7 | 92390.3731
2199-Other reactor vessel problems | 1 | 1 | 0.01 | 1.0002
2265-Pressurizer (also see codes 2290; 2330; and 2340) | 3 | 3 | 2135 | 220839.483
2320-Other reactor coolant valves (including RCS boundary valves in connected systems) | 2 | 2 | 1125.44 | 26571.1431
2399-Other miscellaneous reactor coolant system problems | 1 | 1 | 141 | 36890.3
2540-Other steam valves | 8 | 8 | 134.1 | 36832.4393
2599-Other steam generator problems | 3 | 3 | 1585.72 | 46519.1348
2604-High pressure valves | 8 | 8 | 104 | 31950.9333
2649-Other emergency core cooling/residual heat removal system problems | 1 | 1 | 213.55 | 5007.7475
2816-Valves and piping | 2 | 2 | 1446 | 56370.1997
2842-Auxiliary feedwater pump steam turbines (including steam control valves) | 1 | 1 | 11 | 55.9167
2844-Auxiliary feedwater valves | 1 | 1 | 124.54 | 46577.96
2849-Other auxiliary feedwater problems | 1 | 1 | 806.53 | 6102.7431
2890-Condenser off-gas system problems | 1 | 1 | 378.3 | 7994.7399
3170-Condenser inspection (use code 3110 to report looking for tube leaks) | 1 | 1 | 325 | 4100.4164
3180-Major condenser overhaul | 1 | 1 | 49 | 36994.1833
3248-Cooling Tower Overhaul | 1 | 1 | 25 | 102398.3333
3291-Waste water (zero discharge) system fouling | 1 | 1 | 103.6 | 783.9066
3345-IP heater head leaks | 2 | 2 | 643.3 | 44955.04
3419-Feedwater pump drive - gear | 2 | 2 | 1054.5 | 136984.4996
3453-Feedwater Booster Pump Drive Motor - Variable Speed | 2 | 2 | 334 | 1482.8832
3456-Feedwater Booster Pump Drive - Steam Turbine | 3 | 3 | 1195 | 7154
3457-Feedwater Booster Pump Coupling and Drive Shaft | 2 | 2 | 598 | 324081.8331
3542-LP Extraction steam instruments and controls | 2 | 2 | 248.3 | 475.5849
3826-Closed cooling water strainer | 1 | 1 | 485 | 2425
3881-Seal air fan drive - motor | 1 | 1 | 38.1 | 3329.94
3882-Seal air control dampers and drives | 3 | 3 | 628.7 | 5324.9249
4009-Nozzle bolting A | 1 | 1 | 18.38 | 21.137
4011-Diaphragms A | 1 | 1 | 137.2 | 237221.0866
4101-Inner casing B | 2 | 2 | 1520 | 591.333
4110-Nozzles and nozzle blocks B | 1 | 1 | 223 | 613.25
4120-Shaft seals C | 4 | 4 | 1846.6 | 19351.9345
4200-Outer casing C | 3 | 3 | 969 | 15173.2829
4215-Wheels or spindles B | 1 | 1 | 237 | 865.05
4282-Lube oil conditioners | 3 | 3 | 867.74 | 75863.1013
4411-Steam turbine gear box (single shaft configuration) | 1 | 1 | 195.38 | 338.6586
5020-Low pressure shaft D | 1 | 1 | 70 | 14
5230-Heat shields C | 4 | 4 | 220 | 34908.4999
5411-High pressure bearings B | 3 | 3 | 183.33 | 119013.3141
5470-Combustor casing B | 1 | 1 | 45 | 37251
5474-Flashback (including instrumentation) | 2 | 2 | 133.5 | 172
5498-Expansion joints B | 1 | 1 | 52 | 598
5600-Reduction gear A | 1 | 1 | 274.38 | 46004.3798
5630-Heat shields A | 5 | 5 | 691 | 18671.3165
5641-Fire in unit B | 1 | 1 | 49.9 | 2012.6333
5670-Hot end inspection A | 1 | 1 | 64 | 51514.6666
5762-crankshaft | 2 | 2 | 28.1 | 332.35
5811-HT water pre heater | 1 | 1 | 19 | 76
5890-Major overhaul (use for non-specific overhaul only; see page B-1) D | 1 | 1 | 11.04 | 103.224
6031-LP superheater | 1 | 1 | 188 | 2030.4
6120-IP steam piping up to turbine stop valves - Between 200 & 600 PSIG (see 0790 for piping supports) | 5 | 5 | 387.9 | 6750.0115
6135-LP steam isolation/boundary valves | 4 | 4 | 684.64 | 3981.0357
6143-HP Desuperheater/attemperator drums | 1 | 1 | 152 | 4653.7332
6153-LP Desuperheater/attemperator drums | 1 | 1 | 225.25 | 337.875
6162-HP Startup bypass tanks or flash tanks | 2 | 2 | 54 | 292.5
6170-IP Startup bypass system piping (including drain lines up to heaters or condenser) - Between 200-600 PSIG | 3 | 3 | 626.35 | 255634.4757
6430-Unit H2S emission limitations ? regulatory | 2 | 2 | 104 | 2896.9333
7840-Discs | 1 | 1 | 97.4 | 48.7
7910-Outer exhaust casing | 12 | 12 | 858.82 | 8803.7934
7940-Evactor | 1 | 1 | 25.8 | 304.44
8003-Bucket elevators | 5 | 5 | 3423 | 11387.6161
8220-Strainers or filters | 6 | 6 | 180.69 | 130778.3284
8425-Miscellaneous mechanical failures | 4 | 4 | 625 | 26440.75
8460-Testing | 2 | 2 | 248 | 497.2333
8524-Strainers or filters | 1 | 1 | 27.1 | 78.1383
8527-Other piping; ducting; and damper problems | 2 | 2 | 336 | 7355.5999
8541-Recycle feed bins | 1 | 1 | 197 | 2364
9139-Ground water or other water supply problems (OMC) | 2 | 2 | 675.46 | 30632.3172
9230-High vanadium content | 1 | 1 | 56 | 28.9333
9310-Operator training | 3 | 3 | 479.65 | 918.0941
9504-Regulatory (environmental) proceedings and hearings - regulatory agency initiated | 4 | 4 | 1278 | 2784104.7333
9603-SO2 stack emissions (gas turbine) | 3 | 3 | 389.7 | 22438.8999
9624-Particulate stack emissions (jet engines) | 2 | 2 | 70 | 111142.5
9634-Opacity (jet engines) | 3 | 3 | 186.6 | 23414.1533
9655-Other stack or exhaust emissions (Internal Combustion/Reciprocating Engines) | 6 | 6 | 67.22 | 856.2925
9670-Noise limits (not for personnel safety) (fossil and nuclear) | 1 | 1 | 435 | 2958
9686-Fish kill (hydro and PS) | 3 | 3 | 41.9 | 32143.18
Total Result | 53738 | 53738 | 6690007.3 | 399175709.2256

## Data
CauseCode | CauseCodeName | SystemName | ComponentName | EventTypeCode | EventTypeName | EventYearNbr | FuelCategory | FuelCode | UnitTypeCode | UnitTypeCodeDesc | RegionCode | Season | MWHrsLost | MWLost | DISTINCT_UNITS | EVENT_COUNT | Cause | EventType | UnitType
0000 | Reserve shutdown | External | Economic | D1 | Forced - Immediate | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Winter | 63410.5005 | 8.73 | 1 | 1 | 0000-Reserve shutdown | D1-Forced - Immediate | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0000 | Reserve shutdown | External | Economic | SF | Startup Failure | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Summer | 136.7391 | 106.55 | 1 | 1 | 0000-Reserve shutdown | SF-Startup Failure | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0000 | Reserve shutdown | External | Economic | U1 | Forced - Immediate | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Off-Peak | 30.1891 | 106.55 | 1 | 1 | 0000-Reserve shutdown | U1-Forced - Immediate | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0000 | Reserve shutdown | External | Economic | U1 | Forced - Immediate | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Summer | 665.9375 | 106.55 | 1 | 1 | 0000-Reserve shutdown | U1-Forced - Immediate | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0000 | Reserve shutdown | External | Economic | SF | Startup Failure | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Summer | 246.8408 | 106.55 | 1 | 1 | 0000-Reserve shutdown | SF-Startup Failure | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0000 | Reserve shutdown | External | Economic | D1 | Forced - Immediate | 2023 | Gas | GG | 300 | Gas Turbine/Jet Engine (Simple Cycle Operation) | WECC | Winter | 22823.15 | 10.69 | 1 | 1 | 0000-Reserve shutdown | D1-Forced - Immediate | 300-Gas Turbine/Jet Engine (Simple Cycle Operation)
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 48580.6 | 358 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 81811.2164 | 343 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 223 | 223 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 248 | 248 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1139.6332 | 358 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 365.8664 | 448 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1430.8666 | 338 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7648.6665 | 298 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 133.4666 | 104 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5570.1332 | 448 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1861.2 | 198 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1312 | 328 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 470.4 | 448 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | U1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7319.9998 | 288 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16290.1331 | 368 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2284.9 | 313 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21368.5331 | 368 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0020 | Coal car dumpers; shakers; and unloaders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18529.9997 | 408 | 1 | 1 | 0020-Coal car dumpers; shakers; and unloaders | D1-Forced - Immediate | 100-Fossil-Steam
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 16.0333 | 13 | 1 | 1 | 0022-Unloading/receiving hopper (train/truck) | D1-Forced - Immediate | 800-Miscellaneous
0022 | Unloading/receiving hopper (train/truck) | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 810 | Multi-boiler/Multi-turbine | NPCC | Winter | 262800 | 30 | 2 | 2 | 0022-Unloading/receiving hopper (train/truck) | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0024 | Rotary plow | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4704.3832 | 277 | 1 | 1 | 0024-Rotary plow | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 869.5 | 370 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 815.1665 | 365 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1045.8633 | 238.6 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 682.2549 | 405.3 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50828.8 | 125.4 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 209.0833 | 65 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1201.4166 | 65 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1758.25 | 65 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3638.75 | 355 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97938.75 | 455 | 1 | 1 | 0028-Dust collection system | U2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1214.4166 | 65 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18232.5 | 330 | 1 | 1 | 0028-Dust collection system | U2-Forced - Delayed | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 787.5 | 375 | 1 | 1 | 0028-Dust collection system | D1-Forced - Immediate | 100-Fossil-Steam
0028 | Dust collection system | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2435.3333 | 65 | 1 | 1 | 0028-Dust collection system | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41 | 205 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1391 | 214 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2079.0831 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3295.67 | 370.3 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1341.6665 | 500 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2308.3333 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 406.6666 | 80 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 540 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2371.5832 | 191 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1127.3333 | 190 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22.9991 | 106.15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.115 | 106.23 | 1 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 203 | 60 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469.3331 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 479.3999 | 423 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 231 | 132 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 682.7332 | 418 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 751.6665 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 731.825 | 21.9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2530.95 | 359 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7787.9999 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 7.2 | 7.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5364.45 | 393 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46655 | 533.2 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 100 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 333.6667 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.1666 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2205.3333 | 160 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 14399 | 484 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 315 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1803.4 | 508 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1956.3997 | 438 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2655 | 295 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 85.05 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2731.35 | 393 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5540.7331 | 383 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33501.7664 | 406 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.8 | 96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 60.4166 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1059.6665 | 187 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15812.3 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33.3333 | 10 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 164.9999 | 198 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 849.3333 | 35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1597.695 | 463.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 878.1498 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2460 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2630.8331 | 350 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13499.1997 | 429 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 41.4867 | 12.7 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2793.6999 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9373.95 | 333 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2265.25 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50 | 15 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 467.8666 | 116 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21607.5 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.25 | 349 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 421.6333 | 91 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 163.1667 | 22 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 321.75 | 429 | 4 | 4 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1699.8998 | 267 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2700 | 540 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2149.7666 | 143 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2651.25 | 303 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1030.44 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 273.7 | 51 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93.8349 | 114.9 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 404.1667 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 700 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1698 | 283 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3736.25 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 702 | 351 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.8333 | 9.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7.65 | 17 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1297.6832 | 343 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 50.758 | 24.76 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2986.5498 | 483 | 2 | 2 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.008 | 106.89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1162.3333 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6783 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7467.9497 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.2 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 165.6 | 184 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 620.4 | 264 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1699.9998 | 300 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3883.1999 | 144 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6603 | 440.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31 | 7.75 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 332.1498 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1006.95 | 411 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1093.1666 | 70 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1372.5 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13042.4999 | 423 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1620 | 540 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 290.3332 | 268 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 580.7333 | 124 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.5306 | 327.68 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 508.3331 | 305 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.5 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 940 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5286.133 | 461 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 136 | 48 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 211.8082 | 363.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 512.01 | 56.89 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 580.8332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 689.6464 | 440.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72.1664 | 433 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 307.5 | 205 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 538.65 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3192 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2362.95 | 267 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3542.4 | 144 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96.3 | 107 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1035.98 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4445.5 | 523 | 1 | 1 | 0030-Coal conveyors and feeders | U2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 44.2708 | 106.25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 360 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5650.6332 | 427 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 431.1665 | 199 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5789.3499 | 417 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2111.2 | 232 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1224 | 510 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.7249 | 106.35 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 324 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1747.2 | 96 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 799.4815 | 403.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3038.5 | 295 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3946.6666 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.6332 | 334 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4759.3333 | 220 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2299 | 209 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3161.6 | 304 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 279.496 | 104.16 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16521.7664 | 361 | 1 | 1 | 0030-Coal conveyors and feeders | U3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 61.25 | 25 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.3333 | 40 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2212.8333 | 110 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.8 | 24 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5159.7 | 378 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.19 | 14.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 650 | 260 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 813.5999 | 432 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 990 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1020.9666 | 281 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1040.4 | 289 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1428.45 | 107 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2238.3332 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 120 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 470 | 141 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1948.7998 | 288 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 252.6499 | 93 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 128732.833 | 515 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 599.9998 | 360 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 616.6664 | 370 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1497.2498 | 339 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4282.5999 | 399 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208.08 | 520.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 363.35 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1713.6 | 102 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 394.8 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 600.25 | 343 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 976.6666 | 293 | 2 | 2 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1415.4945 | 206.14 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 241.6667 | 50 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1195.8 | 159.44 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1262.5 | 202 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2180.4 | 316 | 1 | 1 | 0030-Coal conveyors and feeders | D3-Forced - Postponed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4.5 | 27 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17.7016 | 106.21 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 81.75 | 45 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 512.4 | 42 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2185.6666 | 332 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2360.1666 | 170 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.1666 | 55 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 800.8 | 154 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 863.3332 | 185 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1512.5 | 250 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 550 | 220 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1440 | 320 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 520.9167 | 47 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.8 | 44 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 382.5 | 153 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 154.0832 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5337.0999 | 318 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23151.35 | 773 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 360 | 20 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 785.7 | 291 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1536.1332 | 164 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6359.6047 | 500.1 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 203.5 | 66 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 688.08 | 28.67 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17691.7 | 439 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 19.312 | 12.07 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3749.625 | 126.25 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 616.3332 | 215 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 80.1 | 106.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 220.8332 | 265 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446.3332 | 412 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 678.1098 | 490.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 911.05 | 57 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2248.1666 | 329 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3210 | 214 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 315 | 180 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3003 | 273 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1718.6999 | 153 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2460.9665 | 371 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1604.1332 | 227 | 1 | 1 | 0030-Coal conveyors and feeders | D2-Forced - Delayed | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 354.56 | 22.16 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 100-Fossil-Steam
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 789.6 | 65.8 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 86.0167 | 13 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 782.4 | 65.2 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 3825 | 85 | 1 | 1 | 0030-Coal conveyors and feeders | U1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 6 | 4 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 650-Fluidized Bed
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 107.6 | 269 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1251.15 | 439 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2788.8496 | 579 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 300.2831 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2926.0165 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1695.8665 | 644 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1722.7 | 749 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5492.6664 | 749 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 223.4665 | 419 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 450.6666 | 169 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0030 | Coal conveyors and feeders | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 318.45 | 579 | 1 | 1 | 0030-Coal conveyors and feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1601.9832 | 277 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | D2-Forced - Delayed | 100-Fossil-Steam
0035 | Metal detector/collector (including magnetic separator) | Boiler | Boiler Fuel Supply to Bunker | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7372.8664 | 427 | 1 | 1 | 0035-Metal detector/collector (including magnetic separator) | U2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 433.0999 | 106.5 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.624 | 106.17 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 943.4999 | 153 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 671.6666 | 130 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 855.0499 | 147 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 272.7999 | 186 | 1 | 1 | 0060-Coal crushers including motors | D2-Forced - Delayed | 100-Fossil-Steam
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1212.8999 | 117 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 650-Fluidized Bed
0060 | Coal crushers including motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 143.3333 | 43 | 1 | 1 | 0060-Coal crushers including motors | D1-Forced - Immediate | 650-Fluidized Bed
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 609.5332 | 164 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 48 | 48 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 170.85 | 67 | 1 | 1 | 0075-Storage silos/hoppers | D2-Forced - Delayed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1187.5 | 125 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2051.4 | 526 | 1 | 1 | 0075-Storage silos/hoppers | U1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 123.5 | 114 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 34.1667 | 41 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0 | 0 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.3038 | 37.03 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3.2167 | 9.65 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4971.6666 | 314 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 339 | 45 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3280 | 820 | 1 | 1 | 0075-Storage silos/hoppers | D3-Forced - Postponed | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36491.6666 | 145 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 93.75 | 45 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0075 | Storage silos/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4175.9999 | 216 | 1 | 1 | 0075-Storage silos/hoppers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3072.57 | 445.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 57.0267 | 9.4 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3419.01 | 510.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3510 | 390 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 907.3 | 17.2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 13.5768 | 15.37 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3057.39 | 443.1 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3784.6365 | 538.1 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 32.5 | 15 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 6.5067 | 3.2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 148.9317 | 19.3 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 6.12 | 10.2 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 100-Fossil-Steam
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 360.75 | 39 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 175.5 | 39 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 204.75 | 39 | 1 | 2 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0080 | Stackers/reclaimers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 253.5 | 39 | 1 | 1 | 0080-Stackers/reclaimers | D1-Forced - Immediate | 800-Miscellaneous
0084 | Coal conveyor scales-storage coal pile | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5022.733 | 458 | 1 | 1 | 0084-Coal conveyor scales-storage coal pile | D1-Forced - Immediate | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 340.9 | 48.7 | 1 | 1 | 0085-Bunker feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0085 | Bunker feeder coal scales | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 64.6 | 19 | 1 | 1 | 0085-Bunker feeder coal scales | D1-Forced - Immediate | 800-Miscellaneous
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2362.6666 | 320 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 547 | 54.7 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0090 | Bunker fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4791.2332 | 358 | 1 | 1 | 0090-Bunker fires | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.808 | 54.72 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1315.2 | 192 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 743.0166 | 109 | 1 | 1 | 0095-Bunker flow problems | D2-Forced - Delayed | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 794.0625 | 90.75 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 247.5 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 250.4083 | 15.1 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4668.9999 | 210 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3667.2 | 191 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7771.255 | 98.06 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1.5833 | 2.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.424 | 51.36 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2008.9999 | 210 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2323.4166 | 245 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1113.75 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 77 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163 | 81.5 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.1665 | 190 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1592.3742 | 319.54 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.2499 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 30.6666 | 230 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 123.75 | 25 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7014.3333 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2900.3333 | 220 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 9987.1695 | 131.67 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 263.9999 | 99 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 100-Fossil-Steam
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 468 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1482 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 419.25 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 208 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 234 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 178.1 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 546 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 279.5 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 126.75 | 39 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 273 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 253.5 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 117 | 39 | 1 | 2 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 165.75 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 214.5 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 380.25 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 195 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 273 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0095 | Bunker flow problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 234 | 39 | 1 | 1 | 0095-Bunker flow problems | D1-Forced - Immediate | 800-Miscellaneous
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 501.8 | 38.6 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3297.8166 | 161 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 469.9333 | 76 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 320.45 | 87 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0100 | Bunker gates | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 455 | 50 | 1 | 1 | 0100-Bunker gates | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18609.8667 | 38 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10669.7667 | 38 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21386 | 37 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7752 | 38 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6368.1667 | 38 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0105 | Bunker structures | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20321.1333 | 38 | 1 | 1 | 0105-Bunker structures | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22.3413 | 167.56 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.6667 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.3333 | 125 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.5333 | 56 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1863.3332 | 520 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 396 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 674.3332 | 170 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8178.3166 | 341 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2256.6831 | 841 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 25682.78 | 45.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 683.421 | 87.06 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2741.57 | 210.89 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 343.3999 | 204 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 20 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 803.4665 | 262 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D2-Forced - Delayed | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 627 | 627 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 494 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 546.3332 | 298 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.8 | 48 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.25 | 119 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120.6666 | 40 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 157.4999 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2044.0833 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5850.4166 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30 | 10 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4101.1333 | 45.4 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 151.8 | 69 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1865.5831 | 305 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1026 | 120 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 62.7 | 38 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1674 | 270 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 136.0333 | 154 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.4372 | 418.65 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 622.9012 | 30.71 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1545.3333 | 95 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13346.6665 | 220 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | D1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5400 | 675 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 100-Fossil-Steam
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 241.536 | 100.64 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 650-Fluidized Bed
0110 | Other coal fuel supply problems up through bunkers | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 13406.2331 | 769 | 1 | 1 | 0110-Other coal fuel supply problems up through bunkers | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 26.35 | 5.27 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 502.24 | 14.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 73.1167 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 14.7 | 1.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 201.96 | 9.18 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 8.62 | 4.31 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 11.5 | 5.75 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 6763.1666 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 214.9 | 30.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 2304.7 | 6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 14.9333 | 7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 29.93 | 8.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 51.12 | 17.04 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 5128.88 | 24.4 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 46.72 | 23.36 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 56.2467 | 2.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.54 | 2.77 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 9.6 | 9.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 337.5 | 37.5 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 25.32 | 8.44 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 5.2 | 2.6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 35.5138 | 0.37 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 801.1666 | 55 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 6.9 | 1.38 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 28.29 | 2.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 33.3 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2.3 | 2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 387.6855 | 11.59 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 15.56 | 7.78 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 18.09 | 6.03 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 200.3722 | 1.67 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 8.715 | 8.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 13.68 | 6.84 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 125.2733 | 9.2 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.6 | 2.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 142.72 | 12.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 326.5167 | 14.3 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 40 | 10 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 95.06 | 9.8 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 20.1 | 6.7 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 267.8938 | 11.17 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 120.6 | 18 | 1 | 1 | 0111-Solid fuel feeder conveyors | U1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.782 | 0.98 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 52.1192 | 2.21 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 169.4 | 6 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 74.6667 | 32 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 36.68 | 5.24 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 650-Fluidized Bed
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2100 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 173.5 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 314.1667 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 26.25 | 15 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0111 | Solid fuel feeder conveyors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 55.4166 | 25 | 1 | 1 | 0111-Solid fuel feeder conveyors | D1-Forced - Immediate | 800-Miscellaneous
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 62 | 31 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0112 | Solid fuel feed tanks/hoppers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 703.5167 | 22.1 | 1 | 1 | 0112-Solid fuel feed tanks/hoppers | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1403.325 | 24.3 | 1 | 1 | 0113-Solid fuel tank/hopper fires | U1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 403.92 | 15.3 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 2.5667 | 2.8 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 24.6 | 8.2 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0113 | Solid fuel tank/hopper fires | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 33.0733 | 8.2 | 1 | 1 | 0113-Solid fuel tank/hopper fires | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.6 | 4.2 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.1 | 6.1 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 27.5 | 5.5 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10.8 | 5.4 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 229.2 | 72 | 1 | 1 | 0114-Solid fuel volumetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0114 | Solid fuel volumetric feeder | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 962 | 52 | 1 | 1 | 0114-Solid fuel volumetric feeder | D2-Forced - Delayed | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 907.2895 | 37.83 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 278.6666 | 55 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 329 | 47 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 270 | 54 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 16 | 20 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 137.5 | 11 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 28.6167 | 17 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 128.25 | 57 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D1-Forced - Immediate | 650-Fluidized Bed
0115 | Solid fuel gravimetric feeder | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1670 | 10 | 1 | 1 | 0115-Solid fuel gravimetric feeder | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0116 | Solid fuel feeder motors | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 249.9683 | 8.3 | 1 | 1 | 0116-Solid fuel feeder motors | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 10 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 11.4 | 3.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 79.17 | 2.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 18 | 3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 28.7 | 12.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 52.16 | 0.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 53.65 | 5.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 728.715 | 11.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 14.02 | 7.01 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 152.7167 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 5.6 | 1.4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 28.65 | 1.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 695.7383 | 16.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 73.8 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Off-Peak | 295.68 | 12.32 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 513.0417 | 17.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 99.2 | 24.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 18.9333 | 7.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 217.5475 | 25.95 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 20.3967 | 5.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 22.1 | 17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 868.49 | 1.9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 67.875 | 18.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 20.7733 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 119.6583 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1035.1133 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 180.9867 | 2.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 877.455 | 15.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9.1 | 1.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 72.3483 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 157.7 | 19 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2.6517 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 95.205 | 3.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 121.1867 | 0.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 28.5 | 1.9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | TRE | Summer | 603.1666 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1098.765 | 24.3 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 156.8933 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 29.415 | 5.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3.69 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3.9 | 1.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 13.9717 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Winter | 7.3667 | 22.1 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 765.675 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 69.875 | 3.9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 10.29 | 1.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 11.7 | 1.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 12.8 | 1.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 15.92 | 7.96 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 47.04 | 3.36 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 111.93 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 141.6 | 4.8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 6.9517 | 4.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 264.88 | 14.19 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 264.94 | 15.6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 249.0067 | 8.2 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 83.9 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 86.1817 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Winter | 24.81 | 8.27 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 58.2383 | 8.3 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2268 | 7 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 305.25 | 55 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1312.2 | 24.3 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 650-Fluidized Bed
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 97.3333 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 280 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 835.4167 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 14.9 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 205.8333 | 10 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 113.6 | 32 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 181.8333 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 17.2666 | 25.9 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 34.5833 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 791.45 | 33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 584.5667 | 13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 48.1833 | 24.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 206.925 | 4.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 296.3333 | 17.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 97.8 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 13.65 | 13 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 80.3 | 33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 169.2 | 18 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 168.3 | 8.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 150.3667 | 26 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 152.9 | 22 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 417.6333 | 22 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 701.6667 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 40.145 | 25.9 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 687.5 | 33 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 148.0833 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 39.9167 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 66.5 | 17.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 141.4 | 12 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 245.8333 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 97.5333 | 7 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 59.5 | 17 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 22.4167 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 184 | 32 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 58.4 | 4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 80.9333 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1079.9167 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 15 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 61.6 | 16 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 20.125 | 10.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 571.2 | 18 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 196.9583 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 273.2917 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 121.6667 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 43.75 | 15 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 51.3333 | 14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 551.6667 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 227.3667 | 38 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 68.85 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 83.1667 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 423.8333 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 28.7583 | 8.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 235.2167 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 332.9333 | 22 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 261.3333 | 28 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 26.4167 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 136.8 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 261.45 | 21 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 752 | 24 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 829.75 | 15 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 477.6 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D2 | Forced - Delayed | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 151.9167 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D2-Forced - Delayed | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 21.0833 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 608.75 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1214.1667 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 25.6667 | 11 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 40.25 | 5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 143.9 | 6 | 1 | 2 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 325.2833 | 29 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 669.1667 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 39.3 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 93.6 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 29.3533 | 25.9 | 1 | 1 | 0121-Other solid fuel feed problems | U1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 270.25 | 23 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 462 | 21 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 167.8833 | 7 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 197.8 | 23 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 293.0667 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 53 | 20 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 852.5 | 15 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 75.6 | 8 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 4398.3 | 18 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | NULL | NULL | 800 | Miscellaneous | NPCC | Winter | NULL | NULL | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 524.75 | 15 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 76.3 | 6 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 48.4167 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 179.9583 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 10.7333 | 7 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 179.4333 | 14 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 733.35 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 367.9333 | 4 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 146.85 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 45.2833 | 6.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 65.7083 | 2.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 94.35 | 25.5 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 50.8333 | 25 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0121 | Other solid fuel feed problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 1155.6 | 9 | 1 | 1 | 0121-Other solid fuel feed problems | D1-Forced - Immediate | 800-Miscellaneous
0125 | Coal crusher dryer hammers | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4352.8331 | 287 | 1 | 1 | 0125-Coal crusher dryer hammers | D1-Forced - Immediate | 100-Fossil-Steam
0127 | Other coal crusher dryer problems (see code 0106) | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 418.8 | 72 | 1 | 1 | 0127-Other coal crusher dryer problems (see code 0106) | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.3333 | 85 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 86.1666 | 110 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 201.8333 | 35 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 201.6332 | 263 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 250.1665 | 190 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2564.0531 | 282.8 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1406.2 | 89 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 618.35 | 149 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2203.1998 | 243 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 112 | 60 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 100-Fossil-Steam
0129 | Other coal processing system problems | Boiler | Boiler Fuel Supply to Bunker | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 453.9165 | 419 | 1 | 1 | 0129-Other coal processing system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0156 | Other sorbent feed problems | Boiler | Sorbent Supply (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 787.35 | 87 | 1 | 1 | 0156-Other sorbent feed problems | D1-Forced - Immediate | 650-Fluidized Bed
0163 | Bed material feeders | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 5.728 | 0.64 | 1 | 1 | 0163-Bed material feeders | D1-Forced - Immediate | 650-Fluidized Bed
0164 | Bed material feeder motors | Boiler | Bed Material Preparation System (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 18.4 | 16 | 1 | 1 | 0164-Bed material feeder motors | D1-Forced - Immediate | 800-Miscellaneous
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 626.85 | 179.1 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1808.4 | 264 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2321.6 | 96 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D3-Forced - Postponed | 100-Fossil-Steam
0200 | Pulverizer exhauster fan (for indirect firing) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12248.26 | 75.7 | 1 | 1 | 0200-Pulverizer exhauster fan (for indirect firing) | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1897 | 42 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 591.9316 | 79.1 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7346.21 | 134.3 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 477 | 90 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2708.1 | 100.3 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4105.1032 | 134.3 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D1-Forced - Immediate | 100-Fossil-Steam
0205 | Pulverizer exhauster fan drive | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1412.6 | 42 | 1 | 1 | 0205-Pulverizer exhauster fan drive | D2-Forced - Delayed | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 594.3 | 198.1 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 269.3166 | 124.3 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4140.2666 | 112 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 114.0627 | 22.22 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 862.4 | 539 | 1 | 1 | 0240-Pulverized coal bin | U1-Forced - Immediate | 100-Fossil-Steam
0240 | Pulverized coal bin | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 819 | 91 | 1 | 1 | 0240-Pulverized coal bin | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107.1833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 269.4667 | 47 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 278.3816 | 283.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 399 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 717.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 853.125 | 227.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3450.2666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33639.9915 | 293.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.4166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.35 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96 | 72 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 96.1066 | 90.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 169.845 | 60.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 445.8899 | 80.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 497.9333 | 106.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1044.9999 | 165 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1714.1666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70.938 | 202.68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 79.1633 | 25.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 118.9366 | 115.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 181.9999 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 256.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 903.805 | 65.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 952 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 59.15 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7 | 21 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16.5 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 366.8332 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 368 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 602.0833 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 955.1667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 46 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 168.75 | 125 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207 | 23 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 118 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.7833 | 77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 86.8 | 62 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2612.0166 | 53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 409.53 | 80.3 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 231.8333 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 183.6833 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.8666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.2 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 118.125 | 262.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 170.905 | 39.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 220.5082 | 281.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 299.725 | 63.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 473.9582 | 162.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 619.0833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 657.0666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2002.9149 | 152.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.3333 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.9 | 50.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 61.0665 | 229 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88.8333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.1333 | 51.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 124 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125.4 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186.7032 | 141.8 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 197.5 | 158 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 288 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 304.5 | 203 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 337.3666 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 455.7666 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 921.9166 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1588.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1705 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 116.8119 | 92.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 236.2499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 311.6666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 437 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 463.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 540 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 638.65 | 241 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 850 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 859.845 | 129.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 926.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3450 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29.4833 | 29 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.25 | 41 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 688.5999 | 132 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.97 | 7.71 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 53.325 | 106.65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.25 | 205 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 196.6666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 444.8333 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 458.25 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 628.9333 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1771.9666 | 106 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.2347 | 15.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.6666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.45 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.1 | 35.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 117.7832 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.5 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 484.9847 | 19.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 617.2666 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 741.4166 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23.31 | 5.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 243.8333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 477 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 538.3333 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 900 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1603.8665 | 184 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2325.1065 | 420.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1257.4166 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 253 | 12 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 40 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3316.815 | 71.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 856 | 107 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.8 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 97.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 108.5333 | 148 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 206.8176 | 151.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 232.3332 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 290.3333 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 682.541 | 76.69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 742.8749 | 157.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.105 | 9.9 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.0983 | 70.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64.6666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201.0833 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 207.7333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 227.5 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.7832 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 590.0833 | 73 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 743.4666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 762.5 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2237.1999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12886.4499 | 291 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.0727 | 22.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22.2191 | 102.55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.3833 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.9466 | 32.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 139.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 157.7333 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 158.3333 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 316.35 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 520.64 | 260.32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 850 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1595 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1651.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 146.9 | 113 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 584 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 997.5 | 105 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13.05 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 133.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 396.4166 | 71 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 520 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 222.6 | 106 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 491.0666 | 254 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 858 | 130 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 70 | 10 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 144.1333 | 46 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1171.0833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49.5833 | 25 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 610.4999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1446.6665 | 560 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15.2166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.05 | 84.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141.1666 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 159.0833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 180 | 120 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 208.8 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 242.9666 | 197 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 250 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306.1333 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 993.25 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9590 | 280 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 15562.9333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14.835 | 38.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44.45 | 38.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.7499 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124.7 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.6 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 582.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 794.4 | 331 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1037.7666 | 326 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1529.1666 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2974.6 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.2573 | 22.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97.5333 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348.3333 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 407.9999 | 306 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 536 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 969 | 102 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1259.3 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2146.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 193.5 | 86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 314.5 | 17 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 898.9166 | 67 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 94.6 | 129 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132 | 22 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4983.7666 | 182 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2865.4166 | 115 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 440.183 | 539 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.935 | 50.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 120.7499 | 157.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 291.45 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 530 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 543.4332 | 137 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 550.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 599.2666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 604.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 729.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1642.5333 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1708.3332 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.6666 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.9333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.3166 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 263.75 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 265.95 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 372.5999 | 243 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 514.267 | 60.86 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1491.2333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3516 | 293 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 220.8333 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 254.2333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 335.8 | 138 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 471.625 | 122.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 477.4 | 65.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 925.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1141 | 32.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 27 | 36 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1673.9164 | 379 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 684.4 | 116 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 388.8 | 72 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22650 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.996 | 22.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 68.9999 | 207 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 85.2 | 142 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 89.9166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250.8 | 76 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 337.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 430.4999 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 684.5832 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 911.7216 | 106.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5290.8331 | 350 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14847 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.25 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 97.3666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 216.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 253.5 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 331.7666 | 269 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 336 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 640.6666 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 732.1233 | 90.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 832 | 32 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3834 | 270 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.054 | 87.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.5 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 218.6666 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 250.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 250.8333 | 175 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 315 | 210 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 629.4166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6401.6332 | 134.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5270.4998 | 249 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 56 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 921.5 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 81 | 54 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 85 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | NULL | NULL | 100 | Fossil-Steam | SERC | Winter | NULL | NULL | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 325.2666 | 164 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 69.4167 | 35 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 654 | 21.8 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 646.65 | 81 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 678.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.5333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 950.4 | 108 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 395.85 | 63 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 898.9666 | 149 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 24.7997 | 25.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30.3166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.5 | 18 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70.6971 | 146.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 82.4999 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 474 | 316 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1213.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2049.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4.2 | 7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10.75 | 15 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.0203 | 42.62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 33 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 35.5333 | 106.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 253 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 275.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 380.25 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 903.3533 | 75.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1940 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2968.7366 | 80.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 108.99 | 36.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 132.8375 | 106.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 143.4999 | 246 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 236 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 692.55 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1766.75 | 191 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1980 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2779.1833 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4301.8 | 314 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 193.6 | 121 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 235 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 132 | 66 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 159.6 | 57 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 688.3333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2064.9866 | 84.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2664.9385 | 155.39 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 370.4166 | 127 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 435.0666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 169.1667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.1333 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 186 | 186 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 376.4833 | 49 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 426.25 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 615.9999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2708.2999 | 159 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4394.9999 | 180 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23076.55 | 147 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.35 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 169.75 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194.3999 | 182.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 213.75 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.0666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391.5 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 395.0366 | 320.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1582.35 | 231 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 225.0083 | 87.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 286.6666 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 565.5 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 795.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 55.25 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 71.5 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 978.6666 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 248.3999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 323.3999 | 99 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 447.7666 | 101 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 306.9005 | 242.29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 602.5999 | 276 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4599.4665 | 196 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28.6 | 26 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 201.1666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25.6667 | 35 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6079.6666 | 260 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22.75 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.6 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.6346 | 162.44 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.7499 | 285 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 175.9999 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.4165 | 193 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1017.3332 | 140 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3838.9333 | 94.4 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9798.75 | 335 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.8833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.5 | 129 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 115.0825 | 106.23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1305.2373 | 78.08 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2010 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3515.6 | 188 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34.5833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49.8 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 228.99 | 76.33 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 291.28 | 99.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 500 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 552.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 686 | 245 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1033.6833 | 109 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.55 | 39 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 238.1333 | 94 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 116 | 16 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165.3166 | 91 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 169.4166 | 107 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 837.5833 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 49.5 | 16.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 189.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 311.6 | 4.1 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 694.1666 | 350 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1266.3499 | 93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11340 | 420 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.5666 | 127 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 175261.5 | 765 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18.5167 | 22.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23.037 | 65.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49.5833 | 106.25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 75.04 | 40.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 80.2333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 100.2916 | 207.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 118.5 | 79 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.4 | 182 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 150 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 172.05 | 111 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 263.2 | 28 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 402.5 | 69 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 468 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 714.8499 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 801.1333 | 122 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1489.8999 | 141 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2235 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2351.6666 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.8333 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.4333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114.7833 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185.2499 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206 | 41.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 330.3999 | 168 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 346.8 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 451.23 | 80.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 472.5832 | 265 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 613.6666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 637.2 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3667.1332 | 268 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8379 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13478 | 293 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18153.9097 | 31.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95.7016 | 63.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 751.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1884 | 157 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 44.3333 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 42.4 | 10.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 49.1666 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2217.7766 | 56.6 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48.05 | 31 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1043.0999 | 164.7 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 51.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176 | 30 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 206.2666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 295.5166 | 149 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 149.45 | 49 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 169.1666 | 70 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 784 | 280 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44.135 | 25.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71.82 | 102.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 130.1666 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 198.0415 | 242.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 314.6666 | 59 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 349.45 | 241 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.2 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458.3333 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 627.9 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 637.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 946.35 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1380 | 103.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1504 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4344 | 181 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5022.48 | 81.6 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 96.25 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.5 | 174 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 168.8666 | 149 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 313.1333 | 77 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 313.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 388.1333 | 82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 522.5 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 714.0833 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 810 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 872.1 | 171 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.7499 | 75 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 86.2499 | 207 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 89.4666 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 187.05 | 87 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 630 | 90 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 646 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 857.3666 | 89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 975 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1010 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1719.9999 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4989.4498 | 261 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26789.3333 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 388.5333 | 62 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 75 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 166.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 200 | 96 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 78.7833 | 163 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.05 | 24.55 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 653.3 | 278 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 109.7 | 109.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 140.5333 | 136 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 265 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 310.4999 | 162 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 314.3333 | 92 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 603.75 | 115 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1188.5833 | 85 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1979.5 | 214 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2200 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8904.1665 | 250 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.595 | 37.19 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62.6673 | 30.82 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.3666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.5667 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.24 | 195.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 377.9999 | 81 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 560 | 112 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671.505 | 80.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1026 | 95 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1069.8333 | 122.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1553.6665 | 295 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2585.3 | 206 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.7166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 66 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 166 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 202.9167 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.1349 | 83.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 252.4829 | 98.37 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 4737.6 | 288 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 338 | 130 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 90 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 339.1667 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 199.9999 | 120 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 80.85 | 147 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 245.1166 | 77 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 137.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.5333 | 28 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1634.1666 | 53 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2.3333 | 20 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35.5666 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 48.5 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.0365 | 156.43 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98 | 56 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.5 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 218.25 | 97 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.3332 | 200 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 470.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 795 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1608 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1672.1249 | 157.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.5177 | 15.22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.3366 | 33.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.1 | 126 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.2249 | 106.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 222.3 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 440.2667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 715.8666 | 104 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1929.3049 | 83.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10538.4 | 144 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11.8242 | 20.27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 22.5 | 25 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 66.4 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 353.8333 | 55 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361 | 60 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 568.3333 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 652.6666 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2003.8749 | 127.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2128.5 | 110 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 145.75 | 53 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 698.5 | 22 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 826.6666 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 450.1166 | 113 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 908.96 | 34.96 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2186.2499 | 225 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 249.55 | 93 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 354 | 59 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1420.25 | 247 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27891 | 60 | 1 | 1 | 0250-Pulverizer feeders | D3-Forced - Postponed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 21.1 | 422 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10.5 | 10 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25 | 25 | 1 | 2 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.1666 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 81.1486 | 173.89 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.5 | 70 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143.7333 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 173.6916 | 109.7 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.4999 | 247.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 260.4583 | 117.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 279.433 | 294.14 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 335 | 134 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 340.0833 | 35 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 399.5 | 117.5 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 450 | 150 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1430.38 | 120.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2033.3433 | 164.2 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2435.225 | 165.1 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3840 | 240 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6580 | 120 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 16.5 | 45 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.95 | 65.3 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.2 | 176 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.8 | 84 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224.3666 | 127 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 293.4 | 27 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 514 | 257 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 598 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 648.7833 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 880.3666 | 98 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2026.6666 | 160 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 47.5 | 50 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 128 | 64 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 153 | 51 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 218.0333 | 211 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 419.25 | 195 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 420.8333 | 125 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 680 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1144.6666 | 170 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19450 | 100 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 677.0833 | 65 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1441.5 | 155 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 66.0833 | 61 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 216.6667 | 26 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 42.4666 | 52 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1357.2 | 18.85 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4363.0333 | 166 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 38.1833 | 29 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3952 | 30.4 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 188.4166 | 95 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 427.35 | 111 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 772.5665 | 539 | 1 | 1 | 0250-Pulverizer feeders | U1-Forced - Immediate | 100-Fossil-Steam
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 976.6333 | 83 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 10533.6 | 88 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 3 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1715.8666 | 68 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 57.6667 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 309.3999 | 78 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 117.3333 | 80 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 64 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 173.3333 | 40 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 53.5 | 30 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 239.7333 | 58 | 1 | 1 | 0250-Pulverizer feeders | D2-Forced - Delayed | 650-Fluidized Bed
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 624 | 20 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 800-Miscellaneous
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 29862 | 63 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Winter | 3036 | 23 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 23294 | 38 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0250 | Pulverizer feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 768 | 48 | 1 | 1 | 0250-Pulverizer feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1068.6517 | 46.7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 150.75 | 60.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3400 | 170 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15.5167 | 19 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7 | 7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 45.8333 | 10 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1143.25 | 85 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1210 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 240.7716 | 25.3 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 114.3333 | 28 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.1667 | 38 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3472 | 112 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 983.4413 | 513.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5661.3333 | 80 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.1 | 38 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1860.64 | 80.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 279.9999 | 210 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 351.345 | 53.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 614.5 | 30 | 1 | 1 | 0253-Pulverizer feeder motor | D2-Forced - Delayed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2300.1032 | 160.1 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2851.8166 | 139 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 618.8333 | 94 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 690.75 | 307 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20965.095 | 160.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 56.7 | 56.7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.765 | 56.7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70.5 | 94 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1185 | 60 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 261.5666 | 118 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2100 | 210 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4716.7 | 202 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4239.9066 | 80.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 295.0933 | 110.66 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5907 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1.2166 | 73 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.7133 | 170.2 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1474.2 | 84 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 27.2166 | 71 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.5 | 50 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1171.51 | 60.7 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.5 | 151.5 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 159.825 | 106.55 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 487.6666 | 110 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7080.1 | 70.1 | 1 | 1 | 0253-Pulverizer feeder motor | D1-Forced - Immediate | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 526591.2 | 70.1 | 1 | 1 | 0253-Pulverizer feeder motor | D3-Forced - Postponed | 100-Fossil-Steam
0253 | Pulverizer feeder motor | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13501.3332 | 415 | 1 | 1 | 0253-Pulverizer feeder motor | U2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3649 | 178 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 272 | 17 | 1 | 1 | 0255-Pulverizer feeder coal scales | D1-Forced - Immediate | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 317.3333 | 160 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0255 | Pulverizer feeder coal scales | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1145.2666 | 164 | 1 | 1 | 0255-Pulverizer feeder coal scales | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2879.1999 | 177 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 113.58 | 63.1 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 56941.3165 | 473 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 658.5661 | 859 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 871.5 | 415 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6661.7165 | 193 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 68.25 | 117 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 285 | 95 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 98355.4 | 836 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2673.75 | 155 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 306.9582 | 132.5 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.0833 | 41 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 291.3933 | 80.2 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 68150.3996 | 576 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1777.2666 | 106 | 1 | 1 | 0256-Seal air system (air to pulverizers) | U1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 277.6667 | 35 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.5 | 110 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D1-Forced - Immediate | 100-Fossil-Steam
0256 | Seal air system (air to pulverizers) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 153.75 | 75 | 1 | 1 | 0256-Seal air system (air to pulverizers) | D2-Forced - Delayed | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 896.4166 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1593.9166 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 646.767 | 130.66 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 766.6833 | 157 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0257 | Coal Crusher/dryer between feeder and pulverizer | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1035.9166 | 155 | 1 | 1 | 0257-Coal Crusher/dryer between feeder and pulverizer | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3210.9 | 278 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28105.2 | 148 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.6667 | 20 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 91.3 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15.1667 | 13 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2916.8332 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67.5 | 30 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3782.66 | 13.18 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3779.35 | 577 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26771.4 | 417 | 1 | 1 | 0260-Primary air fan | U2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91.3333 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2001 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2152.75 | 32.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4917.4 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29002.9353 | 79.54 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1462.5 | 117 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7163 | 65 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4170 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6801.5 | 30 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4089.8 | 286 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 102 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165.85 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6084.733 | 428 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7523.3332 | 370 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 157.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 205 | 41 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 235.4167 | 25 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1911 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9365.9998 | 360 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.5 | 26 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 193.3333 | 29 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34741.6666 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 800 | 200 | 1 | 1 | 0260-Primary air fan | D3-Forced - Postponed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3186 | 29.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 719.8999 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8574.9999 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 203 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.3333 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.3333 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 642.15 | 14.27 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 841.7333 | 107 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68962 | 410 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 445.8666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 592.6666 | 28 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8466.1665 | 395 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18274.833 | 551 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 301 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 18000.4998 | 555 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1286.8666 | 194 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 17833.5 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 39752.9999 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 65 | 20 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141 | 23.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33107.3661 | 841 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100.2666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4339.5 | 526 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5543 | 241 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 170.4 | 24 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1745.9 | 158 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 84 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 826.7666 | 34 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1108.08 | 41.04 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3595.6 | 40.4 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.8 | 12 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7041.8333 | 55 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 93.7333 | 148 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 114.4 | 143 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 657.7999 | 138 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1646.4998 | 267 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18881.3329 | 680 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 292.2666 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1273.6 | 128 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 282 | 94 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1602.9667 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1683 | 340 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 9.9 | 18 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.75 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 532.98 | 29.61 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1224.78 | 8.22 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.4333 | 38 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1193.7333 | 56 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.3998 | 231 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4778.3 | 142 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12402.6998 | 254.85 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136.98 | 7.61 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 467.1 | 17.3 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2223.88 | 41.96 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 28.5333 | 16 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67716.3995 | 762 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 773.3 | 66 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4787.9999 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 110.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 693.3331 | 320 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 914.9999 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1237.1333 | 77 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2137.7499 | 255 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 280 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2519.7 | 111 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 310.6883 | 28.46 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 214 | 40 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 412.5 | 33 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1000.8 | 41.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2448 | 27.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15131.2666 | 263 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.6667 | 26 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 398.9333 | 64 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 424.7333 | 92 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 620 | 155 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1669.7999 | 207 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2157.3 | 27 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8060.0582 | 231.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.1666 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 504 | 21 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 610.5 | 55.5 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722 | 19 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 918.14 | 15.83 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2849 | 259 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4223 | 410 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 221.65 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.25 | 35 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1641.0333 | 91 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2370.2498 | 285 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2819.5663 | 502 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3187.4999 | 450 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 456 | 480 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5628.3333 | 110 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10125 | 150 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 40891.5 | 270 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.1666 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.3333 | 40 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 931.04 | 73.6 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.025 | 40.5 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15372.333 | 431 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9166.9999 | 267 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.9933 | 40.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.06 | 16.2 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 167.6333 | 107 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1974.6666 | 40 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 948.2 | 44 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 517.5 | 90 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5100.9 | 34.7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6.2 | 31 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 541.7333 | 136 | 1 | 1 | 0260-Primary air fan | D2-Forced - Delayed | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 759.5 | 86.8 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.835 | 488.1 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 100-Fossil-Steam
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3086.1 | 24.3 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1.8667 | 7 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 93.555 | 24.3 | 1 | 1 | 0260-Primary air fan | U1-Forced - Immediate | 650-Fluidized Bed
0260 | Primary air fan | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 429.2833 | 43 | 1 | 1 | 0260-Primary air fan | D1-Forced - Immediate | 800-Miscellaneous
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 579.6998 | 561 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 761.45 | 157 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 328.1599 | 246.12 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6989.9999 | 450 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 755 | 20 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 138 | 138 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0262 | Primary air fan lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7985.7 | 342 | 1 | 1 | 0262-Primary air fan lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 63.7 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.0833 | 118.9 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.4997 | 450 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 176.8666 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 185.0333 | 26 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2368.9162 | 655 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 59.2666 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2749.3 | 28.94 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4650.6666 | 160 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 54.99 | 18.33 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 382.08 | 15.92 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 247.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70 | 30 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 215.1333 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 370 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 791 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 292.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62 | 30 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1749.3331 | 820 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 25872.5 | 655 | 1 | 1 | 0263-Primary air fan drives | U2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 952 | 17 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3449.6662 | 655 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129.7333 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 720 | 180 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 8910.5833 | 115 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6337.3333 | 40 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 80.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 318 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 92.4 | 28 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 235.5 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.7667 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 176.6666 | 100 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 406.21 | 8.29 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 675 | 900 | 1 | 1 | 0263-Primary air fan drives | U1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 55.0333 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66 | 132 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.9333 | 26 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 399 | 30 | 1 | 1 | 0263-Primary air fan drives | D1-Forced - Immediate | 100-Fossil-Steam
0263 | Primary air fan drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 207 | 34.5 | 1 | 1 | 0263-Primary air fan drives | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15572.6666 | 131.6 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19888.76 | 63.34 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2373 | 565 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2661.9998 | 660 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 565.95 | 231 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1713.7498 | 225 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1148.8331 | 565 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 126.5833 | 35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 11189.9999 | 225 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 175 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4450.4166 | 275 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 40591.7499 | 255 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.2999 | 339 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4496.6666 | 200 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 391.3 | 91 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1209 | 31 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6252 | 3.13 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325.3219 | 168.27 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1750.875 | 33.35 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5115 | 31 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 35060.7833 | 91 | 1 | 1 | 0264-Other primary air fan problems | D2-Forced - Delayed | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 46.25 | 25 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1871.88 | 32.84 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8097.5 | 395 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1792 | 112 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 350 | 250 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15230.8332 | 490 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 203.5333 | 71 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2044.5 | 235 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 860.25 | 31 | 1 | 1 | 0264-Other primary air fan problems | D1-Forced - Immediate | 100-Fossil-Steam
0264 | Other primary air fan problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 2688.795 | 24.3 | 1 | 1 | 0264-Other primary air fan problems | U1-Forced - Immediate | 650-Fluidized Bed
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 229.5833 | 47.5 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19791.4998 | 690 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 5135 | 395 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8435.3998 | 306 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 698.3166 | 293 | 1 | 1 | 0265-Primary air heater | D2-Forced - Delayed | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 150 | 150 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1406.4 | 293 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51367.4999 | 405 | 1 | 1 | 0265-Primary air heater | U1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 338.3333 | 87.5 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 100-Fossil-Steam
0265 | Primary air heater | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 39.7833 | 11 | 1 | 1 | 0265-Primary air heater | D1-Forced - Immediate | 800-Miscellaneous
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 10.5 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6666 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.3333 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1548.2499 | 82.5 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1403.3832 | 523 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 528 | 132 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 180.5 | 30 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 435 | 435 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2713.6666 | 140 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2368.2116 | 70.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.5833 | 95 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6683.7331 | 416 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7585.0665 | 416 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1585.7512 | 630.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 235.4 | 33 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34.0666 | 28 | 1 | 1 | 0267-Primary air flow instrumentation | D2-Forced - Delayed | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1133.1663 | 523 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 374.17 | 220.1 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31.3333 | 40 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 940.5 | 114 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1290.0663 | 523 | 1 | 1 | 0267-Primary air flow instrumentation | U1-Forced - Immediate | 100-Fossil-Steam
0267 | Primary air flow instrumentation | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 343.1999 | 198 | 1 | 1 | 0267-Primary air flow instrumentation | D1-Forced - Immediate | 650-Fluidized Bed
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184.9167 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1523.5 | 110 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 146.25 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 242.55 | 33 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 758.3332 | 140 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1230 | 72 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 102.2667 | 26 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 243.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2437.5 | 130 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240 | 24 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 251.8167 | 29 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6219.5832 | 275 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 111 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.6667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 307.8833 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.8333 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 991.6665 | 500 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.4 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2588.25 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3031.4666 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 313.6 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 891.5016 | 320.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 104.8319 | 120.96 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1979.4499 | 183 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1140 | 380 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1338 | 446 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1339.8 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1515.05 | 157 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 50295.7 | 182 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 350 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1048.32 | 70.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3949.6295 | 134.57 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 54.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1049.95 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2032.1166 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 15069.95 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13311.6666 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 882 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4639.9999 | 240 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23653.4411 | 347.93 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 95.1 | 95.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 265.5 | 59 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 393.3 | 57 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 595.9599 | 95.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 256.64 | 80.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 354.65 | 41 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1900 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 70 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 247.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.1667 | 5 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1764.105 | 95.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405.3833 | 13 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 804.9667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 557.75 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 450 | 125 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 259.1423 | 130.66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2619.7332 | 256 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3902.5 | 35 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29 | 20 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 190.855 | 93.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 361.05 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 106.2 | 53.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 280 | 70 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 388.7166 | 83 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 585 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29 | 14.5 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 585.8333 | 95 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 883.8233 | 182.86 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1306.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.8666 | 28 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1569.75 | 455 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2190.8331 | 275 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.6 | 12 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.75 | 15 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.08 | 10.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 70.1333 | 105.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 673.8667 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 63.75 | 51 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 115.5316 | 67.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 348.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1958.7332 | 267.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5773.75 | 75 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42.4333 | 38 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 162.5333 | 46 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 54.1666 | 65 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 312.4789 | 210.66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 842.6665 | 395 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1402.5 | 66 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.05 | 123 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 566.6665 | 250 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 638 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 527.5666 | 49 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 235.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 341.3333 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1378.3333 | 100 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2652.2083 | 120.1 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1200 | 60 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15750.9333 | 56 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.106 | 170.53 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 69.85 | 127 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 418.0999 | 339 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.12 | 40.3 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 116.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1771.4666 | 182 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288.75 | 275 | 1 | 1 | 0270-Primary air duct and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.3333 | 10 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 577.15 | 97 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.5066 | 140.2 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385.047 | 21.94 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 34.6666 | 40 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 42611.9 | 101 | 1 | 1 | 0270-Primary air duct and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 359.3333 | 98 | 1 | 1 | 0270-Primary air duct and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.2 | 24 | 1 | 1 | 0270-Primary air duct and dampers | D3-Forced - Postponed | 100-Fossil-Steam
0270 | Primary air duct and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20770.75 | 415 | 1 | 1 | 0270-Primary air duct and dampers | U2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.4331 | 386 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 804.1665 | 386 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6787.1665 | 386 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1343.0832 | 227 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1707 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 624.15 | 65.7 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 114 | 45 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4707 | 180 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1932 | 69 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15349.3333 | 64 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 68.85 | 81 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 693.7883 | 92.3 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5759.8899 | 95.1 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5284.5 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 88570.0833 | 123.5 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 22 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59.3333 | 40 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3460.1666 | 130 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 322.9166 | 155 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 396.1499 | 171 | 1 | 1 | 0280-Pulverizer fires | D2-Forced - Delayed | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 712.5 | 95 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10 | 60 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 661.5 | 490 | 1 | 1 | 0280-Pulverizer fires | D1-Forced - Immediate | 100-Fossil-Steam
0280 | Pulverizer fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4153.3332 | 280 | 1 | 1 | 0280-Pulverizer fires | U1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3344 | 88 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 189 | 14 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33432.0833 | 205 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36941.2499 | 225 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 100-Fossil-Steam
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 13480 | 25 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0290 | Pulverizer reduced capacity due to wear | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 217439.1 | 261 | 1 | 1 | 0290-Pulverizer reduced capacity due to wear | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7520 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16354.25 | 209 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 133.75 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 187.5 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 829.25 | 155 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1399.9166 | 157 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3441.4333 | 98 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2238.5 | 55 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 83.0167 | 17 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 279.5 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10846.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7779.6333 | 169 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 127.6667 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 716 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 742.0333 | 226 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3039.3333 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2445.0683 | 60.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1164.2666 | 296 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 331.5 | 90 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 31.4166 | 65 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1170 | 45 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 225 | 75 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3360 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 126.8999 | 81 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4580.7127 | 15.22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.6 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 76.25 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6.5 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.665 | 110.66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 305 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 756.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 165.9 | 63 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3542.2331 | 323 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13090.35 | 39 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 436 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1920 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2465.75 | 105 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 724.3499 | 395.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 47.5 | 25 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.95 | 61 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 411.6666 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 654.55 | 247 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 307.1666 | 97 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 397.5 | 150 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75.1333 | 28 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 391.05 | 33 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1263.0516 | 63.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8329.0833 | 127 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129 | 21.5 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0.16666 | 10 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1141.3333 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4262.55 | 157 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.6666 | 85 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 514.6666 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 900 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 333.7499 | 80.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 854.13 | 80.2 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4831.3649 | 80.1 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 524.6 | 86 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.98 | 22.33 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 260.3333 | 110 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 307.4417 | 46.7 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 890.75 | 35 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141.9164 | 340.6 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.7333 | 38 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205.2 | 81 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4093.2 | 216 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.3333 | 100 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4822.5 | 50 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13077.9 | 66 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.6667 | 20 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9786.6666 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 233.6666 | 140.2 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31.5 | 30 | 1 | 1 | 0300-Pulverizer motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 380.265 | 75.3 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1176.9998 | 330 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6342 | 40 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.4667 | 22 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 477.3333 | 80 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 271.8332 | 233 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0300 | Pulverizer motors and drives | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4060.2665 | 368 | 1 | 1 | 0300-Pulverizer motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 84 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 183.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 252 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 256.1166 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 270.6 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 300.15 | 200.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 648 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 871 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 940 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3237.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3705 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7658.3332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 62425 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.5833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 129.1033 | 100.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 201.6 | 27 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 205 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 216.7 | 197 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 227.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.3333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 267.7766 | 119.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.4333 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 307.4833 | 97.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 541.6666 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 637.8166 | 71 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 724 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 737.2749 | 114.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1276 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90989.5666 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.3166 | 45.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 55.9171 | 81.83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 132.55 | 120.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 361.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 449.1666 | 77 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1313.3332 | 400 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1685 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6446.5665 | 178 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 133.3 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176 | 16 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 893.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1881.6 | 19.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2086.55 | 87 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.8333 | 25 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102 | 8.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 145.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 351.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4956 | 35.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 513.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1040.4 | 20.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.7999 | 108 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2931.75 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 185 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 280.4333 | 94 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 198.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 73.8 | 27 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 146.1333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1011.6331 | 682 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 73.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 108 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 121.3333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 189.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202.5 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 450.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 756 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1893 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3922.8666 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4746.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7542.6666 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31120 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88.484 | 120.66 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91.5 | 183 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 483 | 161 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 514.5833 | 47.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 532.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1016.7331 | 302 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2569.75 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3704.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7873.6666 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24385.1285 | 97.21 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 75.7167 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 88.9833 | 56.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 124.8416 | 105.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 133.2 | 111 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 427.5 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1244.9997 | 450 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1743.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5812.5 | 125 | 2 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 46 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 86.8 | 93 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 89.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 94.25 | 87 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 304.2666 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1387.1665 | 410 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 13635.1666 | 115 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 31.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 90.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 99.7333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 367.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 815.8666 | 84.4 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.71 | 191.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 57.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 132.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 310.25 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 404 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 526.3998 | 282 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 576.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 711 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 852 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1148 | 164 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1182.75 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1218 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1503 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1853 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2078.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4748.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8554.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9863.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19616 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32954.9999 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.9833 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 61.5 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 280 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 399.3499 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 590 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 857.6 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1261.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2994.6666 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3352.0833 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3536.25 | 115 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6848 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40745 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64989.3333 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56.0999 | 99 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69.6666 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 74 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.8333 | 121 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 191.3332 | 164 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 348 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 385.6667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 732.6667 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 743.0166 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1933.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4075.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 101.4333 | 34 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 479.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 815.7333 | 46 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1151.2 | 48 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2046.9333 | 64 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.9999 | 75 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 824.5 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 61.95 | 63 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 486.1999 | 102 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 556.9666 | 62 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 156.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1361.115 | 134.1 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 877.0333 | 83 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1271.3633 | 32.2 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 143.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 183.4366 | 97.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.9132 | 239.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 232.2667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 264 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.6 | 29.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 507 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1759.0833 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1817.7 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2194.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 69.9833 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.2666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 198 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 430.1166 | 197 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 459.9999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1005 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1347 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6119.75 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7837 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.1 | 18 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 65.1667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 100.65 | 11 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 124.5 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 326.5333 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 922.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 996.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1062.5 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2091.4833 | 91 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2502.8383 | 93.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56.3333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 261 | 145 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 85.25 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 91.4666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 119.2333 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 23.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 413.8666 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 420.5333 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 648 | 13.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 651 | 18.6 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1053.5 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1071 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1298.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 102.2666 | 104 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 160.9999 | 84 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.8 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 840 | 5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 102 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 141.71 | 114.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.6666 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 250 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 278.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 343 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 458 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 523.5166 | 311 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 535 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 700 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 991.0166 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1104 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1297.8333 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1317.6 | 164.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1628 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1757 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5528.7667 | 23.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5853.9 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6060.4 | 21.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9967.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12067 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44003.5668 | 112.69 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.9999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 157.9998 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 185.9999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 355.3333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 397.1 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1012.7 | 247 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1026.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1045 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1454.9166 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1467.7499 | 171 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1751.75 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3118 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4539.8666 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5032.73 | 164.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57408.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 106.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.6833 | 125.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 248.4166 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 274.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 767 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 794.7499 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 872 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2226.8246 | 54.49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11845.5 | 149 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 49.4666 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.4999 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 225.5666 | 134 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 53.1 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 172 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 49 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 83.65 | 21 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 436.5 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 32423.0666 | 56 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 310.03 | 44.29 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1200 | 45 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 436.3333 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 625.4166 | 79 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 227.05 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 84.9333 | 26 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.8 | 32 | 1 | 2 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 466.1333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 942.4666 | 84.4 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1679.2083 | 95.5 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64147.6997 | 762 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 33 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 71 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.6 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 164.9666 | 141.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 209.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 210 | 140 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 212.5 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 223.8133 | 119.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 246.5 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 284.35 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 303.975 | 135.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 346.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 443 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 720 | 360 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1188 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1498.84 | 141.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2442.6 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.6666 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 87.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 201.4999 | 195 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 213.5 | 61 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 254.8 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 275 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 317.6333 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1217.3333 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1680 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5444.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30893 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27.3373 | 58.58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 38.6667 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 177.75 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 258.3 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1747.1666 | 95.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5880 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.5333 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 36.9 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1925.3333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.4333 | 38 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 581.4666 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1348.6664 | 340 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9628.0832 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.4667 | 41 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 117.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1117.25 | 205 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80 | 160 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 863.4 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 82.1333 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 157.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46.4 | 58 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 123.6833 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126.6667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 140 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 215.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 257.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 262.5 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 330.75 | 81 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 370.8333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1909.3167 | 21.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1991.4999 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2857.785 | 160.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8016 | 160 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.9166 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.9333 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 154.4333 | 41 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 166.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 215 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 227.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 241.6 | 48 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 264 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319.05 | 106.35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 346.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 421.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 435.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 450 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 496 | 62 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 504 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 517.5 | 450 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 571.9933 | 41.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 620.5 | 51 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14164.5 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 43.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 94.05 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 102.4999 | 75 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 209 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 795.3999 | 291 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2095.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4917.1665 | 181 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.8333 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 66.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99 | 33 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 366.9833 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 685.1 | 40.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1600.6666 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1636.02 | 26.82 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 73.3833 | 37 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 165 | 90 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 106.7 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 123 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 371.2 | 116 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 380.8 | 102 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1680 | 36 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 212.8 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 220.15 | 37 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 346.1333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200.4666 | 31 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 581.25 | 31 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1109.3599 | 84.9 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50754.1664 | 650 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.8333 | 5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.5 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 179.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 244 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276.2666 | 64 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 510.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 597.9583 | 63.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 632 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 850 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1252.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1409.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2275 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3158.75 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4611.6 | 164.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.35 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.3333 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 138.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 158.8933 | 70.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.8467 | 10.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 969.75 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1125.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1222 | 260 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1280.6667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3.9667 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 126.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486.6533 | 32.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 593.8666 | 272 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 175.0666 | 52 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 844.7999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1168.85 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 622.88 | 18.32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1029.37 | 13.03 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1535.5 | 18.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160 | 50 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 557.7333 | 94 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 218 | 20 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.2667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.9333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 425.25 | 405 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4316 | 260 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 37 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 38.25 | 135 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111.0699 | 114.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.2 | 36 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 219.2 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 492.3032 | 261.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 495.8333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 718.6666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 763.0666 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 911.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1188.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1327.333 | 440 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1342 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1461.135 | 69.03 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3922.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4579.8 | 134.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6039.5 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.5333 | 76 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 116.6666 | 125 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 333.3333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 671 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2408 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3301.3499 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15237.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 600.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8493.3333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17419.5 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 188 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 369 | 9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2020.1833 | 53 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2764.8833 | 91 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 432.8333 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1253.7 | 19.9 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2389.2 | 18.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 481.8333 | 98 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 496.5 | 33.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 738 | 120 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2209.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3874.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 149.3333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 879.24 | 129.3 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 128.2166 | 49 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 86.5666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.9333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 101.8383 | 124.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 113.6666 | 124 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.7 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 147 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 183.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240.9167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 272.04 | 680.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304.4166 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 645.0753 | 152.38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1208.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1316.64 | 253.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1508.6666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6398.1666 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.35 | 3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 132.4 | 8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 162.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 314.775 | 139.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 326.0833 | 65 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 336 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 568.9333 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1291.5 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1345.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1892.6666 | 68 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1897.3166 | 79 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2198.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5584 | 120 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7593 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 180.5 | 95 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 760 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9916.6665 | 350 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.5333 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 241.9666 | 122 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.5 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 379.9166 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 29228.6166 | 203 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 408.065 | 26.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1164.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1747.15 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 758.2166 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 426.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46602.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 253.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29200 | 800 | 1 | 1 | 0310-Pulverizer mills | SF-Startup Failure | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 0.99996 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 76.7832 | 271 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 145 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 176 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 183.3333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 193.5832 | 505 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 373 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 756 | 63 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 766.3332 | 209 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 976 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1070.6665 | 220 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1385.5 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1853 | 109 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.3333 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 102.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120.4 | 129 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 206.25 | 165 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 369 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 482.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 656 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3530.8333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9808.5 | 117 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.3333 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.1 | 38.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 53.7333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 103.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 149.45 | 49 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 176 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 193.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 238 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 340 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 460 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2698.6666 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7907.625 | 24.3 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 21165 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.6833 | 53 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 350.1333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 120.8666 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 657 | 30 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1648.1666 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13.8667 | 26 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78 | 13 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 951.78 | 17.4 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2150 | 43 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5033.3332 | 200 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43.9166 | 31 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77.8667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 295.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162.75 | 31 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 25075.5831 | 655 | 1 | 1 | 0310-Pulverizer mills | U3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.3333 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 101.4999 | 210 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 271.25 | 105 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 777.3333 | 80 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 798 | 266 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 908 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1622.5 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1809 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2465.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6014 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9295.8332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 13366.8333 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.0333 | 14 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.0833 | 55 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67.1999 | 144 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 186.6666 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 270 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 318.5 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 500 | 100 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 597 | 199 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 612.2666 | 28 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 670 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 811.3116 | 247.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 859.4333 | 23 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2244 | 170 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5278.1 | 141 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8175 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9634.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 113 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 146 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 189.25 | 15 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 200.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 219.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1354.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1445 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4029.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4091.5 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5381.6667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 264 | 72 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 24.1 | 48.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 91 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 348.5 | 82 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1890 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2209.7 | 57 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 75.7166 | 77 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 83.5833 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 161.25 | 45 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1 | 10 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 98 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 104.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 138.8333 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 173.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 184 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 202 | 40.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.835 | 139.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 429 | 39 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 936.3333 | 26.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1018.3333 | 130 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1092.2 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1876.8 | 36.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2667.4666 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5158.3332 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.5833 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.6666 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.74 | 76.74 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85.5667 | 17 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.6666 | 127 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 257.7666 | 140.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 306 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 714.5832 | 245 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4353.7 | 197 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7291.6666 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 177.0249 | 145.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 187 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 221.8333 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300.9997 | 420 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 902.7666 | 73 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 934.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1202.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1347.1 | 19 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6225 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1081106.5999 | 147 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 181.9999 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 347.9 | 142 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 266.9332 | 143 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 69.7 | 82 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 93.3333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.5 | 90 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 677.1666 | 170 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 712.6 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 756.6 | 97 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1122 | 22 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1349.4 | 17.3 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6698.5417 | 27.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2947.5 | 135 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 69.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 83.5833 | 85 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 317.2 | 104 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 26.6667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 48.0666 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 282.3333 | 28 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28.5 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 96 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 143.9833 | 163 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 172.35 | 114.9 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211.4667 | 26 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 275 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 309.4 | 154.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 422.1166 | 31 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 560.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 593.0667 | 32 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 873 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1073.65 | 21.8 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3920 | 196 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5515.4167 | 35 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8223.75 | 43 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.6666 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.3333 | 40 | 1 | 2 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 76.2666 | 143 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 85.85 | 101 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.5433 | 79.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 196.17 | 100.6 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 260.7999 | 96 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 304.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 304.95 | 107 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.2333 | 166 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 462.5 | 150 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1071 | 119 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1080 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1431 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3092.2999 | 102 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5383.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10064.345 | 106.22 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 68 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1286.5 | 83 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3879.9998 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3884.9999 | 180 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 35.25 | 47 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 181.8 | 54 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.6666 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66 | 13.2 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 137.5 | 125 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 777.92 | 45.76 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1097.2 | 21.1 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 128.5333 | 8 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 188.4166 | 95 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1049.0667 | 32 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 32 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58.1333 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 431.4667 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 254 | 30 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 327.18 | 79.8 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 285.0165 | 244.3 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 158.95 | 33 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 178 | 24 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 208.5333 | 34 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406.9333 | 112 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 537.3333 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 539 | 110 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 557 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 713.9965 | 308.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1008.2667 | 38 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2614.9666 | 98 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7000.6466 | 112.4 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58657.5 | 237 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 357 | 85 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 362.8333 | 70 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 417.7333 | 104 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 445.8333 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 477.0833 | 25 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 504.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 771.3333 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 978.0833 | 97 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1644.7366 | 164.2 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1679.1665 | 250 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2172 | 240 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1.515 | 10.1 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 69.1667 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 79 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 80 | 40 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 94.3916 | 120.5 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 402.5 | 50 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 720.6667 | 20 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 812 | 56 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8883 | 126 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13657.5 | 45 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21400 | 30 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 23.7666 | 46 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 176.3 | 86 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 152.4166 | 155 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1075.7 | 34.7 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1528.8 | 28 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 62.4999 | 150 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668.04 | 17.58 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1287 | 16.5 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 383.1666 | 110 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1357.05 | 83 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175.9999 | 240 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 332.3166 | 127 | 1 | 1 | 0310-Pulverizer mills | D2-Forced - Delayed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65.6 | 32 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 34.1 | 31 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.0667 | 44 | 1 | 1 | 0310-Pulverizer mills | D3-Forced - Postponed | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1202.7164 | 427 | 1 | 1 | 0310-Pulverizer mills | U1-Forced - Immediate | 100-Fossil-Steam
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 443.9383 | 3.7 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 650-Fluidized Bed
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 60136.7333 | 59 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 344568 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 4488 | 60 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 8992.4999 | 198 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 4891.6 | 84 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0310 | Pulverizer mills | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 1485 | 198 | 1 | 1 | 0310-Pulverizer mills | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4418.4133 | 80.8 | 1 | 1 | 0312-Pulverizer mill classifiers | D3-Forced - Postponed | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19.41 | 64.7 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 958.5333 | 26 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1091.5666 | 143 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.9483 | 124.3 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 957.6998 | 471 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4040 | 60 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.58 | 115.6 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3578.1666 | 70 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 207.8916 | 123.5 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 598.3333 | 100 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 589.035 | 110.1 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8537.9166 | 155 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 227.9999 | 136.8 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 568.76 | 144.6 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2323.5998 | 471 | 1 | 1 | 0312-Pulverizer mill classifiers | U1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 406.0333 | 26 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1261.8266 | 80.8 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 425 | 25 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 383.68 | 65.4 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1296.6666 | 200 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2064.15 | 81 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 107.5 | 10 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1854.7333 | 86 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1229.8 | 26 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145.0166 | 124.3 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 119.3833 | 123.5 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2196.25 | 251 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0312 | Pulverizer mill classifiers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 151.83 | 144.6 | 1 | 1 | 0312-Pulverizer mill classifiers | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 774.2 | 98 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 649 | 59 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D2-Forced - Delayed | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 897.5166 | 157 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0313 | Pulverizer mill trunnion seals | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3737.7166 | 169 | 1 | 1 | 0313-Pulverizer mill trunnion seals | D1-Forced - Immediate | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15.6 | 26 | 1 | 1 | 0315-Pulverizer mill coal level controls | D2-Forced - Delayed | 100-Fossil-Steam
0315 | Pulverizer mill coal level controls | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 449.6799 | 153.3 | 1 | 1 | 0315-Pulverizer mill coal level controls | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 435.05 | 77 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 174.85 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 510.9 | 39 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 568 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 189.8 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 15.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.9333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32.9943 | 19.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 179 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60 | 15 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 177.5 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 581.02 | 26.41 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 205 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 62.5166 | 31 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 314.5 | 102 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42.4666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 268.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 103.7 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1253.15 | 71 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 315 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 341.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 25.5 | 51 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.2 | 38 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 244.8166 | 37 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 449.92 | 14.06 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 84.9333 | 98 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 133.95 | 28.5 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.98 | 4.74 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 363 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 426.6666 | 100 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37.2666 | 43 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432.6667 | 44 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 729.6 | 228 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28.5157 | 22.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 70.4666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69.1666 | 83 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19.5 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64 | 16 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 127.8666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 110 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 322.9166 | 155 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2106 | 180 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 576.9166 | 215 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 688.3333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 77.0666 | 34 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16.1467 | 24.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 106.8666 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.5 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 156.8667 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.6656 | 79.22 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 111.4666 | 76 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 181.5333 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 173.3333 | 26 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 303 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 498.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D2-Forced - Delayed | 100-Fossil-Steam
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 67.6667 | 20 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 226.8 | 28 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 101.5 | 30 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0320 | Foreign object in Pulverizers mill | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 361.6667 | 50 | 1 | 1 | 0320-Foreign object in Pulverizers mill | D1-Forced - Immediate | 650-Fluidized Bed
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12508.3333 | 50 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23.5387 | 25.22 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 296.9466 | 222.71 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 307.6832 | 184.61 | 1 | 1 | 0325-Pulverizer skidding | D1-Forced - Immediate | 100-Fossil-Steam
0325 | Pulverizer skidding | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 0325-Pulverizer skidding | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 339.5 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 148.7333 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1285.0999 | 213 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 441.6 | 138 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 118.3333 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 305.35 | 93 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4973.0832 | 415 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1738.6666 | 163 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 307.0666 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 343 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.1667 | 14 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 347.0833 | 175 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 901 | 90.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 279.0833 | 85 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 384 | 60 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 68.8333 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.8 | 42 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 160.65 | 81 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 180 | 75 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1335.5 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 963.3332 | 170 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51.5667 | 26 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 249.3333 | 80 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 265.5166 | 179 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 228.9 | 63 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 93905.1666 | 230 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | U1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.2016 | 33.1 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 360 | 15 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7396 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 976.9833 | 73 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1655.5 | 215 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 246 | 90 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 400 | 125 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2905.3333 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.7016 | 100.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 575 | 150 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 382.6666 | 82 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 34.4167 | 35 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 98.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 175 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38.2666 | 28 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 241.2666 | 94 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 579.8333 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D3-Forced - Postponed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1248.9 | 362 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4803.4 | 146 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 601.8333 | 157 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 324.0866 | 112.4 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 234.5999 | 207 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 534 | 45 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 908.6666 | 290 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 261.3333 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 198 | 110 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 214.6666 | 70 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2554.6666 | 40 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 152 | 30 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 168.0333 | 71 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 93.2167 | 47 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7.6667 | 23 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 449.4333 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 324.45 | 103 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 480.1999 | 84 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2907.1166 | 157 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1841.9166 | 155 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 498.1666 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 627.25 | 193 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.4166 | 97 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 829.6749 | 129.3 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 391.4833 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 491.6333 | 98 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2862.75 | 165 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 188.1333 | 83 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D2-Forced - Delayed | 100-Fossil-Steam
0330 | Pulverizer coal leak (pulverizers only) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 9265.9333 | 92 | 1 | 1 | 0330-Pulverizer coal leak (pulverizers only) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 304 | 120 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 773.8666 | 145.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 309 | 90 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 241.6 | 48 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 570.65 | 113 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 371.7 | 126 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 187 | 60 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1000 | 200 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 463.4 | 28 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 166.85 | 47 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66.6 | 74 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 122.6666 | 40 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.21 | 120.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 893.1167 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 150.1666 | 53 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 152.7833 | 103 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 584.865 | 95.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 266.28 | 95.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1266 | 211 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 411.9998 | 240 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1264.5 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 304.7667 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 485.55 | 70.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 156.6983 | 63.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.25 | 45 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 318.9999 | 435 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.04 | 50.7 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 290.1433 | 90.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 241.8833 | 63.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 73.6083 | 80.3 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 356.29 | 90.2 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 415.6664 | 430 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 211 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 145.55 | 41 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 140.9233 | 63.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 273.045 | 98.1 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 351.75 | 105 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 416.6666 | 100 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 690 | 30 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D2-Forced - Delayed | 100-Fossil-Steam
0331 | Pulverizer system coal leaks (other than pulverizers; see code 0330) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 357.6666 | 185 | 1 | 1 | 0331-Pulverizer system coal leaks (other than pulverizers; see code 0330) | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42.3333 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 508 | 80 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 39402 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 480 | 96 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 576.6667 | 50 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150.8333 | 25 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224 | 56 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 244.2666 | 64 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310 | 62 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6490.9914 | 406.11 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 257.9666 | 142 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 165.2 | 24 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 152.6667 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 155 | 155 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 183.7333 | 208 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 198 | 110 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18390.85 | 37 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3405.8664 | 412 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14.5667 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 105.7333 | 26 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 111553.2 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 345.6 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 72.75 | 45 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 486 | 216 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 610.6666 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9631.0833 | 235 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10620 | 236 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 342 | 24 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23507 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 20 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 166.25 | 95 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.4667 | 38 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.2917 | 12.5 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.8716 | 110.66 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 294 | 98 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 259.6 | 88 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2186.6666 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 416.25 | 135 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1006.1333 | 77 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 199.1831 | 323 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 192 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 563.75 | 82.5 | 1 | 1 | 0335-Pulverizer lube oil system | D3-Forced - Postponed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 365 | 100 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1559.5666 | 122 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1355.0833 | 101 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 408.4166 | 169 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3938 | 132 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2355 | 471 | 1 | 1 | 0335-Pulverizer lube oil system | U1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 593.9833 | 157 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3855.6 | 126 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 264.48 | 165.3 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695.97 | 70.3 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2610 | 300 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1364.96 | 35.92 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1489.6332 | 134 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1056.6 | 108 | 1 | 1 | 0335-Pulverizer lube oil system | D2-Forced - Delayed | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 89.6165 | 283 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 305.3333 | 40 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 234.3333 | 74 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 589.9999 | 120 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 695.4 | 183 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4746.6666 | 320 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 100-Fossil-Steam
0335 | Pulverizer lube oil system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 10146 | 89 | 1 | 1 | 0335-Pulverizer lube oil system | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 283.4166 | 95 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.2 | 72 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 126.6666 | 76 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225.0699 | 95.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 225.4999 | 165 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1469.4167 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 924.7332 | 286 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 30 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 547.8 | 83 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.08 | 30.2 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.4 | 24 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 298.35 | 153 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 83.7118 | 313.92 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 383.04 | 31.92 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 59.2666 | 127 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | U1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 0.8 | 4 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.6667 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1383.8 | 66 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 171.4166 | 121 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 52.8667 | 26 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 379.5665 | 193 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 319.0833 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.6666 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2127.0699 | 95.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 209.6666 | 85 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 253.9333 | 26 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 685.5333 | 28 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.45 | 81 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.6666 | 40 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 614.9799 | 95.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231.4666 | 56 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3589.75 | 173 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 252.4633 | 85.1 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 495.4166 | 102.5 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.3333 | 20 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D1-Forced - Immediate | 100-Fossil-Steam
0338 | Pulverizer control systems (temperature and pressure) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 51.9167 | 35 | 1 | 1 | 0338-Pulverizer control systems (temperature and pressure) | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2924.6665 | 410 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 123.7499 | 135 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 158.6666 | 80 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 134.25 | 45 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 258.9166 | 65 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3280.8329 | 635 | 1 | 1 | 0339-Pulverizer System Puff | U1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 63.9166 | 65 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8.8667 | 19 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.5333 | 26 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5142.5 | 150 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 238.3333 | 110 | 1 | 1 | 0339-Pulverizer System Puff | D2-Forced - Delayed | 100-Fossil-Steam
0339 | Pulverizer System Puff | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19.2573 | 22.22 | 1 | 1 | 0339-Pulverizer System Puff | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.8167 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7.6 | 19 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16.8 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100.4667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 305.6 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 664.4 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1210.4 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5372.0633 | 80.2 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 230605.6666 | 140 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 191.25 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2686.6666 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14.5833 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1409.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3402.4999 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.0667 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192.8167 | 50.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 392.4 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1656.0833 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 108.9133 | 19.22 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 176.12 | 6.29 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1064.7 | 5.46 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 77.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 205.2833 | 109 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 100.1667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122.8667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 138.6 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.6666 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1262.8 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 909.72 | 14.44 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30.6666 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2547.1666 | 52.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107.1 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 609.7333 | 136 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2978.6666 | 160 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45 | 7.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 191.6249 | 157.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 765 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1306.2666 | 194 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2500 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3444.3 | 80.1 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.3333 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.6 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 284.2666 | 164 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1407.9705 | 218.29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2381.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 30.3333 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 139.2 | 174 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.5 | 5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 442 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.6667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13093.025 | 101.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 66.1333 | 64 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 118.6666 | 89 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 392.6999 | 99 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1586 | 26 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2047.9331 | 278 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30.3333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 128.0666 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 454.6667 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 563.3333 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 849.6 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3012.5 | 241 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 169.1666 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 448 | 120 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1243.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3105.6664 | 770 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 46.5 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.25 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 424 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2175.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2336.9999 | 90 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.4667 | 8 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 330.75 | 147 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 686.9333 | 184 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1519.6666 | 97 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 226.2399 | 212.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 449.0966 | 101.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 466.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 950 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1941.5833 | 101.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5101.745 | 119.9 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6130.9333 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7765.8333 | 25 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32782.5 | 155 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.6699 | 160.2 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1562.7499 | 142.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2838.3999 | 192 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 32670.2666 | 236 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 39.1 | 69 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.7667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 97.6 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 118.5 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.3667 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.6666 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 159.1333 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 225 | 15 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 328 | 164 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 380 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 529.2 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 722.4683 | 40.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29.75 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35 | 100 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 99 | 132 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 565.5 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 365 | 30 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10120.875 | 492.5 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5467 | 770 | 1 | 1 | 0340-Other pulverizer problems | U1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.905 | 37.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 305.8698 | 251.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.0333 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67.1833 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 114.3999 | 264 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 322.4166 | 73 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 531.5333 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1040.6 | 44 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1509.3166 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1058.4583 | 95.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 519.84 | 6.84 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56.3333 | 26 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.1333 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 119 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 260.5832 | 147.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3325.5833 | 35 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3419.8333 | 85 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38.6333 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 47.6 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 70.7 | 14 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 114.3999 | 78 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 130.9 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 309.8333 | 65 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 408.5 | 95 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 317.3333 | 80 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 497.25 | 195 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3537 | 270 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10943.3332 | 134 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 65.3333 | 28 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1037.7333 | 86 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3785.8333 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.8666 | 74 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.6667 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 76.8 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 308 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 375.2 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 557.9199 | 95.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 984.3 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 56 | 40 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 177.0666 | 83 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 872.6666 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 8432 | 136 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14720.4 | 104.4 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1871.5 | 30 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 64.9999 | 75 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.8 | 30.7 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11.3333 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 80.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.2 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1079 | 52 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2184 | 91 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5.5831 | 335 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2251 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4112.3333 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6800.5 | 70 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 203.3333 | 152.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 902.8333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.8333 | 29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88.4 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 89.6667 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.3333 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130 | 10 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 232.75 | 142.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 327.5333 | 68 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 72 | 30 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 534.49 | 94.6 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6409.3328 | 836 | 1 | 1 | 0340-Other pulverizer problems | SF-Startup Failure | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 325.2 | 27.1 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1195.8333 | 175 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 31785 | 300 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 115.2 | 144 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 194.7914 | 467.5 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 319 | 20 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 538.725 | 65.3 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 823 | 60 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7193.8332 | 170 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 152.6 | 28 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 178.27 | 218.29 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1625 | 130 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.7 | 38 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.05 | 119 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 333.3332 | 200 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1372.4666 | 34 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2052.8 | 24 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.99 | 4.13 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 304.8332 | 155 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 37 | 30 | 1 | 1 | 0340-Other pulverizer problems | D2-Forced - Delayed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11027.6 | 290.2 | 1 | 1 | 0340-Other pulverizer problems | D3-Forced - Postponed | 100-Fossil-Steam
0340 | Other pulverizer problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 1376.7166 | 43 | 1 | 1 | 0340-Other pulverizer problems | D1-Forced - Immediate | 650-Fluidized Bed
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46.7646 | 255.08 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1692 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 21621.2 | 191 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 102 | 30 | 1 | 1 | 0342-Pulverizer inert system | D2-Forced - Delayed | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 740 | 100 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1265 | 100 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 318.9999 | 435 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 891 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 162.792 | 135.66 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 469 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 908 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 451 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 926.35 | 191 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 6339.2 | 283 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0342 | Pulverizer inert system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 816 | 60 | 1 | 1 | 0342-Pulverizer inert system | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 211.2 | 99 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 87.99 | 29.33 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.05 | 240.2 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 436.08 | 18.96 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3496 | 380 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 122.9166 | 125 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16.02 | 80.1 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.7833 | 13 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 816.6666 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 628.02 | 69.78 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 888 | 60 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 268.8166 | 127 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2423.5833 | 127 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1108.0966 | 80.2 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11850 | 237 | 1 | 1 | 0344-Pulverizer inspection | D3-Forced - Postponed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 691.35 | 99 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 713.4 | 12 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 198.3333 | 70 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 249 | 83 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2171.3333 | 40 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3079.2666 | 76 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 96.7499 | 135 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 95.94 | 7.38 | 1 | 1 | 0344-Pulverizer inspection | D2-Forced - Delayed | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 289.4667 | 26 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.9333 | 32 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 100-Fossil-Steam
0344 | Pulverizer inspection | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 17195.5 | 119 | 1 | 1 | 0344-Pulverizer inspection | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23931.6 | 36 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1885.75 | 95 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4936.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 840 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1138.6666 | 28 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1598 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.3333 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 391.0666 | 28 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 459 | 18 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2014 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2074 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3033.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 0 | 92 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3248 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 411.4 | 22 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1173.25 | 13 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14149.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 96 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1105.84 | 120.2 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 373.75 | 23 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1310 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 404.7 | 19 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11.2117 | 19.22 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 541.5 | 18 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3276.6666 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3724.6667 | 20 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50595.75 | 135 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.25 | 15 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2459.3333 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6716.6666 | 40 | 1 | 1 | 0345-Pulverizer overhaul | D2-Forced - Delayed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 168 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 768.8 | 24 | 1 | 1 | 0345-Pulverizer overhaul | D3-Forced - Postponed | 100-Fossil-Steam
0345 | Pulverizer overhaul | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 9855 | 73 | 1 | 1 | 0345-Pulverizer overhaul | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 500.9665 | 226 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 227.5 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 190.06 | 5.59 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 436.3333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 299 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.8333 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.8766 | 89.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 587.0666 | 296 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 155.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 10.6167 | 13 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.8 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156.6833 | 79 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 151.5833 | 107 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 210.9333 | 113 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98.1667 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 585.2 | 266 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1300 | 65 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1088.78 | 14.14 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 110.05 | 71 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 133.3 | 129 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 210.2333 | 119 | 1 | 2 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 72.8 | 78 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.6666 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 134.3666 | 139 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 930.05 | 57 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.9167 | 19 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 543.9773 | 79.22 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 45.8333 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 245 | 75 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 861.4666 | 91 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 158.2 | 113 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 312.8 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3808 | 224 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 205 | 41 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1745.1665 | 283 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2613.3 | 186 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 95.2 | 84 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 113.3 | 103 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.0166 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 77.7 | 74 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 162.8 | 37 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 537.75 | 135 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 112.6666 | 104 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 97.3916 | 89.9 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 162 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2529.9999 | 264 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 346.6666 | 100 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 158.6666 | 85 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1779.3333 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D3-Forced - Postponed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2139.5 | 110 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3532.5333 | 208 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.3333 | 80 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 256.6666 | 77 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9436.0666 | 236 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 348.45 | 101 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1383.7 | 202 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 24573.6999 | 186 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 127.5 | 34 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 361.9999 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 190 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 159.6832 | 143 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 237.5 | 125 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 978.0833 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 120 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2954.0665 | 292 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82 | 40 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 125.3166 | 73 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 85.05 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 205.2 | 81 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.8499 | 153 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2460 | 30 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 126.9 | 94 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 143.1 | 53 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 880 | 220 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 143.1833 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 326.7 | 121 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 339.2 | 96 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 41.1667 | 26 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.5666 | 103 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 142.2 | 79 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 174.15 | 129 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 82.8 | 72 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 505.2666 | 106 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.9333 | 38 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 93.3333 | 35 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 108 | 120 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 274.5 | 27 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2601.9 | 177 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.4 | 12 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 141.9 | 86 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.4 | 17 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9579 | 186 | 1 | 1 | 0346-Pulverizer pyrite removal system | D1-Forced - Immediate | 100-Fossil-Steam
0346 | Pulverizer pyrite removal system | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 362.1333 | 112 | 1 | 1 | 0346-Pulverizer pyrite removal system | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 285 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15.3333 | 20 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 592.0833 | 145 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 261.25 | 33 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1191.96 | 60.2 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33.8667 | 16 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112.1833 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.75 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 211.8783 | 100.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 302.1 | 114 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 63.5 | 38.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.52 | 106.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 950.0167 | 17 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 85 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 46.5666 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.8125 | 227.25 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 98.55 | 73 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34.6166 | 31 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1349.3333 | 40 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 39.5 | 10 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 165.502 | 29.91 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.9907 | 15.76 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3016 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 385.2333 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 124.1333 | 106.4 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 13.3333 | 16 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1813.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 93.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25.467 | 39.18 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1279.9667 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 136.5 | 35 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 130.0167 | 29 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 461.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10250.5 | 41.5 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 66.6666 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.3333 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 203.0333 | 243.64 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275 | 50 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 137.6666 | 140 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D2-Forced - Delayed | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 100 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4424.7073 | 51.49 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0 | 0 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1171.0833 | 235 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 785.6333 | 49 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43.7333 | 32 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.7833 | 127 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 702.1683 | 60.1 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5700 | 38 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | D1-Forced - Immediate | 100-Fossil-Steam
0350 | Pulverized fuel and air piping (from pulverizer to wind box) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 3023.9332 | 268 | 1 | 1 | 0350-Pulverized fuel and air piping (from pulverizer to wind box) | U1-Forced - Immediate | 650-Fluidized Bed
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 1335.1 | 39 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0358 | Oil burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92 | 55.2 | 1 | 1 | 0358-Oil burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.3 | 286 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 305.2 | 109 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 407.4 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 108.15 | 63 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 780.7664 | 397 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2370.0831 | 595 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 487.0833 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 495.6 | 24 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2663.1 | 591.8 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 60.125 | 92.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 317.9165 | 175 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1318.0933 | 94.6 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 207.9 | 462 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2071.9997 | 480 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1402.533 | 536 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 265.065 | 129.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 556.2499 | 375 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2594.4 | 368 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 258.3 | 63 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1062.4 | 256 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1920.6666 | 344 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 66.8666 | 59 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1129.7333 | 74 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 3939.4666 | 79 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7386.8 | 472 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 665.833 | 850 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 727.5 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 95.6331 | 302 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 463.26 | 110.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 720.3 | 63 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 462548.1 | 222 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 227.5 | 350 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1180.3546 | 585.3 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1187.8166 | 170.5 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 715 | 286 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4481.1999 | 408 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2017.5996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 155.15 | 107 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 22.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 52.7 | 51 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2942.1332 | 472 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9901.5 | 138 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 4982.4 | 72 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 475.2996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 266.6665 | 250 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 3667.6 | 53 | 2 | 2 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 141.3166 | 139 | 1 | 2 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 8680.4664 | 836 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1131.5798 | 585.3 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3455.04 | 566.4 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 258.72 | 26.4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 2842.4 | 57 | 2 | 2 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1208.5328 | 824 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 620.7996 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3537.1 | 434 | 1 | 1 | 0359-Gas burner piping and valves | U3-Forced - Postponed | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37.8666 | 284 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 295.9999 | 120 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 44.1 | 63 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 102.6666 | 110 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 135.4666 | 254 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1638.84 | 585.3 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4314.0664 | 397 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10103.3331 | 350 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 979.6998 | 582 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 177.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 39.5 | 395 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 127.2 | 21.2 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 51.3333 | 44 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 51.1333 | 26 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 51.8 | 29.6 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 36.55 | 43 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 55.72 | 59.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 117.8 | 12 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 211.5 | 94 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 10.1733 | 43.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4.8 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 19.3333 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 180.6667 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3412.14 | 47.7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 276.0666 | 101 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 228.8542 | 16.25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 52.5 | 30 | 1 | 1 | 0359-Gas burner piping and valves | SF-Startup Failure | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 10.2 | 36 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 6262.1997 | 378 | 1 | 1 | 0359-Gas burner piping and valves | U1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | U3 | Forced - Postponed | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 6315.2333 | 58 | 1 | 1 | 0359-Gas burner piping and valves | U3-Forced - Postponed | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 18082.9833 | 23 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 851-CC GT units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 1397.7983 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 82.8 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 12.3 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 14.8 | 6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 256.65 | 53.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3129.8667 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 9483.5 | 39 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 189.81 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 37.7333 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 265.3333 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 344.05 | 21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 43.1249 | 103.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 79.1343 | 55.21 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 319.5 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 15.0667 | 8 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1724.9999 | 165.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 75.8333 | 70 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 606.9233 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 118.6666 | 89 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 316.6667 | 25 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 600 | 120 | 1 | 1 | 0359-Gas burner piping and valves | D2-Forced - Delayed | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Winter | 2215 | 20 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 116.1333 | 53.6 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 1069.7316 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2.05 | 41 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 17059.9999 | 120 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 55.125 | 24.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1881 | 90 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 494.4433 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 792 | 55 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 181.425 | 53.1 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 831.8833 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 69.8 | 4 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 185.15 | 7 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2055.1033 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 5342.25 | 45 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 742.6666 | 80 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 6205.1466 | 70.3 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 167.4999 | 100.5 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 5605.25 | 105 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0359 | Gas burner piping and valves | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 505.9999 | 120 | 1 | 1 | 0359-Gas burner piping and valves | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10.4 | 78 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 26.6666 | 64 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 191.6833 | 217 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 242 | 121 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1704.9999 | 150 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 325.2 | 24 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 374.6667 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 40108.4499 | 87 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1910.4833 | 79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 13.3333 | 16 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1893.78 | 11.34 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3651.9 | 658 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 119.2333 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 158.8913 | 216.67 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 773.3333 | 80 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1646.1666 | 70 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 550.85 | 69 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2306.4999 | 105 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 397.15 | 169 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3677.1368 | 157.93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4806.25 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 610.5 | 55 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 173.3333 | 80 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1381.66 | 9.94 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 55 | 110 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 303.3667 | 38 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 619.2 | 8.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 59.04 | 6.56 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 61.9999 | 120 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19771.7825 | 57.77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 68.75 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 48.3333 | 10 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16.5 | 66 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 508.2332 | 158 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14.3 | 78 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 105.6 | 48 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 108.3333 | 5 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1677.9499 | 111 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 421.0833 | 163 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 5 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 40 | 120 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 104.8833 | 217 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3068.7499 | 375 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.9833 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 94.5833 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 24.0833 | 17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 69805.3333 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 712.98 | 41.94 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 336 | 105 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 204.1666 | 98 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 389.3333 | 73 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.6666 | 40 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10447.75 | 79 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 108 | 72 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10.8333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12.3333 | 74 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 76 | 76 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 133.98 | 22.33 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 532.65 | 201 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 39797.5 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6491.9833 | 83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 68 | 34 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 262.6666 | 80 | 1 | 1 | 0360-Burners | SF-Startup Failure | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 274 | 120 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16.8 | 42 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 271 | 67.75 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 151.03 | 13.73 | 1 | 1 | 0360-Burners | D2-Forced - Delayed | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 104.1666 | 125 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 126.5833 | 217 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1617 | 147 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 71.3333 | 107 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 100-Fossil-Steam
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 40.5 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Winter | 258.75 | 115 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 800-Miscellaneous
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 75 | 100 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 50.71 | 50.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 7.544 | 2.46 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 135.971 | 28.93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 137.25 | 15 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 174.42 | 51.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 507.35 | 73 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 58.0833 | 69.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 350 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 42.01 | 42.01 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 59.06 | 59.06 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 84.41 | 84.41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 521.8999 | 102 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 20.1 | 60.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 29 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 48.77 | 48.77 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 9.1833 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1676.25 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 500 | 48 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 24.0417 | 28.85 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 66.75 | 66.75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 58.77 | 65.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 39.93 | 39.93 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 49.17 | 49.17 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 871.75 | 33 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 255.55 | 19 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 96.28 | 96.28 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 46.3867 | 49.7 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 49.49 | 49.49 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 22.71 | 22.71 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 32.89 | 32.89 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6.44 | 48.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 8.01 | 8.01 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 15.69 | 15.69 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 33.98 | 33.98 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 25.521 | 8.46 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 55.1 | 29 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 1764.1 | 26 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 44.52 | 44.52 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 857.35 | 13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2.415 | 48.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3.22 | 48.3 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 41.6666 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 850-Combined Cycle Block
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 2817 | 36 | 1 | 1 | 0360-Burners | U1-Forced - Immediate | 851-CC GT units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 17.6667 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 64.5833 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 9610.25 | 65 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 126 | 56 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 454.8 | 36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1123.4 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 2932.2333 | 121 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 77.4 | 36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2067.45 | 11 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 294 | 120 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 77.0666 | 68 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 45.8333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 30787.5 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2990.0667 | 2 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 202.515 | 52.83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 33.705 | 44.94 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 85.7433 | 44.35 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2768.3 | 6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 41 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 9.5667 | 41 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 50.4513 | 39.83 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 103.6775 | 55.05 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 104.4 | 36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 706.1667 | 38 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 61.5 | 45 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 16.71 | 50.13 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 108 | 90 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 142.4433 | 56.6 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 31.6667 | 20 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 109.92 | 54.96 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 358 | 60 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 105 | 75 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 63.6 | 36 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1850 | 50 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1908.3333 | 25 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 156.2 | 66 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5.26 | 31.56 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 852-CC steam units
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 3110.23 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 102.1733 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 412.6433 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 1430.1633 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 438.9767 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 2110.09 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0360 | Burners | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Winter | 1311.4 | 15.8 | 1 | 1 | 0360-Burners | D1-Forced - Immediate | 860-Co-generator Block
0361 | Burner orfices | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 184.5333 | 16 | 1 | 1 | 0361-Burner orfices | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 37.0667 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 11 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2.1 | 21 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Off-Peak | 21.06 | 7.02 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 7543.9998 | 690 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 1361.5996 | 552 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 341 | 124 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 49.4998 | 297 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 262.4666 | 127 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3031.6663 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 250.0998 | 246 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 276.0333 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 104.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1.2 | 12 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28742.1333 | 52 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 977.3833 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9.6663 | 580 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1624.5 | 570 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 285.6 | 112 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 785.8331 | 410 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 374.6166 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1675 | 500 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 19.505 | 8.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.4167 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 144.9999 | 300 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 309.8333 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1746.1798 | 240.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8123.0832 | 535 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1137.9333 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 366.3249 | 439.59 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4743.6333 | 202 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U3-Forced - Postponed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 29 | 30 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 671.3333 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 98.7999 | 296.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 26074.4 | 132 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 159.6 | 532 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 64.9999 | 150 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 4802.4 | 552 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | SF-Startup Failure | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 379.5 | 330 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 173.4299 | 110.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 537.3333 | 208 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.5 | 30 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 20 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 120.6666 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 33183.15 | 77 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 64389.8666 | 37 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1666.9164 | 415 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16012.75 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 640739.25 | 415 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4.2667 | 8 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 158.75 | 127 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 26666.6665 | 500 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 414 | 552 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 107.6667 | 17 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 173.5666 | 127 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 777.4 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58.96 | 40.2 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 15513.5 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 23571 | 54 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 101.6666 | 305 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13515.8664 | 668 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 447.7331 | 368 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18.8 | 24 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17.4665 | 262 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 27.65 | 79 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 47.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2219.84 | 396.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3005.2662 | 739 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 242.2333 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 340.8166 | 169 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 433.9999 | 120 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 383.3333 | 40 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 100-Fossil-Steam
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 6.2792 | 15.07 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 800-Miscellaneous
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 44.0683 | 19.3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1912 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 427 | 28 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 985.25 | 281.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 58.2667 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 850-Combined Cycle Block
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 91.2333 | 17 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 1137.6667 | 10 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 103.5925 | 37.67 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 851-CC GT units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2.4 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 57.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 752.4 | 38 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2.9 | 3 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 38.3333 | 100 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 813 | 60 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 268.2917 | 23.5 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1904.6 | 89 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 49.8833 | 41 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 31.5 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 114.8 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 503.58 | 92.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 107.1017 | 17.9 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2502.4999 | 231 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 187.8333 | 35 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | U1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 1420.65 | 28.7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 123.6491 | 157.85 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 322.7 | 7 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 19.8 | 36 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 0 | 0 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 6861.25 | 75 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 17.5 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 170.94 | 92.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 39 | 26 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 79.3333 | 56 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 30.3333 | 70 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2304.7332 | 191 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 24597.4667 | 44 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 317.7 | 18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 6.6 | 18 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D3 | Forced - Postponed | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 43971 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D3-Forced - Postponed | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 302.3165 | 213.4 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 29.3333 | 80 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 169.62 | 61.68 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 852-CC steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 642.5 | 15 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 862-CoG steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 214.2 | 63 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 862-CoG steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 308 | 66 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 862-CoG steam units
0370 | Burner instruments and controls (except light-off) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 109.8 | 61 | 1 | 1 | 0370-Burner instruments and controls (except light-off) | D1-Forced - Immediate | 862-CoG steam units
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 690.7998 | 264 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.9883 | 15.1 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 700 | 350 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58 | 60 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14430 | 1110 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1153.3333 | 100 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 723.0663 | 493 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 396.6665 | 238 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 160.55 | 247 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12499.2 | 288 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 564.2 | 364 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 782.55 | 111 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 688.6163 | 523 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 374.1 | 258 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 414.6663 | 622 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.5 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1395.8332 | 125 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810 | 405 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2601.0963 | 68.51 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1246.6417 | 21.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Summer | 53 | 12 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5214.5496 | 627 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 92.5876 | 326.78 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 393.75 | 157.5 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 64.4 | 69 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3702.4 | 832 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.97 | 64.6 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 700 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 491.6665 | 500 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 100-Fossil-Steam
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 80.5266 | 51.4 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | OG | 850 | Combined Cycle Block | SERC | Off-Peak | 1824 | 114 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1325.2733 | 53.8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 390.3066 | 58.4 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 67.04 | 83.8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 231.19 | 18.3 | 2 | 2 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 508.0599 | 79.8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 850-Combined Cycle Block
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 0.81663 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 63.7 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 12089.1665 | 178 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1.6333 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | SF-Startup Failure | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 17.9666 | 49 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | U1-Forced - Immediate | 851-CC GT units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 46.6666 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 723.3333 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 34810.75 | 39 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 997.1 | 39 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2.97 | 19.8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 162.1666 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 172.0711 | 55.21 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 21501.35 | 19 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 18.6666 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 19.8333 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 35 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 84 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 425.8333 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 4.62 | 19.8 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 54.8333 | 70 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0380 | Light-off (igniter) systems (including fuel supply) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1464.45 | 39 | 1 | 1 | 0380-Light-off (igniter) systems (including fuel supply) | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 534.3332 | 140 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 79.1667 | 50 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1169.3333 | 8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1481.7999 | 372 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6318.45 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1780.9332 | 361 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5308.4831 | 739 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.25 | 35 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1391.5 | 110 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 866.9165 | 515 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 973.5 | 110 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 425.8833 | 101 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 375 | 125 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 170 | 51 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 10.6167 | 13 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 625.1662 | 682 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81 | 108 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 129.85 | 53 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 346.1332 | 352 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 617.0998 | 306 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2050 | 820 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 739 | 739 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 325.6 | 33 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2812.1665 | 470 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4395.3 | 546 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86.35 | 157 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 631.655 | 207.1 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4143.8667 | 8 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 810.7 | 134 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1593.4 | 93 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 82.5 | 55 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.3 | 102 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8400 | 400 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1406.005 | 119.66 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 779.7 | 138 | 1 | 1 | 0385-Igniters | D2-Forced - Delayed | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8991.1662 | 739 | 1 | 1 | 0385-Igniters | SF-Startup Failure | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 245.9666 | 157 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 306.25 | 245 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 301.35 | 123 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2032.25 | 739 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 95.2 | 119 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 100-Fossil-Steam
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | OG | 850 | Combined Cycle Block | SERC | Summer | 690 | 115 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 850-Combined Cycle Block
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 6040 | 160 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 78 | 13 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 852-CC steam units
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 921.3 | 83 | 1 | 1 | 0385-Igniters | U1-Forced - Immediate | 860-Co-generator Block
0385 | Igniters | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Off-Peak | 278.4832 | 269.5 | 1 | 1 | 0385-Igniters | D1-Forced - Immediate | 860-Co-generator Block
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 97.4167 | 35 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 31.5 | 35 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1663.3333 | 40 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 163.3666 | 58 | 1 | 1 | 0390-Burner wind boxes and dampers | D2-Forced - Delayed | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1002.6666 | 40 | 1 | 1 | 0390-Burner wind boxes and dampers | D1-Forced - Immediate | 100-Fossil-Steam
0390 | Burner wind boxes and dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3398.6331 | 682 | 1 | 1 | 0390-Burner wind boxes and dampers | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16000.8 | 48 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 196614.6664 | 668 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13779.1166 | 53 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6575 | 20 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240045.8 | 668 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113016 | 68 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6021.9333 | 118 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 210 | 70 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57092.8331 | 673 | 1 | 1 | 0400-Burner wind box fires | U2-Forced - Delayed | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 90356.5333 | 118 | 1 | 1 | 0400-Burner wind box fires | D1-Forced - Immediate | 100-Fossil-Steam
0400 | Burner wind box fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19104.8 | 668 | 1 | 1 | 0400-Burner wind box fires | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 624.1333 | 151 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 360.75 | 92.5 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 617.5 | 247 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 79780.4333 | 34 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 33.4 | 12 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16733.9896 | 543.9 | 1 | 1 | 0410-Other burner problems | U1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2046.2933 | 35.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 100-Fossil-Steam
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 587.9466 | 83.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 751.1867 | 10.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2839.55 | 133 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 14486.6067 | 20.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 7982.3166 | 81.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 198.26 | 9.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 118.15 | 69.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 3396.8233 | 35.8 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 564.4 | 27.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 14137.18 | 84.2 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 131.0083 | 99.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4883.9583 | 98.5 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 850-Combined Cycle Block
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1389.3 | 6 | 1 | 1 | 0410-Other burner problems | D2-Forced - Delayed | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 14 | 40 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 71.5 | 66 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1320 | 15 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 3289.7667 | 23 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 148.4533 | 58.6 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1261.4333 | 71 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Off-Peak | 3575.8333 | 25 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 287 | 41 | 1 | 2 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 185.8666 | 68 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 78.4 | 24 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0410 | Other burner problems | HRSG Boiler | HRSG Boiler Fuel Supply | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 11702.1 | 114 | 1 | 1 | 0410-Other burner problems | D1-Forced - Immediate | 852-CC steam units
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113.3333 | 50 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8.5 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 16.25 | 39 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 0.16667 | 2 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.5333 | 19 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 110 | 55 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 294.5 | 38 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5.1666 | 31 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 43.2 | 216 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.9 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 195 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 373 | 74.6 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 63.9166 | 65 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 107.8 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 19 | 57 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.8 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8.5 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4.5333 | 16 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 7.65 | 27 | 1 | 2 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18.2 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 971.6 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26 | 13 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 16.8665 | 253 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1.9333 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 12.9999 | 78 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3.4667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20.15 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1001.65 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11 | 5.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 120 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 210.8333 | 46 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 281.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 56.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 532.5 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14.7333 | 52 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1.4 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3360.5 | 39 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 379.4 | 42 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1.9167 | 23 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 9.8 | 21 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5012.583 | 455 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 63.4333 | 22 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 437.8 | 39.8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 30 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2573.9 | 42 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43324.2832 | 511 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 154.1667 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 614.3333 | 20 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 744.6833 | 91 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 405 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4.2667 | 8 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 19.05 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7.65 | 27 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 461.1 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3.6166 | 31 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 432.96 | 39.36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45 | 22.5 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 670.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 54.9666 | 34 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60 | 15 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8.3333 | 25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 14.25 | 45 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 54.9332 | 206 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2.1333 | 32 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6.0667 | 26 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1 | 4 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24.7333 | 53 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 702.6666 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 81 | 270 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1.6 | 24 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 21.15 | 47 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 651.2167 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1386.6666 | 64 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 40 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 107.7833 | 223 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1027.4 | 44 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 97.3333 | 40 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 201 | 50.25 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1669.08 | 59.61 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 13.6667 | 41 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 53.9 | 98 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63.25 | 33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 99.99 | 33.33 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 355.8 | 36 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 46.3665 | 214 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 15.4 | 44 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 86.85 | 27 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 638.9667 | 29 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11787.4333 | 79.6 | 1 | 1 | 0415-Cyclone feeders | U1-Forced - Immediate | 100-Fossil-Steam
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 41.0833 | 29 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 189.1664 | 454 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Winter | 123.3332 | 185 | 1 | 1 | 0415-Cyclone feeders | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 19.75 | 79 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3610.3831 | 419 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 60.4333 | 14 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 63.25 | 69 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0415 | Cyclone feeders | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 27 | 9 | 1 | 1 | 0415-Cyclone feeders | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1690 | 50 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 364.3333 | 20 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 10 | 40 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 939.5 | 30 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 312.6667 | 35 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 16.4 | 12 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 807.6667 | 10 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 594 | 45 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1809.5 | 22 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1921 | 30 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 118.5333 | 8 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 86.6667 | 25 | 1 | 1 | 0420-Cyclone crusher | D3-Forced - Postponed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8.1333 | 61 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 739.7833 | 7 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 6.2 | 31 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.3333 | 40 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2053.6667 | 20 | 1 | 1 | 0420-Cyclone crusher | D2-Forced - Delayed | 100-Fossil-Steam
0420 | Cyclone crusher | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 0.89999 | 27 | 1 | 1 | 0420-Cyclone crusher | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6.7833 | 37 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 35.3332 | 265 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 0.85 | 17 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172.25 | 65 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 20.1667 | 11 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 0.58333 | 5 | 1 | 1 | 0425-Cyclone dampers | D1-Forced - Immediate | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 534.0833 | 29 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 100-Fossil-Steam
0425 | Cyclone dampers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 2970.5664 | 439 | 1 | 1 | 0425-Cyclone dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 699.9999 | 105 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1.2333 | 1 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 97.0667 | 32 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 536.75 | 57 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 37.7 | 39 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 6.4167 | 7 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 10.6166 | 91 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 70.8333 | 34 | 1 | 1 | 0426-Cyclone air ducts | D2-Forced - Delayed | 100-Fossil-Steam
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 220.5 | 18 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 800-Miscellaneous
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 11.75 | 15 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 800-Miscellaneous
0426 | Cyclone air ducts | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 45.9 | 18 | 1 | 1 | 0426-Cyclone air ducts | D1-Forced - Immediate | 800-Miscellaneous
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22853.8333 | 70 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2510.5667 | 11 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16824 | 144 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 30.6667 | 10 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9475.6666 | 62 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1185.6 | 24 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 21565 | 190 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 40 | 20 | 1 | 1 | 0430-Cyclone furnace | D2-Forced - Delayed | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8022.4 | 24 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3188.6333 | 34 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4550.8 | 24 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 411.1 | 1 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6180.2666 | 128 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2121.6667 | 38 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 768.8667 | 19 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0430 | Cyclone furnace | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11340.4667 | 38 | 1 | 1 | 0430-Cyclone furnace | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3810.17 | 137.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 45.2 | 226 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 58.5 | 13 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 276.19 | 77.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4709.8933 | 47.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 834.9 | 19.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2056.1667 | 33.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 121.3333 | 56 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12654.4 | 48 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 400 | 20 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9469.3333 | 80 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 320.79 | 57.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 389.8199 | 262.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 343.4166 | 65 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 51.03 | 37.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 17.3333 | 208 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 14 | 14 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 97.65 | 37.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 830.0066 | 62.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 436.9766 | 77.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4 | 4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.7866 | 72.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44 | 22 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 405.3333 | 40 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3 | 30 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 122.04 | 67.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 863.1699 | 247.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21242.5 | 145 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18550 | 84 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 100.5333 | 52 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 100-Fossil-Steam
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 41.6 | 2.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 12.8 | 1.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3 | 1.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9.9 | 1.1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 8140.5 | 405 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3.8 | 1.9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 147.2 | 4.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 9.5 | 1.9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 140.5683 | 1.9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 14 | 2.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 20.54 | 15.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 33.6 | 2.4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 13.2 | 2.2 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 4.8 | 1.6 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9.9 | 0.9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 7 | 1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 13.3 | 1.9 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 39.6 | 1.8 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 38.5 | 3.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 14.8 | 3.7 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 151.7 | 4.1 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3.9 | 1.3 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 9 | 4.5 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 21.25 | 3.4 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0435 | Other cyclone problems | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2722.9999 | 420 | 1 | 1 | 0435-Other cyclone problems | D1-Forced - Immediate | 650-Fluidized Bed
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 504.9164 | 415 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 374.1248 | 307.5 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 39 | 130 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | SF | Startup Failure | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3016.6665 | 250 | 1 | 1 | 0440-Fuel oil pumps (general) | SF-Startup Failure | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 294.9999 | 300 | 1 | 1 | 0440-Fuel oil pumps (general) | D1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Summer | 25646.3999 | 369.9 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 100-Fossil-Steam
0440 | Fuel oil pumps (general) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 46.6917 | 43.1 | 1 | 1 | 0440-Fuel oil pumps (general) | U1-Forced - Immediate | 850-Combined Cycle Block
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 618.6665 | 232 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | U1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 96 | 48 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0441 | Fuel oil pumps (burner supply) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 765 | 17 | 1 | 1 | 0441-Fuel oil pumps (burner supply) | D1-Forced - Immediate | 100-Fossil-Steam
0450 | Fuel oil heaters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 669.1965 | 262.43 | 1 | 1 | 0450-Fuel oil heaters | U1-Forced - Immediate | 851-CC GT units
0450 | Fuel oil heaters | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 468.027 | 183.54 | 1 | 1 | 0450-Fuel oil heaters | D1-Forced - Immediate | 852-CC steam units
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4363.3333 | 25 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0460 | Fuel oil atomizers | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 40 | 30 | 1 | 1 | 0460-Fuel oil atomizers | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1330829.4996 | 546 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 366.9332 | 128 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 355.5 | 158 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1474.3998 | 582 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2648 | 48 | 1 | 1 | 0470-Oil and gas fires | D1-Forced - Immediate | 100-Fossil-Steam
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 2043.75 | 75 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 11550 | 28 | 2 | 2 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 37638.85 | 25.5 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 42016.8 | 28.7 | 2 | 2 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 131760 | 90 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 37125 | 90 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 37633.75 | 25.5 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0470 | Oil and gas fires | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 132843 | 90 | 1 | 1 | 0470-Oil and gas fires | U1-Forced - Immediate | 850-Combined Cycle Block
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 93.3332 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 605.8667 | 16 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3668 | 524 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 364.7 | 104.2 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2143.05 | 157 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20135.733 | 536 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 185.6499 | 141 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8330 | 595 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 65.2667 | 22 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 192.4999 | 330 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 481.3999 | 249 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 177.3332 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 930.3665 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 11.0833 | 19 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 727.9997 | 480 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 468.6667 | 19 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 102.5585 | 19.29 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2638.9997 | 435 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 42141.6 | 585.3 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 171 | 19 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 79.3332 | 280 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1390.9332 | 256 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1803.4 | 254 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 203.4 | 108 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 986.6998 | 234 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 77.8665 | 292 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1843.2 | 256 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 53.04 | 10.4 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 90.3 | 86 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 219.5833 | 25 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 42.3666 | 31 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 75.998 | 379.99 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1811.8666 | 254 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 691.6 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 469.3 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 62.9997 | 378 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 315 | 135 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 28.4999 | 342 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 265.993 | 379.99 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2217.6 | 231 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1330 | 380 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2688 | 480 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 126.9088 | 23.87 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | D1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 440.4833 | 247 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 100-Fossil-Steam
0480 | Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | HRSG Boiler | Boiler Fuel Supply from Bunkers to Boiler | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 2520.3 | 186 | 1 | 1 | 0480-Other oil and gas fuel supply problems (see codes 0360-0410 for burner problems) | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 38560.3333 | 145 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 110889.5663 | 526 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 821426.6665 | 650 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1524.6165 | 538.1 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 42281.6332 | 526 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65473.5665 | 554 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3178.6662 | 745 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 68205.9332 | 227 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 31496.65 | 661 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 63715.4166 | 145 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6964.6095 | 713.1 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 255344.8662 | 637.3 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U3-Forced - Postponed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3931.85 | 23 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9967.9999 | 120 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 3.6 | 27 | 3 | 3 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 9.9 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 4.05 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 5.4 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 6.75 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 5.4 | 27 | 1 | 4 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 4.95 | 27 | 1 | 3 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 2.7 | 27 | 2 | 3 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 3.15 | 27 | 2 | 3 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 7.65 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 15.75 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 16.2 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 6.75 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 9 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 2.7 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 39.15 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 17.1 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 12.6 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 2.25 | 27 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 830-Geothermal
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 15622.3666 | 287 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 159.5999 | 126 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 281.4 | 126 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 5996.4666 | 148 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 207.9 | 126 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 1659.8833 | 163 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 6861.3199 | 152.7 | 2 | 2 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 851-CC GT units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 865.5833 | 85 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 10109.9999 | 225 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 4294.7666 | 106 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | U2-Forced - Delayed | 852-CC steam units
0500 | Main steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 41710.3915 | 369.5 | 1 | 1 | 0500-Main steam piping up to turbine stop valves | D1-Forced - Immediate | 860-Co-generator Block
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 79.2 | 8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 932.8333 | 145 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 24.3 | 243 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 719.0333 | 53 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 8905.4166 | 55 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 31.2666 | 67 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1210.8 | 100.9 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1967.9999 | 180 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 132.8 | 48 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 236.8 | 128 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 305.6667 | 35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17068 | 680 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 392 | 16 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 420 | 35 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1481.2 | 138 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 288.75 | 21 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 252.1998 | 291 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 784.6997 | 399 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 474.5831 | 425 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8086.0499 | 189 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19.95 | 57 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 16652.8933 | 53.8 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5963.95 | 659 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 30.8 | 28 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4748.8 | 32 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 648.3331 | 389 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1024.9998 | 300 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1710 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 229.5 | 153 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D3-Forced - Postponed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38156.25 | 625 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5118.7499 | 189 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 23896.08 | 577.2 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U2-Forced - Delayed | 100-Fossil-Steam
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 642.6 | 189 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | SF-Startup Failure | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3631.2 | 272 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | U1-Forced - Immediate | 851-CC GT units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 62.25 | 15 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0510 | Main steam relief/safety valves off superheater | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 1183.2 | 348 | 1 | 1 | 0510-Main steam relief/safety valves off superheater | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 5624.2666 | 112 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4847.5 | 554 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17227.65 | 197 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3012.6566 | 122.3 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 9081.1666 | 230 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 27592.4998 | 234 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 726.7996 | 552 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38253.6 | 552 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U3-Forced - Postponed | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3560.4 | 552 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12477.0663 | 568 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 206.15 | 57 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | SF-Startup Failure | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2033.1998 | 552 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2527.9997 | 480 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 100-Fossil-Steam
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 650 | Fluidized Bed | TRE | Winter | 16731 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 48028.7498 | 525 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 650-Fluidized Bed
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 67164.1663 | 550 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1092 | 240 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 80553.7332 | 484 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 850-Combined Cycle Block
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 9072 | 168 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 754.6667 | 32 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3698.7782 | 160.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 88.85 | 177.7 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 19557 | 180 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 157.3333 | 32 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 5949.3332 | 194 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U2-Forced - Delayed | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 98 | 196 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 5620.2666 | 176 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3698.0877 | 160.67 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 250.5 | 167 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 23.6664 | 355 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 851-CC GT units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 329.15 | 29 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 3925.3332 | 128 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6389.4265 | 277.6 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Winter | 3480.7333 | 109 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 221 | 130 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | D1-Forced - Immediate | 852-CC steam units
0520 | Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Summer | 131.6166 | 74.5 | 1 | 1 | 0520-Other main steam valves (including vent and drain valves but not including the turbine stop valves) A | U1-Forced - Immediate | 860-Co-generator Block
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155.9832 | 191 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 2999.5833 | 25 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3195.3999 | 156 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.8106 | 77.48 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1545.3333 | 20 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6330 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 129.03 | 7.59 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 10155.1998 | 528 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 412.5 | 10 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67747.6664 | 361 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 382.5 | 15 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 510 | 15 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 16259.5 | 310 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 5 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11866 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 590.9353 | 63.77 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 254 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12696 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 529.5333 | 52 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16447.5 | 30 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 21.75 | 15 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1146.6 | 49 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 6175 | 247 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 100-Fossil-Steam
0530 | Other main steam system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 22564.9 | 251 | 1 | 1 | 0530-Other main steam system problems | D1-Forced - Immediate | 650-Fluidized Bed
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 258.6 | 43.1 | 1 | 1 | 0530-Other main steam system problems | U2-Forced - Delayed | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1932.22 | 56.83 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 46413.4999 | 267 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 149.625 | 47.5 | 1 | 1 | 0530-Other main steam system problems | D2-Forced - Delayed | 850-Combined Cycle Block
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 196.5332 | 176 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 518 | 259 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 851-CC GT units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Winter | 135.4164 | 325 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 50.15 | 51 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1034.3165 | 271 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 852-CC steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 862 | CoG steam units | TRE | Off-Peak | 44.2 | 66.3 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 862-CoG steam units
0530 | Other main steam system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 862 | CoG steam units | TRE | Off-Peak | 51.935 | 66.3 | 1 | 1 | 0530-Other main steam system problems | U1-Forced - Immediate | 862-CoG steam units
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 683.6498 | 339 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5588.1833 | 187 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81257.16 | 814.2 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4812.4 | 106 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1038.9165 | 455 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 121691.615 | 897.1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6632.2667 | 38 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 13832.1 | 141 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 22082.4331 | 586 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9051.75 | 243 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56162.1665 | 455 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U2-Forced - Delayed | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 105351.3328 | 740 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1549.1666 | 110 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 100-Fossil-Steam
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18771.5566 | 157.7 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18648.7466 | 156.1 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 7746.2331 | 562 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 27178.32 | 224.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 850-Combined Cycle Block
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 96581.4498 | 237 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 7520.1724 | 227.31 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 93771 | 230 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 28954.0332 | 218 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2095.5999 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2053.9999 | 156 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 1051.7332 | 272 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 851-CC GT units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 29783.16 | 118.8 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 6947.4999 | 210 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 943.6665 | 190 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 13911.1666 | 95 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | D1-Forced - Immediate | 852-CC steam units
0540 | Hot reheat steam piping up to turbine stop valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 107572.8332 | 262 | 1 | 1 | 0540-Hot reheat steam piping up to turbine stop valves | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 5731.7665 | 461 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 26052.1328 | 824 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 57699.1564 | 358.9 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U2-Forced - Delayed | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 145687.5 | 375 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2794.65 | 93 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5307.2 | 85.6 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 100-Fossil-Steam
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 5186.1332 | 272 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 35.7332 | 134 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 4792.6666 | 260 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 850-Combined Cycle Block
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 14538.5832 | 147.5 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 14391.75 | 155 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 38786.85 | 157 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 9334.9333 | 184 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 14536.125 | 147.5 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 851-CC GT units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 33016.5 | 330 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 16447.2 | 178 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 144.2998 | 234 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 248.7332 | 182 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 5732.8666 | 113 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 5463.192 | 34.72 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 852-CC steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 72312.5 | 178 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 861-CoG GT units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 74086.5665 | 178 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 861-CoG GT units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 365.8 | 118 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 862-CoG steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 20.9 | 114 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | D1-Forced - Immediate | 862-CoG steam units
0541 | Cold reheat steam piping up to boiler | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 88403.4 | 214 | 1 | 1 | 0541-Cold reheat steam piping up to boiler | U1-Forced - Immediate | 862-CoG steam units
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 807.3 | 46 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2725.2329 | 662 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9444.2666 | 76 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1088.75 | 15 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 58.9 | 38 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 86.4166 | 61 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 510.9833 | 23 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5382.0666 | 28 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 469.8 | 162 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 912.5999 | 162 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8777.5665 | 214 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 181.9999 | 168 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6899.3332 | 262 | 1 | 1 | 0550-Reheat steam relief/safety valves | U3-Forced - Postponed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3724.8 | 72 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Summer | 824.412 | 40.02 | 1 | 1 | 0550-Reheat steam relief/safety valves | U1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 51.6 | 72 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 323 | 30 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 853.6666 | 65 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1170 | 72 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 100-Fossil-Steam
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1109.9833 | 21.8 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 17375.3997 | 378 | 1 | 1 | 0550-Reheat steam relief/safety valves | U2-Forced - Delayed | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 23.9999 | 180 | 1 | 1 | 0550-Reheat steam relief/safety valves | D1-Forced - Immediate | 851-CC GT units
0550 | Reheat steam relief/safety valves | HRSG Boiler | HRSG Boiler Piping System | D2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 11399.7332 | 248 | 1 | 1 | 0550-Reheat steam relief/safety valves | D2-Forced - Delayed | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 18496.1833 | 247 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9923.3329 | 650 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 48.3165 | 223 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10826.75 | 635 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 372.45 | 573 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 840 | 420 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 15690.2331 | 614.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 688.4999 | 243 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 22071.1998 | 282 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 6408.0498 | 573 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 645.1663 | 490 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 5330 | 260 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 878.5998 | 573 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 489.0997 | 438 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 18259.5996 | 573 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 638.4 | 228 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 850-Combined Cycle Block
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 3401.2332 | 167 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 6822.9 | 189 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 6103.9082 | 180.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 6747.4166 | 215 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3102 | 330 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 15986.6666 | 176 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 116.625 | 155.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 12767.3666 | 180.5 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 421.2 | 162 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 538 | 269 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1767 | 155 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 81.4 | 148 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 16714.3 | 463 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3217.9332 | 158 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 58.3 | 106 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 4915.3333 | 40 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3651.45 | 99 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 766.8332 | 215 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 224 | 112 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 12115.2 | 128 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 127.4999 | 153 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 114.75 | 153 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 474.9998 | 285 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 57.33 | 163.8 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0560 | Other hot reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 6228.4 | 184 | 1 | 1 | 0560-Other hot reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 10400 | 80 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 53.1299 | 289.8 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 100-Fossil-Steam
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 53814.4165 | 366.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2392.5 | 290 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 850-Combined Cycle Block
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 261.8361 | 221.27 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 372.6666 | 172 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 65.3333 | 7 | 2 | 2 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 638 | 232 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 643.5 | 234 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2285.3998 | 234 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 1060.6666 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2265.8665 | 232 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1992.3 | 229 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 344 | 215 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2036.6498 | 231 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4082.4 | 189 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 851-CC GT units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 682 | 248 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 390.5498 | 321 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 317.6249 | 157.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2153.0165 | 247 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 971.2499 | 157.5 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 2422.1332 | 248 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1335.5666 | 103 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3735.4999 | 186 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 223.1666 | 103 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 14768.7497 | 417 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 2958.6666 | 317 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 177.6665 | 410 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | U1-Forced - Immediate | 852-CC steam units
0561 | Other cold reheat steam valves (not including turbine stop or intercept valves) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 248.4999 | 210 | 1 | 1 | 0561-Other cold reheat steam valves (not including turbine stop or intercept valves) | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 646.6666 | 80 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 346.2666 | 106 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 16660 | 350 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 94.5832 | 227 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7412.5333 | 56 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171.4166 | 55 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 50 | 25 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3986 | 10 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 41404.53 | 65.41 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 149.3333 | 56 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 392 | 56 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 793.2333 | 106 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1971.6 | 106 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4927.52 | 47.38 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 100-Fossil-Steam
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 605.7332 | 236 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 850-Combined Cycle Block
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 580.8 | 96.8 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 27.4666 | 206 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 13126.3332 | 212 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 333.4666 | 164 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 188.8332 | 206 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 99.8999 | 162 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 985.4166 | 215 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 10083.9266 | 122.8 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 89.9999 | 135 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 826.4666 | 161 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 851-CC GT units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3.5666 | 107 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 413.25 | 285 | 1 | 1 | 0570-Other reheat steam problems | U1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 3114.6 | 36 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9547.9999 | 120 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1704 | 160 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0570 | Other reheat steam problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 6450.6666 | 160 | 1 | 1 | 0570-Other reheat steam problems | D1-Forced - Immediate | 852-CC steam units
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2730 | 140 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20836.0413 | 485.5 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12527.9515 | 559.7 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3347.2633 | 94.6 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7754.0196 | 553.2 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1149.84 | 159.7 | 1 | 1 | 0580-Desuperheater/attemperator piping | D1-Forced - Immediate | 100-Fossil-Steam
0580 | Desuperheater/attemperator piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9106.35 | 551.9 | 1 | 1 | 0580-Desuperheater/attemperator piping | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1937.9999 | 427.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10713.9164 | 415 | 1 | 1 | 0590-Desuperheater/attemperator valves | U3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2894.6663 | 520 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 8873.5 | 30 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 804 | 67 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4601.3332 | 340 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2877.3 | 417 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 12687.5 | 250 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2273.6998 | 234 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 527.3332 | 140 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1497.25 | 28.25 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 135.8 | 194 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4930.8 | 168 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 71.3 | 69 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2402.5331 | 296 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1139.9997 | 427.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1615.05 | 291 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3559.3532 | 322.6 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3360 | 192 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7068.7999 | 192 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16846.35 | 69 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10628.3398 | 552.6 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 159.18 | 227.4 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 695.5 | 107 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8488.15 | 69 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1135.9999 | 106.5 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11474.1665 | 350 | 1 | 1 | 0590-Desuperheater/attemperator valves | U2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7.7 | 33 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1288.0833 | 205 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7306.45 | 57 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11813.25 | 57 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3549.2832 | 216.2 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7974.3 | 57 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6164 | 134 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3957.6 | 291 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17385.0499 | 339 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 150 | 75 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3666.9597 | 475.2 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 487.7333 | 118 | 1 | 1 | 0590-Desuperheater/attemperator valves | D2-Forced - Delayed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1433.2331 | 277.4 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 72.45 | 9 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3009.3331 | 296 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2502.5 | 350 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9221.3332 | 448 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.1999 | 84 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2022.6666 | 296 | 1 | 1 | 0590-Desuperheater/attemperator valves | D3-Forced - Postponed | 100-Fossil-Steam
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 599.8331 | 305 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 335396.25 | 525 | 1 | 1 | 0590-Desuperheater/attemperator valves | U1-Forced - Immediate | 650-Fluidized Bed
0590 | Desuperheater/attemperator valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 312 | 39 | 1 | 1 | 0590-Desuperheater/attemperator valves | D1-Forced - Immediate | 800-Miscellaneous
0610 | Desuperheater/attemperator drums | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 925.1923 | 208.69 | 1 | 1 | 0610-Desuperheater/attemperator drums | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1975.05 | 693 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1214.205 | 398.1 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 906.6697 | 383.1 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 160.7664 | 689 | 1 | 1 | 0620-Other desuperheater/attemperator problems | D1-Forced - Immediate | 100-Fossil-Steam
0620 | Other desuperheater/attemperator problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2874.3 | 429 | 1 | 1 | 0620-Other desuperheater/attemperator problems | U1-Forced - Immediate | 650-Fluidized Bed
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 60962.4998 | 750 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0630 | Startup bypass system piping (including drain lines up to heaters or condenser) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 177.9 | 593 | 1 | 1 | 0630-Startup bypass system piping (including drain lines up to heaters or condenser) | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4395.0665 | 554 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8448.5 | 554 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1213.3331 | 700 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3455.6 | 652 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13365 | 660 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11703.4661 | 832 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12588.3329 | 650 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 149460.9164 | 355 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20508.8 | 832 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3818.1662 | 739 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 416.79 | 757.8 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24494.1665 | 650 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1514.95 | 739 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62876.8331 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188135.43 | 770.1 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1317.8831 | 739 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6127.4994 | 855 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4480.3996 | 552 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1798.2331 | 739 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.525 | 510.1 | 1 | 1 | 0640-Startup bypass system valves | D1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2463.3331 | 739 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1225.4997 | 855 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1231.6662 | 739 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111434.9995 | 765 | 1 | 1 | 0640-Startup bypass system valves | U2-Forced - Delayed | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20661.2 | 658 | 1 | 1 | 0640-Startup bypass system valves | SF-Startup Failure | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2097.6666 | 290 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 100-Fossil-Steam
0640 | Startup bypass system valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Summer | 160.9498 | 261 | 1 | 1 | 0640-Startup bypass system valves | U1-Forced - Immediate | 800-Miscellaneous
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7.5833 | 35 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | D1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2261.17 | 1330.1 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15254 | 580 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3170.0712 | 1330.1 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0650 | Startup bypass tanks or flash tanks | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1751.2974 | 1330.1 | 1 | 1 | 0650-Startup bypass tanks or flash tanks | U1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.75 | 19 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1155 | 55 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 100-Fossil-Steam
0670 | Feedwater piping downstream of feedwater regulating valve | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 117 | 20 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 800-Miscellaneous
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 788.04 | 159.2 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 358 | 179 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1852.5999 | 177 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | U1-Forced - Immediate | 851-CC GT units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 737.55 | 149 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 178 | 89 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0670 | Feedwater piping downstream of feedwater regulating valve | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3447.4916 | 60.5 | 1 | 1 | 0670-Feedwater piping downstream of feedwater regulating valve | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3599 | 61 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 52.9666 | 90.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15396.3333 | 220 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 902.8665 | 467 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 170.6666 | 64 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2227.5 | 165 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 1542.9166 | 115 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3058.6033 | 65.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88253.9 | 406.7 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U2-Forced - Delayed | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 50789.3333 | 214 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 100-Fossil-Steam
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 62.8833 | 77 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 1353.6079 | 274.38 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 124.5998 | 267 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 137.9498 | 267 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2702.2666 | 104 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 727.107 | 274.38 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 5444.6056 | 277.55 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 3183.1996 | 552 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 321.8666 | 142 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 111.2333 | 142 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 850-Combined Cycle Block
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4236.29 | 31.8 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 40 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1622.5999 | 183 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 532.95 | 49.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 2572.4999 | 126 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4584.8971 | 159.29 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1658.0665 | 187 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 6421.45 | 147 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 10244.95 | 61 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 3280.3332 | 260 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 51.925 | 46.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 851-CC GT units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 4865.0633 | 31.3 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 1235.2083 | 60.5 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Summer | 3494.6666 | 80 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4744.9324 | 164.85 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 244.3333 | 10 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1587.1332 | 179 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 1753.7166 | 139 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 29.8708 | 26.75 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | D1-Forced - Immediate | 852-CC steam units
0680 | Feedwater valves (not feedwater regulating valve) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 4706 | 181 | 1 | 1 | 0680-Feedwater valves (not feedwater regulating valve) | U1-Forced - Immediate | 861-CoG GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5.7 | 19 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3091.2 | 644 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 186.6666 | 175 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.59999 | 9 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3.75 | 9 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.0667 | 44 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 158.4 | 144 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 72.0666 | 94 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 75.5416 | 92.5 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2 | 4 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2611.6832 | 349 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 100-Fossil-Steam
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Winter | 7881.9999 | 105 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 800-Miscellaneous
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 467.0999 | 162 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 851-CC GT units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 9 | 90 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 121.5 | 90 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | D1-Forced - Immediate | 852-CC steam units
0690 | Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Winter | 221.6 | 48 | 1 | 1 | 0690-Other feedwater problems downstream of feedwater regulating valve (use codes 3401 to 3499 for remainder of feedwater system) | U1-Forced - Immediate | 861-CoG GT units
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19768.3331 | 580 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11466.6497 | 814.2 | 1 | 1 | 0700-Blowdown system valves A | SF-Startup Failure | 100-Fossil-Steam
0700 | Blowdown system valves A | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 3678.9333 | 64 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 800-Miscellaneous
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 118.8332 | 230 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 3606.2 | 247 | 1 | 1 | 0700-Blowdown system valves A | U1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 18.15 | 99 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 851-CC GT units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1858.4333 | 127 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0700 | Blowdown system valves A | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 11.3355 | 61.83 | 1 | 1 | 0700-Blowdown system valves A | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 133926 | 505 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14191.6665 | 262 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64809.4 | 335.8 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 113368.6664 | 412 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 12413.9165 | 455 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 74263.3 | 614 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1969.3665 | 262 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1733.3333 | 160 | 1 | 1 | 0710-Blowdown system piping B | SF-Startup Failure | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 989.3333 | 160 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 100-Fossil-Steam
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4868.8 | 179 | 1 | 1 | 0710-Blowdown system piping B | U2-Forced - Delayed | 100-Fossil-Steam
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 8704.4333 | 223 | 1 | 1 | 0710-Blowdown system piping B | U1-Forced - Immediate | 851-CC GT units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1330.3333 | 52 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3961.8833 | 101.5 | 1 | 1 | 0710-Blowdown system piping B | D1-Forced - Immediate | 852-CC steam units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Gas | GG | 861 | CoG GT units | WECC | Summer | 6006 | 165 | 1 | 1 | 0710-Blowdown system piping B | U3-Forced - Postponed | 861-CoG GT units
0710 | Blowdown system piping B | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 4331.6 | 119 | 1 | 1 | 0710-Blowdown system piping B | D3-Forced - Postponed | 862-CoG steam units
0720 | Blowdown system controls / instrumentation | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 555.75 | 171 | 1 | 1 | 0720-Blowdown system controls / instrumentation | D1-Forced - Immediate | 100-Fossil-Steam
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 78.5466 | 54.8 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4251.8399 | 154.8 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 4331.4932 | 157.7 | 1 | 1 | 0730-Other blowdown system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 148.5 | 49.5 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 185.4066 | 54.8 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0730 | Other blowdown system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 386.75 | 65 | 1 | 1 | 0730-Other blowdown system problems | D1-Forced - Immediate | 852-CC steam units
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 385 | 44 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25461.27 | 108.6 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 215495.4666 | 224 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8904.4 | 452 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8103.3333 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3456.1 | 107 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 19472.9331 | 374 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7200 | 600 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7827.5 | 310 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 20083.7846 | 86.78 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 600 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18491.2 | 416 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1010 | 505 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1821.6 | 9.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1985.115 | 9.9 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14980.3332 | 260 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14556.6667 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3719.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 124186.6667 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 526.3333 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 833.7 | 397 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2290 | 200 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 644.9999 | 450 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5175 | 225 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 870 | 232 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6144 | 128 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3669.5 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35833.9996 | 615 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 630 | 450 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 562.5 | 450 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 730.0999 | 294 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2712.5 | 310 | 1 | 1 | 0740-Boiler recirculation pumps | U1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 652.2963 | 86.78 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 28.3333 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 454.6667 | 44 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3359.9167 | 5 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5759.6667 | 20 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14570.1332 | 544 | 1 | 1 | 0740-Boiler recirculation pumps | U2-Forced - Delayed | 100-Fossil-Steam
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 4868.85 | 21 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 800-Miscellaneous
0740 | Boiler recirculation pumps | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 541.1 | 14 | 1 | 1 | 0740-Boiler recirculation pumps | D1-Forced - Immediate | 800-Miscellaneous
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 603.1999 | 174 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 634.8 | 552 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 189.9167 | 5 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 126.5833 | 7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 44109.4 | 446 | 1 | 1 | 0741-Boiler recirculation pumps - motors | SF-Startup Failure | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 386.4 | 552 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 57.2833 | 7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2756.25 | 15 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.2 | 12 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16548.1333 | 104 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4565.5 | 15 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 195.255 | 86.78 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 565.95 | 7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 53384.9999 | 450 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6292.8 | 552 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 511.1333 | 187 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D2-Forced - Delayed | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1963.85 | 7 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 6795.4667 | 17 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 340860 | 380 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 53084.9997 | 450 | 1 | 1 | 0741-Boiler recirculation pumps - motors | U1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1978.6665 | 265 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0741 | Boiler recirculation pumps - motors | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1894.4433 | 103.9 | 1 | 1 | 0741-Boiler recirculation pumps - motors | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 157.6167 | 7 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 241.6 | 2 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 356.4997 | 465 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14 | 4 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 220.1667 | 10 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 406783.55 | 173 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 162.5 | 5 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4761.4999 | 267 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2497.8666 | 272 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 25186.9328 | 824 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | U1-Forced - Immediate | 100-Fossil-Steam
0742 | Boiler recirculation pumps - motors - cooling system | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3241.3332 | 272 | 1 | 1 | 0742-Boiler recirculation pumps - motors - cooling system | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 975 | 300 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | D1-Forced - Immediate | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21932.0999 | 162 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U2-Forced - Delayed | 100-Fossil-Steam
0750 | Boiler recirculation piping including downcomers | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 51099.9998 | 750 | 1 | 1 | 0750-Boiler recirculation piping including downcomers | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 157 | 60 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5100 | 510 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 780 | 260 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 51631.6666 | 260 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4861.8 | 73 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1183.8166 | 73 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 241592.7167 | 29 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 100-Fossil-Steam
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 1609.5345 | 270.51 | 1 | 1 | 0760-Boiler recirculation valves | SF-Startup Failure | 850-Combined Cycle Block
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 813.1665 | 238 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 851-CC GT units
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 149.1666 | 179 | 1 | 1 | 0760-Boiler recirculation valves | U1-Forced - Immediate | 851-CC GT units
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 116.6666 | 140 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 852-CC steam units
0760 | Boiler recirculation valves | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 546.6666 | 160 | 1 | 1 | 0760-Boiler recirculation valves | D1-Forced - Immediate | 852-CC steam units
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5007.6664 | 415 | 1 | 1 | 0770-Other boiler recirculation problems | U1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15851.2 | 12 | 1 | 1 | 0770-Other boiler recirculation problems | D1-Forced - Immediate | 100-Fossil-Steam
0770 | Other boiler recirculation problems | HRSG Boiler | HRSG Boiler Piping System | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 100.5832 | 355 | 1 | 1 | 0770-Other boiler recirculation problems | SF-Startup Failure | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6791.1499 | 213 | 1 | 1 | 0775-Economizer piping | U2-Forced - Delayed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 18135.2333 | 178 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 150.6666 | 113 | 1 | 1 | 0775-Economizer piping | D3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | Boiler | Boiler Piping System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 19939.05 | 531 | 1 | 1 | 0775-Economizer piping | U3-Forced - Postponed | 100-Fossil-Steam
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 7788.5498 | 231 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 850-Combined Cycle Block
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 540 | 36 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 7308.7999 | 171.3 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 786.9 | 183 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 4762.5 | 150 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 851-CC GT units
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 3417 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 3111 | 51 | 1 | 2 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 14579 | 244 | 1 | 1 | 0775-Economizer piping | D1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 2703 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Winter | 2142 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 2652 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0775 | Economizer piping | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 2499 | 51 | 1 | 1 | 0775-Economizer piping | U1-Forced - Immediate | 860-Co-generator Block
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216434.4496 | 1257 | 1 | 1 | 0780-Headers between tube bundles | U2-Forced - Delayed | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 116883.45 | 1231 | 1 | 1 | 0780-Headers between tube bundles | U2-Forced - Delayed | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 1664.7514 | 228.57 | 1 | 1 | 0780-Headers between tube bundles | D1-Forced - Immediate | 100-Fossil-Steam
0780 | Headers between tube bundles | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 410.4 | 18 | 1 | 1 | 0780-Headers between tube bundles | U1-Forced - Immediate | 650-Fluidized Bed
0780 | Headers between tube bundles | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 3961.9332 | 134 | 1 | 1 | 0780-Headers between tube bundles | D1-Forced - Immediate | 852-CC steam units
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 252.3665 | 226 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 465.8 | 274 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | D1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 4835.8333 | 175 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U1-Forced - Immediate | 100-Fossil-Steam
0790 | Pipe hangers; brackets; supports (general) | HRSG Boiler | HRSG Boiler Piping System | U2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 15965.1625 | 378.92 | 1 | 1 | 0790-Pipe hangers; brackets; supports (general) | U2-Forced - Delayed | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11660.1965 | 206.68 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 860.7666 | 31 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 24144.2498 | 741 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 7425 | 25 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9034.3052 | 245.72 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9292.7879 | 158.22 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 38917.7362 | 213.17 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 39201.8033 | 214.12 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10081.75 | 245 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43354.22 | 406.7 | 1 | 1 | 0799-Other miscellaneous piping system problems | U2-Forced - Delayed | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 15209.8451 | 241.49 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 150 | 25 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1003.75 | 25 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 100-Fossil-Steam
0799 | Other miscellaneous piping system problems | Boiler | Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | MRO | Winter | 1865880 | 213 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 800-Miscellaneous
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 4947 | 340 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2468.3999 | 122.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 4073.88 | 122.4 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2157.9433 | 45.8 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 850-Combined Cycle Block
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 495 | 45 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 548.9332 | 179 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 568.75 | 175 | 1 | 1 | 0799-Other miscellaneous piping system problems | U1-Forced - Immediate | 851-CC GT units
0799 | Other miscellaneous piping system problems | HRSG Boiler | HRSG Boiler Piping System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1600 | 75 | 1 | 1 | 0799-Other miscellaneous piping system problems | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 14281.6664 | 836 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 823.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 553.4997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 635 | 635 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17326.05 | 609 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 242.3497 | 393 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 386.54 | 351.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1007.5 | 310 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1491.6 | 339 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 283.5 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3869.6665 | 247 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 524.16 | 166.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 683.4333 | 141.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3036.8799 | 191.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5410.9066 | 141.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 57 | 380 | 1 | 1 | 0800-Drums and drum internals (single drum only) | SF-Startup Failure | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472.4997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 830.25 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 823.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 276.7499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1026.5829 | 635 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3116 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4730 | 860 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12490.9832 | 523 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57.42 | 191.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 449.4832 | 149 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 867.64 | 65.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4319.1864 | 841.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 518.2468 | 208.69 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1932 | 336 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 841.7163 | 208.69 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124.1333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 202.6667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 30191.8332 | 535 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1776.5 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 29.75 | 119 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.2333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 648 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 136625.5197 | 840.6 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 567 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 9437.5 | 125 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6455.9332 | 179 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 209.2497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1066.4999 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 336.9333 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 930.3667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 508.6665 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3426.9667 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22770.0996 | 654 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 317.5464 | 366.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.4 | 36 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8049.0332 | 179 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 385.71 | 41.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 506.6833 | 141.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 654.7497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1420.425 | 481.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 479.2499 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4715.3333 | 220 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U2-Forced - Delayed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 284.75 | 335 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1053.8845 | 208.69 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3808.41 | 131.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 67.4997 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 330.7497 | 405 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 13972.4163 | 535 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 380 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 951.9 | 38 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11812.5066 | 241.4 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 354.6665 | 280 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14492.4997 | 510 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 38.475 | 24.3 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 650-Fluidized Bed
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 540.8539 | 98.04 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 353.8333 | 77.2 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 850-Combined Cycle Block
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1613.6666 | 206 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 8478.5832 | 355 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 76.9164 | 355 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 117.6 | 168 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 11373.6665 | 229 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 14343.0333 | 229 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 50.4 | 126 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 575.7666 | 46 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 851-CC GT units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 15435.6831 | 300.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 24.2 | 60.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 1093.1833 | 107 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 28.5 | 190 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 90.8332 | 218 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 186.6832 | 243.5 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1692.8166 | 150.25 | 1 | 1 | 0800-Drums and drum internals (single drum only) | D1-Forced - Immediate | 852-CC steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 22.3333 | 26.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 36.6266 | 26.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 28.5866 | 26.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0800 | Drums and drum internals (single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 1223.8666 | 26.8 | 1 | 1 | 0800-Drums and drum internals (single drum only) | U1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U3 | Forced - Postponed | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 2642.3833 | 29 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U3-Forced - Postponed | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 219.1 | 313 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Summer | 11.375 | 19.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 1570.2165 | 313 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Winter | 9.75 | 19.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 2011.7333 | 64 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 180.5 | 47.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2681.9465 | 360.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 4701.6664 | 325 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 146.8699 | 231.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 55.7466 | 90.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 4514.3331 | 290 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 252 | 63 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 331.3 | 331.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 344.6331 | 422 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 7.05 | 141 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 87.3 | 291 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 34.5 | 90 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 319.0733 | 45.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 487.4664 | 457 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 18.8733 | 29.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 152 | 114 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 28.6233 | 27.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2667.4998 | 291 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 124.0166 | 212.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 272 | 272 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 132.875 | 106.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 614.1663 | 550 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 143.8164 | 663.77 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 182.8665 | 422 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 449.25 | 119.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 12.0533 | 90.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 585.375 | 156.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 24.3666 | 86 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 1556.01 | 172.89 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 52.625 | 42.1 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3667.3199 | 164.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 5.425 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 16335.8997 | 378 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 894.25 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 43.5833 | 104.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 334 | 167 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 26.4 | 48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 550.3999 | 258 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7.75 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 17.5 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 1662.2499 | 183 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 200.3849 | 164.7 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 28.16 | 51.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 11.625 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 31.775 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 296.0833 | 187 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 23.3333 | 35 | 4 | 4 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 110.4 | 48 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 117.76 | 51.2 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 199.0332 | 170.6 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 18.0833 | 35 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 172.3165 | 211 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 140.25 | 55 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 86.295 | 156.9 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 126.35 | 361 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 6.2 | 46.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 3512.6 | 182 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2.25 | 5.4 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 3079.2299 | 195.3 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 8771.8166 | 161 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 21356.9332 | 248 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 10998.3 | 122 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3.825 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 2594.8855 | 194.86 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 7.2999 | 219 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 890.1666 | 98 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 116.7999 | 219 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 17.425 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 195.7499 | 405 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 4951.0997 | 462 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 1286.1333 | 104 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 219 | 219 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3.4 | 25.5 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 2007.2 | 104 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 136.2999 | 282 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 32.6666 | 49 | 2 | 2 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 16619.1666 | 275 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 237.048 | 139.44 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 190.5166 | 161 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 24580.5833 | 85 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 141.9 | 86 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 215 | 215 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1734.3333 | 110 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3.1208 | 26.75 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 203.9333 | 38 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Winter | 19.5 | 39 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 4695.0333 | 83 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | MRO | Off-Peak | 7620 | 254 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 860-Co-generator Block
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 93.4999 | 165 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 121.8 | 174 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 71.4 | 102 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 862-CoG steam units
0801 | HP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 26.8 | 26.8 | 1 | 1 | 0801-HP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 862-CoG steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 1822.8 | 248 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0802 | IP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 140.5332 | 248 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0802 | IP Drum (including drum level trips not attributable to other causes) | NULL | NULL | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | MRO | Off-Peak | 101.6499 | 160.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 800-Miscellaneous
0802 | IP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Winter | 1898.8665 | 313 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 43.7882 | 202.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 76.0465 | 207.4 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 402.5 | 350 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 42.52 | 212.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 396.6664 | 340 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 84.2082 | 202.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 252.625 | 202.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 301.6066 | 196.7 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 640.5 | 366 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1124.6663 | 602.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 29.45 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 2.325 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 496.899 | 254.82 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2045.8333 | 50 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2.325 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 92.3166 | 191 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 16.5366 | 45.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3.1 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 167.9765 | 219.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 12.4 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 2545.9999 | 142.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U2-Forced - Delayed | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 25.5558 | 117.95 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2725.9999 | 174 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3.1 | 46.5 | 1 | 2 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 530.8749 | 254.82 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3.875 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 150.15 | 214.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 169.68 | 161.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 12702.0833 | 175 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 195.9999 | 168 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 20836.6666 | 175 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 136.5 | 182 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 194.6032 | 147.8 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 20.535 | 136.9 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 5023.55 | 217 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 2453.3749 | 142.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 19.375 | 46.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 8.5345 | 39.39 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 2440.16 | 161.6 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 189.125 | 151.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 103.4999 | 135 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 832.9749 | 214.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 109.6666 | 94 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 109.7431 | 299.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 420.0155 | 178.73 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 45.9166 | 95 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 14.7066 | 110.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 92.9966 | 121.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1.3375 | 26.75 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 87.75 | 117 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 190.9166 | 145 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 473.6345 | 178.73 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 10.625 | 25.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 16.15 | 25.5 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1.32 | 19.8 | 1 | 2 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 6.8666 | 25.75 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Winter | 119.1664 | 325 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 4104.6665 | 262 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3680.85 | 159 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1.7833 | 26.75 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 119.72 | 299.3 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1.65 | 19.8 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 377.0866 | 238.16 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 860-Co-generator Block
0802 | IP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 1002.1215 | 192.1 | 1 | 1 | 0802-IP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | NULL | NULL | U1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | SERC | Off-Peak | 69.3333 | 64 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 800-Miscellaneous
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 92.1 | 307 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 1125.6665 | 307 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 11.5999 | 174 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 220.8332 | 265 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 177.9331 | 314 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 225 | 75 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 850-Combined Cycle Block
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 1053.3333 | 160 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4810.4332 | 221 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 71.12 | 38.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 73.025 | 38.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 781.4333 | 238 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3220 | 161 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 7.155 | 143.1 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | SF-Startup Failure | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 208.5333 | 136 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 501.3333 | 160 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 851-CC GT units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 144.6665 | 310 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Summer | 2786.1332 | 128 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 34.8333 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 305.15 | 51 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 240.6665 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 7698.75 | 45 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | D1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 199.5 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 184 | 120 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 79.1665 | 190 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 455.8998 | 282 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 852-CC steam units
0803 | LP Drum (including drum level trips not attributable to other causes) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 344.76 | 66.3 | 1 | 1 | 0803-LP Drum (including drum level trips not attributable to other causes) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1047.75 | 99 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10323.3666 | 302 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 100-Fossil-Steam
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 7486.05 | 429 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 650-Fluidized Bed
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 95245.4 | 244 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | D1-Forced - Immediate | 650-Fluidized Bed
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Winter | 114824 | 24 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 557.55 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 138.25 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 2073.05 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 16.1 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 250.95 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 895.65 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 533.4 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0810 | Boiler supports and structures (use code 1320 for tube supports) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | NPCC | Summer | 534.8 | 21 | 1 | 1 | 0810-Boiler supports and structures (use code 1320 for tube supports) | U1-Forced - Immediate | 861-CoG GT units
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2673.68 | 17.59 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9714.54 | 21.54 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10046.52 | 25.37 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27689.3666 | 311 | 1 | 1 | 0820-Casing | U3-Forced - Postponed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 554.1666 | 350 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 27260.9998 | 270 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 18967.5 | 270 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 40824.9998 | 750 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2119.4333 | 73 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 13816.3666 | 98 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 149.3499 | 87 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7576.45 | 21 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2379.3 | 22.66 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 21000 | 750 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15081.25 | 125 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 482.85 | 13.05 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1079.1 | 11.99 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8241.4757 | 25.22 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1109.06 | 24.11 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1880.36 | 16.21 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 956.34 | 39.6 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 911.3133 | 94.6 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14151.1333 | 46 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 127260.0499 | 177 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9743.2 | 25.64 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 240 | 10 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2408.64 | 23.16 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15852.05 | 107 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 34073 | 52 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6528.6 | 25.11 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 935.74 | 15.34 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1885 | 650 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 100372.8 | 528 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7716.6665 | 500 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5114.64 | 24.24 | 1 | 1 | 0820-Casing | D2-Forced - Delayed | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8469.05 | 107 | 1 | 1 | 0820-Casing | U1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15500 | 125 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 100-Fossil-Steam
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 28 | 14 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 650-Fluidized Bed
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Off-Peak | 4639.5832 | 131 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Off-Peak | 870 | 150 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Off-Peak | 4269.1999 | 156 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | RFC | Summer | 885 | 118 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 800-Miscellaneous
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 32023.3332 | 520 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 850-Combined Cycle Block
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 11.5 | 5 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 41.25 | 16.5 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 49.5 | 13.5 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 136.3383 | 17.9 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 238.65 | 43 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 13.8 | 6 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 36.25 | 14.5 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 6.9 | 3 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0820 | Casing | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 42.1667 | 11.5 | 1 | 1 | 0820-Casing | D1-Forced - Immediate | 851-CC GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 12663.2 | 48 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 100 | 125 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15676.2663 | 532 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8576.5331 | 416 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 100-Fossil-Steam
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 477.36 | 122.4 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 1033.0832 | 192.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 9562.6666 | 320 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 803.7166 | 116.2 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2290.1666 | 105.7 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 850-Combined Cycle Block
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 125.25 | 167 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 3512.5666 | 167 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 19656.3398 | 310.2 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 571.6667 | 35 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 133 | 35 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 851-CC GT units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Summer | 10832.4333 | 170.5 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 4076.7999 | 192 | 1 | 1 | 0830-Doors | U2-Forced - Delayed | 852-CC steam units
0830 | Doors | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 881.25 | 75 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 852-CC steam units
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | SERC | Summer | 87.3 | 18 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 860-Co-generator Block
0830 | Doors | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 1410 | 100 | 1 | 1 | 0830-Doors | U1-Forced - Immediate | 861-CoG GT units
0830 | Doors | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Summer | 831.9 | 59 | 1 | 1 | 0830-Doors | D1-Forced - Immediate | 862-CoG steam units
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1937.3333 | 80 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 496.9999 | 210 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8326.5 | 273 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57791.6665 | 500 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18809.9998 | 270 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6856.3333 | 67 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 741.15 | 183 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30.9333 | 64 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 555822 | 360 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 95 | 5 | 1 | 1 | 0840-Refractory and insulation | D1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 26270.8332 | 250 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30488.7832 | 251.8 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0840 | Refractory and insulation | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2648.0667 | 44 | 1 | 1 | 0840-Refractory and insulation | U1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 320.4667 | 22 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 14332.89 | 371.8 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 75494.4331 | 333.8 | 1 | 1 | 0847-Other expansion joints | D1-Forced - Immediate | 650-Fluidized Bed
0847 | Other expansion joints | Boiler | Boiler Internals and Structures | D2 | Forced - Delayed | 2023 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 377.75 | 15 | 1 | 1 | 0847-Other expansion joints | D2-Forced - Delayed | 650-Fluidized Bed
0848 | Inlet panel | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 130.8666 | 52 | 1 | 1 | 0848-Inlet panel | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174937.4996 | 1350 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63709.1999 | 162 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 494.5415 | 357.5 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 95 | 15 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 100-Fossil-Steam
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 74 | 37 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 35234.0332 | 203 | 1 | 1 | 0850-Other internal or structural problems | U1-Forced - Immediate | 851-CC GT units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 685.75 | 39 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0850 | Other internal or structural problems | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1926.1333 | 16 | 1 | 1 | 0850-Other internal or structural problems | D1-Forced - Immediate | 852-CC steam units
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5346.45 | 327 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 78.75 | 45 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 228.6 | 12 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 813.4333 | 46 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 230.9333 | 32 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 749.25 | 45 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12720 | 600 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15213.4665 | 262 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 140.8331 | 338 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1.7333 | 13 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 255.15 | 27 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 376.85 | 3 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 821.3333 | 160 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 141 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3139.5 | 390 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3735 | 45 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30014 | 698 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1859.5 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 560 | 40 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 57.8667 | 2 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9372.9999 | 390 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | U1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9255.1799 | 341.1 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1246.2333 | 98 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 454.3 | 154 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D3-Forced - Postponed | 100-Fossil-Steam
0855 | Drum relief/safety valves (Single drum only) | Boiler | Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1503 | 30 | 1 | 1 | 0855-Drum relief/safety valves (Single drum only) | D1-Forced - Immediate | 100-Fossil-Steam
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 61.3333 | 32 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 10552 | 48 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 21.1983 | 7.9 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 5754.2332 | 182 | 1 | 1 | 0856-HP Drum relief/safety valves | U1-Forced - Immediate | 851-CC GT units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 2793.315 | 77.7 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0856 | HP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 3699.1499 | 117 | 1 | 1 | 0856-HP Drum relief/safety valves | D1-Forced - Immediate | 852-CC steam units
0857 | IP Drum relief/safety valves | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2328.8499 | 141 | 1 | 1 | 0857-IP Drum relief/safety valves | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 58028.533 | 494 | 1 | 1 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | Boiler | Boiler Internals and Structures | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65788.1997 | 486 | 1 | 1 | 0859-Tube external fins/membranes A | U2-Forced - Delayed | 100-Fossil-Steam
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 355.9342 | 21.55 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 7789.1664 | 325 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 242.7425 | 14.55 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 106.1108 | 28.55 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 243.2275 | 14.55 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 1067.77 | 28.55 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0859 | Tube external fins/membranes A | HRSG Boiler | HRSG Boiler Internals and Structures | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 780 | 65 | 1 | 1 | 0859-Tube external fins/membranes A | D1-Forced - Immediate | 850-Combined Cycle Block
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 177.59 | 30.1 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 552 | 24 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 178.5 | 34 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 3.3333 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 6.2333 | 11 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1667 | 333.4 | 1 | 1 | 0870-Soot blowers - steam | D3-Forced - Postponed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 156.6 | 29 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11574.42 | 271.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.4167 | 35 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 242.5333 | 68 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12848.2499 | 333 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.5 | 25 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 715.4766 | 271.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8889.1182 | 271.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 86287.5 | 90 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 631.7333 | 92 | 1 | 1 | 0870-Soot blowers - steam | D2-Forced - Delayed | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1455.3333 | 20 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 266.0833 | 103 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 86.3333 | 70 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 5 | 5 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2793.9816 | 271.7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 3.18 | 3.6 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 61.6666 | 50 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 186 | 120 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 902.5 | 190 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1274.7664 | 334 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 5.3333 | 6.4 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 100-Fossil-Steam
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 4.0333 | 2 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 31.7333 | 16 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 11.85 | 3 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 650-Fluidized Bed
0870 | Soot blowers - steam | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 25.55 | 7 | 1 | 1 | 0870-Soot blowers - steam | D1-Forced - Immediate | 800-Miscellaneous
0873 | Soot blower drives | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18.63 | 41.4 | 1 | 1 | 0873-Soot blower drives | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1496.7332 | 286 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.0333 | 17 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 554.3 | 241 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1802.4999 | 309 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9.9167 | 5 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9004.5 | 435 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 27.5 | 30 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.2 | 74 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 92.9233 | 91.4 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 439.1666 | 155 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.3332 | 134 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2396.3332 | 140 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44.7766 | 141.4 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 251.4666 | 164 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 578.2399 | 333.6 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2868.6666 | 104 | 1 | 1 | 0876-Soot blower controls | D2-Forced - Delayed | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7810.8329 | 650 | 1 | 1 | 0876-Soot blower controls | U1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 351 | 270 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1386 | 11 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.1666 | 139 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 96.25 | 75 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31 | 124 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.15 | 129 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.4666 | 149 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 100 | 100 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 127.6499 | 333 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 356.2666 | 64 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 100-Fossil-Steam
0876 | Soot blower controls | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 129.5 | 7 | 1 | 1 | 0876-Soot blower controls | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4591.6665 | 380 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 12 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14891.6665 | 500 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1312.1333 | 104 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 53.01 | 11.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 240 | 40 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 166.6667 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72.5333 | 68 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 78 | 15 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 50 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 475 | 10 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1723.6 | 13.9 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 933 | 93.3 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1757 | 251 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 777.7 | 141.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 58.717 | 24.81 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 46.6667 | 35 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18085.8766 | 219.8 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 420.1533 | 21.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 118.6757 | 19.67 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9329 | 380 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52440 | 230 | 2 | 2 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1276.58 | 440.2 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 1665.6933 | 22.16 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | U1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9500 | 500 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 192.2833 | 83 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 158.1 | 34 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 35.3333 | 40 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2727.2732 | 261.4 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 140 | 40 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 708.5 | 54.5 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 812 | 11.6 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1819.8331 | 305 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D2-Forced - Delayed | 100-Fossil-Steam
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 2255.5 | 130 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 175.5 | 30 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 650-Fluidized Bed
0880 | Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 468 | 39 | 1 | 1 | 0880-Fly ash Removal System (not precipitators; scrubbers; mechanical collectors; or baghouses) | D1-Forced - Immediate | 800-Miscellaneous
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 123.0833 | 35 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3764.9716 | 199.91 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 100-Fossil-Steam
0885 | Fly ash Removal System - wet transport | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 7.4203 | 1.13 | 1 | 1 | 0885-Fly ash Removal System - wet transport | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 627.1665 | 530 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 282.91 | 297.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6874.5333 | 219.4 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13125.125 | 492.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1615.3666 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68213.3332 | 400 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3095.9998 | 270 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6550.25 | 492.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28727.4162 | 1331 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 157.3 | 14.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 310.5 | 23 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9342.4666 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1551.6999 | 157.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31120.75 | 702.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12578.6666 | 106 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 360 | 450 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1454.1 | 262 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1512.4995 | 750 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2662.47 | 307.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1.9 | 3.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21118.7664 | 406 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 63687.8664 | 406 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 744 | 248 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 51.5667 | 11.05 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1066.65 | 19.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2109.75 | 291 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2266.6666 | 100 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 760.2831 | 377 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 0 | 0 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 356.2499 | 171 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 39.5833 | 25 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 83.4 | 278 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D3-Forced - Postponed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5159.1833 | 107 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31207.8664 | 406 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3346.6665 | 200.8 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2431.9266 | 160.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10440 | 360 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15749.833 | 530 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5993.3332 | 310 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107882.2665 | 554 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U2-Forced - Delayed | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4603.75 | 317.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1203.4999 | 217.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8085.86 | 487.1 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2384.4998 | 285 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1079 | 78 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4145.2 | 86 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | U1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.1 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 121.3333 | 16 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 100-Fossil-Steam
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 17.3433 | 4.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 135.705 | 8.3 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 275.8 | 19.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 668.8 | 48 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 282.3667 | 19.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 128.05 | 19.7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 650-Fluidized Bed
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 565.5 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 27.5167 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 131.0833 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 429 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 97.5 | 10 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1316.25 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 137.8 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 165.75 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 40.6 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 60 | 12 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 21.6667 | 20 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 195 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 427.4666 | 28 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 30.1167 | 6.5 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 332.5 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 7.7 | 7 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 57.2 | 13 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 126.75 | 39 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 63 | 6 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 33.3 | 9 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 409.15 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 650.7333 | 43 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 289.8 | 21 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0890 | Bottom ash systems (wet or dry) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Winter | 366.85 | 11 | 1 | 1 | 0890-Bottom ash systems (wet or dry) | D1-Forced - Immediate | 800-Miscellaneous
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7892.5 | 154 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12498.5833 | 115 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1652.7665 | 277 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 153.6 | 18 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2677.6666 | 290 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2156 | 49 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6384.8331 | 290 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14712.6666 | 290 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 461269.1666 | 290 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3017.26 | 204.56 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 148378.5 | 290 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 4.05 | 3 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7227.7333 | 154 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 8.9167 | 5 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16866.7499 | 387 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | U3-Forced - Postponed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 273.3499 | 106.5 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 391.05 | 99 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D2-Forced - Delayed | 100-Fossil-Steam
0891 | Bottom ash hoppers (including gates) | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 518.2999 | 213 | 1 | 1 | 0891-Bottom ash hoppers (including gates) | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 226.6666 | 160 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7576.3332 | 140 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7237.7 | 461 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3538.3333 | 110 | 1 | 1 | 0892-Bottom ash clinker grinders | D1-Forced - Immediate | 100-Fossil-Steam
0892 | Bottom ash clinker grinders | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 72759.2 | 824 | 1 | 1 | 0892-Bottom ash clinker grinders | U2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 950.4533 | 227.2 | 1 | 1 | 0893-Bottom ash water pumps and motors | D2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1096 | 30 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 25354.2332 | 361 | 1 | 1 | 0893-Bottom ash water pumps and motors | U2-Forced - Delayed | 100-Fossil-Steam
0893 | Bottom ash water pumps and motors | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2050 | 410 | 1 | 1 | 0893-Bottom ash water pumps and motors | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1617 | 107.8 | 1 | 1 | 0894-Bottom ash piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13860 | 330 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0894 | Bottom ash piping and valves | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95 | 47.5 | 1 | 1 | 0894-Bottom ash piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 669.061 | 142.86 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3148.5415 | 317.5 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 628.9998 | 255 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 100-Fossil-Steam
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 30.1333 | 8 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 630 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 755.65 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 889 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 255 | 15 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 651 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0895 | Ashpit trouble | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 119 | 21 | 1 | 1 | 0895-Ashpit trouble | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 362.4999 | 435 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8583.333 | 515 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 6175.8 | 423 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 770.8333 | 50 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 819.9999 | 123 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2442 | 330 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1000 | 250 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80663.7495 | 705 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 38754.3 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13720.9831 | 613 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 205.6333 | 62 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 624.8666 | 206 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1396.35 | 321 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 9038.1664 | 427 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 194.4985 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 575.0998 | 243 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7239.8329 | 605 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 43508.7332 | 532 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 172.179 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3064.1 | 235.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4463.333 | 515 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26.3333 | 10 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4761.3498 | 363 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1105.5332 | 206 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 146.671 | 63.77 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 789.25 | 225.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40749 | 564 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9187.1 | 481 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 639.1999 | 204 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2194.7998 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 186 | 465 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 299.2665 | 268 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3635.5999 | 366 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3422.0498 | 267 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 22567.45 | 523 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 235.0832 | 403 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4990.7466 | 185.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1571.4 | 291 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 558.25 | 319 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D3-Forced - Postponed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3646.1996 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20896.2 | 564 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1245 | 249 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 908 | 227 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7087 | 380 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 220 | 100 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 398.43 | 209.7 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1475.7999 | 282 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1681.9 | 278 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34440 | 615 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30039.9996 | 600 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 462.5355 | 106.33 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1616.5 | 530 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 13018.8664 | 433 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3119.4164 | 451 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8279.025 | 330.5 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 598.4999 | 189 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 709.3333 | 190 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1341.2999 | 306 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1754.8998 | 327 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2492.4664 | 343 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9283.6498 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 858.1831 | 341 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4028.5932 | 349.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8078.9799 | 179.4 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5432.4 | 201.2 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 548.1 | 174 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 3852 | 12 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2183 | 370 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6893.0832 | 457 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 17832.7498 | 531 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | U2-Forced - Delayed | 100-Fossil-Steam
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1112.7433 | 46.3 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0897 | Bottom ash rotary (drag chain type) conveyor and motor | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 104 | 26 | 1 | 1 | 0897-Bottom ash rotary (drag chain type) conveyor and motor | D1-Forced - Immediate | 800-Miscellaneous
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2595.45 | 363 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3378.6666 | 140 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 9189.2665 | 461 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1738.5333 | 136 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.7333 | 94 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 100-Fossil-Steam
0898 | Bottom ash pyrite hopper (pulverizer reject) system | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 906.0903 | 37.78 | 1 | 1 | 0898-Bottom ash pyrite hopper (pulverizer reject) system | D1-Forced - Immediate | 650-Fluidized Bed
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 52796.2 | 554 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 36432.5 | 590 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 149458.9832 | 511 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1401.0966 | 77.48 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0900 | Slag-tap (cyclone furnace) | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81170.233 | 554 | 1 | 1 | 0900-Slag-tap (cyclone furnace) | U2-Forced - Delayed | 100-Fossil-Steam
0910 | Slag-tap (other than cyclone furnace) | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13232.9999 | 198 | 1 | 1 | 0910-Slag-tap (other than cyclone furnace) | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 39.75 | 4.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9196.8665 | 268 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 432 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3672 | 270 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 76.58 | 8.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 93.16 | 40.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 393.193 | 34.34 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 17.0617 | 2.9 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 0.78 | 1.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 10.3867 | 8.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 164.56 | 27.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 138.4366 | 59.33 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 354.5365 | 291.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 552.9333 | 11.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 37828.5405 | 208.69 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 85192.3331 | 580 | 1 | 1 | 0920-Other slag and ash removal problems A | U3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 488.9882 | 194.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 583.1467 | 30.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 530.8017 | 22.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76509.9996 | 600 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 26.5767 | 6.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 13.0517 | 4.1 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 40.227 | 17.49 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3419.4333 | 169 | 1 | 1 | 0920-Other slag and ash removal problems A | D2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 508.7499 | 165 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54392 | 416 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 419.1 | 139.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 199.1667 | 25 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2.6867 | 2.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 20 | 5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2349.5966 | 141.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6649.0416 | 222.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 9.18 | 2.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 66.6135 | 10.17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 3202.5519 | 123.81 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1054.3666 | 336.5 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 64.1667 | 10 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 51.8 | 5.6 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2306.025 | 249.3 | 1 | 1 | 0920-Other slag and ash removal problems A | D3-Forced - Postponed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 55335.2996 | 603 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4400 | 200 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 455 | 15 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2.58 | 1.2 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1230.855 | 264.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 20.5333 | 4.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 250 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 41.055 | 35.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 5553.1486 | 34.36 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 39.15 | 17.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1025.7499 | 165 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2307.3832 | 167 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 261 | 87 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 15.92 | 4.8 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57 | 57 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 703.4166 | 115 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 25.2233 | 9.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1051.5999 | 264 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3663 | 333 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 697.6749 | 194.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 24.7133 | 4.4 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 34.1367 | 7.7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41177.5 | 455 | 1 | 1 | 0920-Other slag and ash removal problems A | U2-Forced - Delayed | 100-Fossil-Steam
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Winter | 502.9167 | 17 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 762.1666 | 85 | 1 | 1 | 0920-Other slag and ash removal problems A | U1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2222.3833 | 43 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 10998 | 45 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 100.8 | 7 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 650-Fluidized Bed
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 773.3333 | 40 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 767 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 358.5833 | 13 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 535.6667 | 20 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0920 | Other slag and ash removal problems A | Boiler | Slag and Ash Removal | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 717.1667 | 26 | 1 | 1 | 0920-Other slag and ash removal problems A | D1-Forced - Immediate | 800-Miscellaneous
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 715 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 780 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 390 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0930 | Bed material coolers | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 260 | 32.5 | 1 | 1 | 0930-Bed material coolers | U1-Forced - Immediate | 650-Fluidized Bed
0933 | Bed material fans/blowers | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 467.2 | 24 | 1 | 1 | 0933-Bed material fans/blowers | D1-Forced - Immediate | 800-Miscellaneous
0936 | Bed material conveyors B | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 622.0666 | 43 | 1 | 1 | 0936-Bed material conveyors B | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 65.8667 | 38 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 519.2 | 88 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 2080 | 32.5 | 1 | 1 | 0950-Other bed material system problems | U1-Forced - Immediate | 650-Fluidized Bed
0950 | Other bed material system problems | Boiler | Bed Material Removal System (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 199.4666 | 68 | 1 | 1 | 0950-Other bed material system problems | D1-Forced - Immediate | 650-Fluidized Bed
0952 | Char reinjection piping/valves | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 275.52 | 4.8 | 1 | 1 | 0952-Char reinjection piping/valves | D1-Forced - Immediate | 650-Fluidized Bed
0982 | High pressure loop seal recirculation fan/blower controls | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 73.745 | 30.1 | 1 | 1 | 0982-High pressure loop seal recirculation fan/blower controls | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1874.0833 | 43 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 62.4 | 4.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 384.1333 | 43 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 871.528 | 37.92 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1020 | 34 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 229.9 | 20.9 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 20825.7706 | 100.64 | 1 | 1 | 0989-Other bed solids recirculation problems | U1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 906.0903 | 37.78 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 33.6 | 4.8 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 432 | 27 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 2250.6 | 36 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 906.0903 | 37.78 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 5385.75 | 43 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 623.5 | 43 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 4468.1793 | 37.24 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0989 | Other bed solids recirculation problems | Boiler | Bed Solids Recirculation (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 25.5 | 5.1 | 1 | 1 | 0989-Other bed solids recirculation problems | D1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 135826.2497 | 525 | 1 | 1 | 0990-Refractory | U1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 327.15 | 9 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 650-Fluidized Bed
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2018.5 | 110 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 10495.4999 | 90 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0990 | Refractory | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 6602.5 | 95 | 1 | 1 | 0990-Refractory | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 3257.2333 | 38 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1212.57 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1903.5 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2300.4 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2505.33 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D3 | Forced - Postponed | 2023 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 342.6666 | 40 | 1 | 1 | 0991-Tube leaks | D3-Forced - Postponed | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1684.395 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1950.3733 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 32.25 | 32.25 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1240.5 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Summer | 223.516 | 32.87 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Off-Peak | 2850 | 38 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 635.1 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1021.8 | 18 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 3320.84 | 24.4 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 1614.735 | 24.3 | 1 | 1 | 0991-Tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
0991 | Tube leaks | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 99.1667 | 14 | 1 | 1 | 0991-Tube leaks | D1-Forced - Immediate | 800-Miscellaneous
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.9 | 3.9 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 33 | 3.3 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 82 | 4.1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16.5 | 3.3 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 22.8 | 3.8 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 11.4 | 5.7 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.1 | 3.1 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.2 | 3.2 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
0999 | Other heat exchanger problems | Boiler | External Fluid Bed Heat Exchanger (fbc) | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 34 | 3.4 | 1 | 1 | 0999-Other heat exchanger problems | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5198.3 | 22.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 19824.168 | 180.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 725 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 8256.3 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 174.4165 | 455 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 37.4933 | 23.68 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1648.8523 | 31.13 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44830.5 | 627 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70596 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14046.6665 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36600 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38887.3297 | 437.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15190 | 490 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56040.1665 | 590 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2365.6666 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18395.05 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 109560 | 800 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153155.09 | 234.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 13799.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11697.7637 | 174.29 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15843.7333 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17131.5 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 11498.3 | 66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26887.8998 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 28731.7528 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49979.9997 | 765 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82560.1331 | 622 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43112 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71350.45 | 739 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 973.2314 | 420.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6479.1999 | 168 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 375.245 | 6.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 324.6831 | 354.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7862.4499 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18157 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18187.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 26051.9998 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47106.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9153.2498 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17673.6664 | 370 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28887.4995 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 12054.5999 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 45219.9999 | 300 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 97482.5332 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 32197.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 12888.3331 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 18529.3333 | 208 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3657.8666 | 94.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 12055.3333 | 107 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 55800 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 55895 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 71020 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6622.5 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 85975 | 380 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14210.6 | 164 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37342.5 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 22457.9994 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30736.25 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4333.5 | 32.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14472 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 15339.3332 | 266 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 652.8 | 128 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5575 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20030.9999 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3526.82 | 430.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 74893.5 | 765 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17510.25 | 555 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 42575.8595 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57221.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 85010.4 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 124803.1135 | 466.67 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13938.4332 | 271 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51649.8662 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51871.4 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 61614.2331 | 634 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15660 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 26351.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9503.8332 | 254 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 5280 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 22005.5 | 66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30134 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41774.8331 | 610 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 235280 | 680 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.6 | 96 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 76.3 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2014.1 | 33 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5477.8332 | 230 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 132459.75 | 765 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12288.8833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67333.5 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 144046.6661 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9429.95 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 30262.7831 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 14647.5 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3090.25 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 25650 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5605 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16063.7666 | 139 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 79184.8958 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 87825.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17209.5 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 71545.7498 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34470.7494 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4995.4665 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12072.1663 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36660.5 | 567.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 273.3833 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1359.8666 | 248 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3996.4333 | 226 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 833.4375 | 19.05 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2833.3333 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9748.0998 | 680.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 22881.9997 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 36546.7665 | 491 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 89911.8 | 836 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27794 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28408.2 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16501.7833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29376.7496 | 585 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 44113.3329 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 61049.8332 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4236.2332 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8171.5 | 118 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 19677 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 55800 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9251.6665 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 34329.5662 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192358.1447 | 770.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28229.2494 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 43069.8332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 64692.0464 | 932.61 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10441.6665 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26521.1665 | 567.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32547.6664 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7362.2 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3691.3333 | 196 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18025 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1545.6 | 161 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1933.3332 | 250 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12424.9999 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 779.3167 | 19 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 108.2833 | 73 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1248 | 192 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 21 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 918.135 | 680.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4224 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10290 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18241 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8697.2498 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26896.5 | 417 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 203207.1664 | 758 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4077.3999 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6037.4833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11179.0333 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98000.1165 | 497 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51642 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 24166.6665 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1470.9499 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16333.3333 | 112 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18503.3333 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34180.0831 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52019.3329 | 710 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 141184.9997 | 770.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Off-Peak | 23012.8247 | 374.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 17819.5 | 567.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 30102.1499 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28436.4499 | 339 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.9166 | 53 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 631.2 | 26.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4378.8 | 24.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8999.4 | 28.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7 | 12 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 575.148 | 34.44 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 16134.8332 | 262 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23788.2163 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4902.9333 | 116 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42896.5833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 195951.4663 | 511 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9470.2166 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27930 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 124.6666 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 566.0975 | 18.35 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 645.0025 | 18.35 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4324.9 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10535.5 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16916.3333 | 190 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 55548.5 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 168500 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 19583.3333 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 21957 | 390 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 39486.9997 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 4948.5333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 57243.0829 | 605 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6222.4999 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11725 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19807.2166 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5224.9999 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5738 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15865.1999 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 29394.3328 | 815 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55655.5998 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22847.4998 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 24686.25 | 567.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 548 | 54.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18000 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18600 | 25 | 1 | 2 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1314.5 | 23.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1548.8 | 24.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 26203.4894 | 830.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 444 | 9.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 91.5 | 305 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6109.9999 | 156 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6181.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11100 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30368 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34768.6 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65699.6664 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 94174.2 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 129785.1666 | 115 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 62629.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64389.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87900 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 12798.1 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5070.35 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 18771.6999 | 174 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 27097.85 | 141 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 921.725 | 22.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 9651.75 | 255 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 11293.7 | 66 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9282.85 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 16661.9099 | 335.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12465.8331 | 350 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9052.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 85458.925 | 1330.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4309.5 | 22.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18600 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 155.4 | 42 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 506.88 | 3.96 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 943.8 | 24.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 8 | 6 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1321.25 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 41847.9998 | 480 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 18883.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27191.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 32444.0831 | 661 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57741.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 92546.5448 | 720.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9661.1662 | 637 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 11172 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 17684.9164 | 427 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 42787.4999 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 5419.2708 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 78725 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8491.95 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14697.3332 | 146 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 26657.75 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 5004.9499 | 93 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 58030.7 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Summer | 8261 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 8840 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120315 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27183 | 340 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22042.9995 | 705 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3289 | 25.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4967.2333 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 158.0999 | 153 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 305.6333 | 53 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37083.333 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 460 | 23 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18600 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 602 | 280 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 20218.1378 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 57269.333 | 560 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 57412.933 | 524 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 71482.75 | 505 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57803.1996 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 123210.5 | 658 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12755.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51255 | 510 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 77289.9996 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 8100 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 23547.9997 | 420 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 29340.9999 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 35275 | 500 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3119.5 | 18.35 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11016 | 108 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 714.4267 | 18.35 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19647.8478 | 814.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27335.1 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25401.6 | 162 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30360 | 276 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31347 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 437.6666 | 260 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2126.75 | 47 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8467.1 | 22.7 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7658.3333 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1162.5 | 30 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 639.4667 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 82.7332 | 292 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5001.3999 | 204 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 1140.5249 | 369.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9811.6666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10317.9999 | 165 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17729.9166 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 60439.9998 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8252.5832 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28097.3332 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81213.1824 | 1331 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6878.05 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32400 | 400 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7039.4997 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 14769.9999 | 210 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 6182.85 | 141 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 54000 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1986.6 | 94.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16555.4 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 54505.5 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4133.1 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41.6 | 78 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5699.54 | 370.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 625 | 25 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 244.65 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 63.6166 | 347 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 208.45 | 379 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1149.3333 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5320.4163 | 565 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8861.1833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14692.3 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 34668.5333 | 116 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 65391.3328 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 28083.1831 | 553 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2861.3549 | 206.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17432.1333 | 104 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23710.75 | 595 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27432.36 | 336.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33335.4998 | 570 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66000 | 600 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 91606.6665 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12118.8333 | 178 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 28867.2 | 582 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 54000 | 75 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 69865.2166 | 170.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7535.1666 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11225.1999 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 54786.2498 | 615 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21798.3331 | 580 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9918 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42556.0331 | 673 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111311.6664 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3160.2 | 46 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 664.86 | 15.83 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 285.0698 | 294.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 11294.85 | 108.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 13768.5 | 201 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43432.5496 | 651 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52314.1664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 58131.6664 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 111633.3331 | 850 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2686.0666 | 86 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55849.6662 | 655 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 76212.5 | 650 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 32789.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1104 | 69 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 17573.9666 | 167 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 63101.5625 | 156.25 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 41366.4999 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 5710.5 | 243 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17224.5831 | 335 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 27210.1333 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4122.9998 | 285 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 42377.5998 | 228 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31438.1596 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 31681.5332 | 406 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2989.6499 | 171 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6024 | 25.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 18598.6666 | 116 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 401.3332 | 215 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 76.1707 | 23.68 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1527.2666 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.1779 | 670.1 | 1 | 1 | 1000-Waterwall (Furnace wall) | D3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 141004.5 | 546 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4307.9999 | 90 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12259.2663 | 493 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14296.4 | 412 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 32519.9997 | 450 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3764.2 | 118 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8227.0466 | 94.6 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8906.3 | 169 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14215.4831 | 423.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22551.4664 | 352 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 29694.5 | 110 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 30117.7333 | 122 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6338.6666 | 160 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 10252.7333 | 44 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10714.5333 | 163 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 72775.9097 | 814.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 72446 | 740 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 80315.1 | 766 | 1 | 1 | 1000-Waterwall (Furnace wall) | U2-Forced - Delayed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 72775.35 | 387 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18424.475 | 316.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18464.7833 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26435.76 | 577.2 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 42821.2497 | 855 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 87.8333 | 85 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1764.9999 | 150 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 35.6999 | 153 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10936.8 | 24.8 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 63.9 | 142 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Winter | 319.9 | 319.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22898 | 535 | 1 | 1 | 1000-Waterwall (Furnace wall) | SF-Startup Failure | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7250 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19560.5 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24058.6663 | 520 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 29393.56 | 650.3 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 30096 | 342 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10726.0333 | 151 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15954.8331 | 290 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 50347.5 | 490 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33729.3331 | 820 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 8145.6467 | 22.16 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2847.2499 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13117.8665 | 208 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 20424.2499 | 105 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 45425.28 | 566.4 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50325 | 750 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 100-Fossil-Steam
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 1197.0833 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 4644 | 180 | 1 | 1 | 1000-Waterwall (Furnace wall) | U3-Forced - Postponed | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 68060.9998 | 315 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 22877.1 | 111 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 7985.784 | 100.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 10287.0853 | 100.64 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 479.375 | 32.5 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 3015.3 | 38 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 650-Fluidized Bed
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 865 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 3126.9933 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1482.1333 | 32 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2648 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 93 | 31 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 390 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 648 | 24 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2680.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1038.1583 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 3120 | 39 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 881.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 459 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1505.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 906.15 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 4764.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 1215 | 27 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2368.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 965.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 464 | 29 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 590.8 | 21 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 2118.2333 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2214 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2673 | 22 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 3483.9816 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 840.0233 | 25.9 | 1 | 1 | 1000-Waterwall (Furnace wall) | U1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1110.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 582 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 814.3333 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1013.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1640 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 1201.6667 | 20 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 800-Miscellaneous
1000 | Waterwall (Furnace wall) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 189715.5 | 351 | 1 | 1 | 1000-Waterwall (Furnace wall) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12659.9333 | 106 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U2-Forced - Delayed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 4147.3333 | 40 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 32011.3497 | 387 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 2775.48 | 10.1 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 445.5 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 21241 | 220 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68607.2332 | 406 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 804.2166 | 73 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3258.5 | 30 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | D1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18256.9096 | 543.9 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5536.6 | 589 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15967.1333 | 106 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 3459.3333 | 40 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U3-Forced - Postponed | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 173143.9997 | 480 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 100-Fossil-Steam
1003 | Steam generating tubes between steam drum and mud drum | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Summer | 2066.675 | 19.5 | 1 | 1 | 1003-Steam generating tubes between steam drum and mud drum | U1-Forced - Immediate | 800-Miscellaneous
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4559.6948 | 543.9 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1050 | 25 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 13398 | 280 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 591.8 | 22 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 2456.5267 | 31.4 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2876.6 | 57 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10210.6 | 57 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 23419 | 220 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24005.6665 | 220 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 596.4 | 21 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1226 | 40 | 1 | 1 | 1005-Generating tubes | U3-Forced - Postponed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 537.5 | 25 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 977.0833 | 25 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1437.5 | 25 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17085 | 335 | 1 | 1 | 1005-Generating tubes | U2-Forced - Delayed | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 368.9117 | 10.3 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4212 | 52 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1535.1 | 51 | 1 | 1 | 1005-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1005 | Generating tubes | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 2147.4333 | 46 | 1 | 1 | 1005-Generating tubes | D1-Forced - Immediate | 650-Fluidized Bed
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 20225.5664 | 427 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 18124.1665 | 455 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2113.75 | 475 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6583.0831 | 401 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U1-Forced - Immediate | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 72.45 | 69 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1010 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17028.75 | 475 | 1 | 1 | 1010-Cyclone furnace (in cyclone area only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43277.2494 | 855 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 156.2 | 44 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4812.6 | 156 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23387.3746 | 547.5 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 6744 | 240 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 749.75 | 15 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 33598.5 | 390 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 25035.9998 | 240 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 16685 | 235 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 44.75 | 15 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3744 | 156 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2391.9999 | 390 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 25591.9999 | 240 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39146.2496 | 585 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 31108.5 | 446 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3806.5 | 331 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3888 | 240 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9727.9999 | 240 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1568 | 112 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 100-Fossil-Steam
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7334 | 190 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 69.52 | 12.64 | 1 | 1 | 1020-Convection pass wall (water tubes only) | D1-Forced - Immediate | 650-Fluidized Bed
1020 | Convection pass wall (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 47502.08 | 100.64 | 1 | 1 | 1020-Convection pass wall (water tubes only) | U1-Forced - Immediate | 650-Fluidized Bed
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90402.8329 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 128408.233 | 497 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 107600.75 | 635 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22301.15 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45293.2665 | 497 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 11562.5 | 250 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 5879.1665 | 250 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21953.7499 | 195 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16326.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 111840.3992 | 1239 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6256.6666 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115459.5832 | 487 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 46391.8098 | 316.2 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U3-Forced - Postponed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 819.85 | 11.4 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | D2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4487.9999 | 198 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8828.9665 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10203.2665 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6253.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8282.9165 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2630 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 7813.3332 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 39064.2698 | 720.3 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 67974.4 | 494 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13840.45 | 199 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5095.2 | 193 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8560 | 200 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1030 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33244.3996 | 651 | 1 | 1 | 1030-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 44971.4767 | 390.66 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2030.9999 | 180 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24245.4665 | 271 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34089.5182 | 358.9 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 160 | 40 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64698.9163 | 505 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 314473.25 | 841.4 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6086.9499 | 201 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45849 | 580 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 58532.5 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 68878.3329 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 82824 | 714 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 87386.65 | 577 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 66484.1665 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34181.5499 | 351 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12429.9999 | 300 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.5 | 25 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 604.9167 | 35 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 21611.2666 | 179 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12238.3331 | 350 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66471.3365 | 250.3 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128191.1 | 361 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1131.7333 | 32 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 48484.7999 | 351 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 135417.1164 | 361 | 1 | 1 | 1035-Platen superheater | U2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.4167 | 35 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4480.21 | 441.4 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5880 | 105 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26308.2 | 652 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1424.5833 | 65 | 1 | 1 | 1035-Platen superheater | D2-Forced - Delayed | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56355 | 650 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64975.75 | 535 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 8239.6665 | 380 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 100-Fossil-Steam
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 47496.7499 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 43207.4998 | 315 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 20273.7497 | 525 | 1 | 1 | 1035-Platen superheater | U1-Forced - Immediate | 650-Fluidized Bed
1035 | Platen superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 22767.7998 | 237 | 1 | 1 | 1035-Platen superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 179.35 | 10.2 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13540.9665 | 271 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7058.0766 | 117.7 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12120.15 | 119 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 398.6666 | 130 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 199.4667 | 22 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9612.1999 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118300.5 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 149867.6664 | 770 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27559.3331 | 670 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44879.9996 | 576 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6311.25 | 275 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2433.3333 | 80 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 95281.75 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 29262.09 | 815.1 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16978.1 | 123 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1125 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1100 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26503.8 | 271 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 33122.875 | 702.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 43833.12 | 254.4 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17453.2349 | 206.1 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 78862.8331 | 610 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 18403 | 220 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 25842.8331 | 595 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27003.9166 | 115 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1441.5933 | 144.4 | 1 | 1 | 1040-First superheater | D2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2869.3333 | 80 | 1 | 2 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 57362.5 | 650 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5740.5 | 90 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 15672.15 | 247 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 28888 | 785 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 56736 | 576 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 3477.9516 | 133.34 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 514.9 | 19 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2500 | 80 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 446504.8378 | 839.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7823.25 | 285 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8273.1999 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35328 | 276 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5920.8332 | 203 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 500 | 250 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 70844.0997 | 522 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8364.1999 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23908.4999 | 405 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67214.75 | 635 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 166650 | 660 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 11669.4666 | 56 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 172181.9162 | 745 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 4639.3333 | 40 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26465.4163 | 475 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 1850 | 25 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1730.1667 | 10 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5342.4015 | 123.81 | 1 | 1 | 1040-First superheater | D3-Forced - Postponed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 68590.9999 | 339 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24501.8997 | 477 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35216.0665 | 193 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Summer | 40009.1745 | 466.67 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 69974 | 590 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4588.9999 | 156 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 164268.0328 | 818 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 61704.9383 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6845 | 92.5 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 14994 | 476 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 162331.71 | 333.33 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43151.9428 | 814.7 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 0 | 0 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15010.4166 | 275 | 1 | 1 | 1040-First superheater | U2-Forced - Delayed | 100-Fossil-Steam
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 12143.75 | 335 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2364.375 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2340 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 3320.4166 | 32.5 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 650-Fluidized Bed
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 1607.9583 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 764.75 | 23 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2055.165 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 2301.2166 | 43 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 148.35 | 9 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1551.41 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1370.9733 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 31.35 | 9 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 1424.0683 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 3676.505 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 1788.8266 | 25.9 | 1 | 1 | 1040-First superheater | U1-Forced - Immediate | 800-Miscellaneous
1040 | First superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 46904 | 352 | 1 | 1 | 1040-First superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1045 | In-bed superheater tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 49961.1 | 259 | 1 | 1 | 1045-In-bed superheater tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54672 | 670 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 40555.4997 | 855 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.5 | 90 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 148697.9998 | 297 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1930.39 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 98979.0663 | 613 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1475.6 | 527 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 742.1665 | 365 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 25029.6663 | 595 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50927 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 928 | 116 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5436 | 90 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 2654.19 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44734.9163 | 535 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62.8331 | 290 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 34033.3831 | 577 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 4934.1416 | 104.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 13898.6666 | 160 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24403.5 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 55084.9998 | 690 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 180697.5 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 52167.0331 | 336.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 11542.0499 | 351 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 23179.4164 | 349 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19300.8332 | 475 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 17739.3332 | 236 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8051.9999 | 90 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 115974 | 758 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 23604.4998 | 510 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 10998 | 141 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 43601 | 739 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 10253.0499 | 141 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64041.9998 | 615 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 343.9999 | 240 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 47744.55 | 659 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91456.9831 | 553 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 196428.9832 | 397 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44.6666 | 40 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 232 | 232 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 598.4664 | 382 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13161.2999 | 342 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 38547.8331 | 658 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 611100.4162 | 1317.5 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 1529.99 | 46.2 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117361.1 | 361 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7026.25 | 275 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81612.5665 | 587 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4927.5 | 90 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 20912.6665 | 247 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 367919.3 | 42 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40007.6665 | 380 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47072.1832 | 529 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 85.5 | 190 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 552.5 | 130 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18452 | 280 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17209.255 | 358.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41979.9996 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53049.9996 | 600 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12777.5999 | 198 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 19755.8664 | 427 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1992.1983 | 18.35 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 145410 | 1110 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 950.04 | 208.8 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6003 | 90 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 121788.3328 | 770 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56851.6998 | 582 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 329.9333 | 101 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3860 | 80 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66386.0331 | 709 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 51695.5831 | 401 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 26348.938 | 148.78 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 47198.2864 | 814.7 | 1 | 1 | 1050-Second superheater | U3-Forced - Postponed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 209.6664 | 340 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199417.4991 | 1350 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26501.6332 | 263 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4645.8332 | 250 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 642.25 | 18.35 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 23479.4665 | 256 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 49561.4994 | 855 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 70527.3329 | 635 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 28834 | 520 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 16028.9998 | 351 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 53336 | 590 | 1 | 1 | 1050-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 74898 | 180 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 734.9999 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 12600 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 46593.7498 | 315 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 77498.7496 | 525 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 1756.4999 | 90 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 650-Fluidized Bed
1050 | Second superheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Off-Peak | 2161.355 | 25.9 | 1 | 1 | 1050-Second superheater | U1-Forced - Immediate | 800-Miscellaneous
1050 | Second superheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 46006.2 | 419 | 1 | 1 | 1050-Second superheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31768 | 380 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 128721.6665 | 650 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51430 | 740 | 1 | 1 | 1055-External superheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1055 | External superheater link tubing | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 14382.5 | 523 | 1 | 1 | 1055-External superheater link tubing | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 49274.8666 | 308 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 9186.99 | 246.3 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20777.4666 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23963 | 773 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 147097.6824 | 1331 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17802 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 54637.333 | 560 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3828 | 290 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 11761.8499 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 23268.3333 | 115 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 119070 | 405 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 38531.9994 | 855 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33348.4 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39478.0097 | 815.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 64942.7997 | 414 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10803.8665 | 271 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12886.7498 | 285 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3762.0499 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 37128 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 56205 | 450 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 22880.4 | 552 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 38138.75 | 325 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 318098.4733 | 146.8 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6800.5 | 290 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 14825 | 593 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 18196.6499 | 243 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 83766 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 45228.81 | 814.2 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 15038.9063 | 491.2 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 56.25 | 15 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18463.4665 | 208 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7976.3499 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 31038.8 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64942.2 | 662 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40893.4998 | 510 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 24443.8331 | 335 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18884.9166 | 115 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 60054.75 | 615 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 25574.9999 | 450 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 5773.0446 | 28.57 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 310.5 | 18 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3277.5 | 285 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 51189.5163 | 577 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 55341.6665 | 500 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15252.8333 | 115 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 27158.4499 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 33364.7597 | 815.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 83123.7662 | 766 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2482.35 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3789.4832 | 271 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5949.6 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 14703.15 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 15251.6 | 104 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 40068.9997 | 510 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11637.4999 | 285 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 75946.5 | 630 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6504.5831 | 335 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 66827.4 | 381 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2279.1999 | 168 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3090.45 | 33 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5232.3995 | 762 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 8993.833 | 455 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42215.7 | 654 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2577.7162 | 733 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11296.9997 | 390 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12358.1499 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 46088 | 560 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 49692.4999 | 330 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4221.67 | 630.1 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1789.9998 | 300 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4005.1667 | 10 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 12116.3997 | 414 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33123.05 | 773 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29216.8331 | 634 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43854.4997 | 417 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42799.1666 | 275 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 381 | 10 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 921 | 90 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 151.9999 | 285 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 20254.0999 | 201 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 66720.8465 | 563.6 | 1 | 1 | 1060-First reheater | U2-Forced - Delayed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9770.8331 | 350 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31860 | 150 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 4954.1665 | 250 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 126270.8262 | 1330.1 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87504.6664 | 680 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188429.8997 | 762 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 11532.5 | 350 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140 | 200 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 113464.1666 | 146.8 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 9970.1333 | 64 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 33561.5997 | 414 | 1 | 1 | 1060-First reheater | SF-Startup Failure | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19044 | 552 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 45695 | 650 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 84741.6665 | 500 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16449.7 | 271 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7984.6666 | 116 | 1 | 1 | 1060-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42335.3 | 614 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 61556.25 | 335 | 1 | 1 | 1060-First reheater | U3-Forced - Postponed | 100-Fossil-Steam
1060 | First reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 69408.5332 | 352 | 1 | 1 | 1060-First reheater | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 9175 | 125 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39023.8332 | 310 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 46587.25 | 607 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 31215.6 | 552 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 11818.75 | 125 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 56521.8163 | 607 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49381.8329 | 635 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21547.2333 | 122 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17038.4 | 184 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41347.7897 | 814.2 | 1 | 1 | 1070-Second reheater | U2-Forced - Delayed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 372 | 310 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 34940.6195 | 815.1 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Off-Peak | 60923.7685 | 466.67 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 42218.9164 | 869 | 1 | 1 | 1070-Second reheater | U3-Forced - Postponed | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 282.433 | 458 | 1 | 1 | 1070-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62177.4998 | 570 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9131.1333 | 116 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1070 | Second reheater | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17049.1745 | 815.1 | 1 | 1 | 1070-Second reheater | U1-Forced - Immediate | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 21840 | 455 | 1 | 1 | 1075-External reheater link tubing | U2-Forced - Delayed | 100-Fossil-Steam
1075 | External reheater link tubing | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4139.2166 | 119 | 1 | 1 | 1075-External reheater link tubing | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 9397.0665 | 262 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44722 | 379 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13944.6 | 122 | 1 | 1 | 1080-Economizer | U2-Forced - Delayed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5446.8333 | 110 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4284.7999 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20608.59 | 713.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 246.45 | 9.3 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 213.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 52266.5831 | 577 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52682.5 | 650 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 24295 | 565 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5614.4994 | 855 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 6170.5 | 86 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 25520.1665 | 190 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1165.15 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11308.2665 | 208 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 178010.6666 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 326.7 | 22 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 612.4333 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 431.9 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 5124.5833 | 25 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 23577.415 | 336.1 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 995.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3732.5833 | 47 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46275.2498 | 651 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 64507.5 | 450 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2028 | 80 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 49540.2248 | 543.9 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3081.4667 | 44 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 772.2 | 66 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10181.7 | 486 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 314.4467 | 46.7 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8438.7333 | 169 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5498.25 | 45 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 19931.16 | 495.8 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29025.7496 | 585 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2964 | 114 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5916.3 | 111 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 988.5 | 30 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 421.88 | 10.6 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 887.1683 | 21.7 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6075 | 1350 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2675 | 250 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1400.6 | 47 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4773.6 | 156 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92220.3328 | 770 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 35644 | 380 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 145327.5 | 1350 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6108.795 | 47.3 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 446.8133 | 9.4 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1114.9666 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24598.9998 | 510 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137851.6664 | 773 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2570.5 | 48.5 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 30580.4994 | 855 | 1 | 1 | 1080-Economizer | U3-Forced - Postponed | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Summer | 459.1667 | 19 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 3746.8666 | 31 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70769.9997 | 450 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 39652.9 | 259 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 346.3583 | 46.7 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 796.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70094 | 505 | 1 | 1 | 1080-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 482.6667 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 734.65 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 253.75 | 29 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 499.5167 | 20.5 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 535.5 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 275.1 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1539 | 57 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 233.1 | 21 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | NPCC | Winter | 505.3333 | 20 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 800-Miscellaneous
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 15879.9999 | 300 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1080 | Economizer | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 1680.9 | 18 | 1 | 1 | 1080-Economizer | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1085 | In-bed evaporative tubes (FBC only - includes external heat exchangers) | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 78849.7498 | 315 | 1 | 1 | 1085-In-bed evaporative tubes (FBC only - includes external heat exchangers) | D1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5239.5832 | 125 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1187.84 | 92.8 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 28216.2 | 492 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5026.6663 | 580 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 336 | 28 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 22174.9999 | 375 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 983.5 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 941 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1270.2916 | 107.5 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 144353.7329 | 1243 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 68566.8331 | 577 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191096.8997 | 762 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1063.0666 | 134 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 230980.2 | 474 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 41954.75 | 593 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 637.5 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.38815 | 23.29 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 517.3333 | 97 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 5590.2 | 423.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 274946 | 479 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1222.6667 | 16 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 36461.4165 | 492.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38298.1663 | 595 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 43639.05 | 417 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 260903.5 | 533 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 26400 | 240 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 44080 | 800 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53312.4665 | 644 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1576.2833 | 22.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6372.4165 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41258.7 | 531 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 489.1466 | 132.8 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 35675.5833 | 107 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 52748.4415 | 244.3 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 42440 | 400 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 15052.8666 | 236 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 36753.9 | 606 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28218.2498 | 615 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 136451 | 707 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 33911.9999 | 162 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15836.3333 | 220 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 894.25 | 21 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2208.8333 | 145 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 71.25 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 757.5 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22489.8665 | 374 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 21109.7596 | 537.6 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 109364.6297 | 509.7 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 62933.1 | 606 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18779.8666 | 122 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 52034.6665 | 395 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9059.25 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 199.9999 | 120 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1035 | 15 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26826.7999 | 201 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41707.3996 | 651 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 83947.5 | 450 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12583.9999 | 240 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 82368.9997 | 492 | 1 | 1 | 1090-Other boiler tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29709.4662 | 652 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36772.8 | 652 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 34693.9663 | 598 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 131914.4164 | 707 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12000 | 240 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 139986.3496 | 1239 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 119973.7498 | 225 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7491.7833 | 107 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 176406.6 | 492 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5990.1665 | 635 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 106760.5 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 126555.0828 | 785 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 16744 | 416 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 236826.3328 | 770 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9571.25 | 247 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2439.5 | 238 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2071.3333 | 104 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37535.4 | 662 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134098.25 | 1331 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 31905 | 450 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 534.3333 | 229 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 995.512 | 171.64 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33420 | 600 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116416.1664 | 758 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 12923.75 | 175 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10254.55 | 111 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 61218.0954 | 406.18 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17895.5999 | 162 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128233.5731 | 304.4 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1006.6333 | 23 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12443.833 | 492.5 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16508.3966 | 64.9 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 102528 | 712 | 1 | 1 | 1090-Other boiler tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43459.83 | 757.8 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28413 | 615 | 1 | 1 | 1090-Other boiler tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6328 | 35 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9654.5833 | 235 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16623.7665 | 593 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3256.18 | 24.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 3540.95 | 67 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D2 | Forced - Delayed | 2023 | Coal | OS | 650 | Fluidized Bed | SERC | Summer | 68527.68 | 346.8 | 1 | 1 | 1090-Other boiler tube leaks | D2-Forced - Delayed | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 6940.8053 | 100.64 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 2158.9933 | 24.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 3082.5333 | 24.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 1929.6333 | 24.4 | 1 | 1 | 1090-Other boiler tube leaks | U1-Forced - Immediate | 650-Fluidized Bed
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 190.2833 | 23.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1210.4667 | 13.4 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 218.1833 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 527.15 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 491 | 20 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 81.9 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 105.7333 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 812.5 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 410.835 | 18.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 577.85 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 53.55 | 15.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 858.1783 | 22.3 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 559.4333 | 13 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 800-Miscellaneous
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 13813.0331 | 419 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1090 | Other boiler tube leaks | Boiler | Boiler Tube Leaks | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 59834.1332 | 352 | 1 | 1 | 1090-Other boiler tube leaks | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1.3267 | 19.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 543.97 | 39.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 793.7433 | 104.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1417.9199 | 189.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.615 | 9.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 150.5 | 105 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17017.1 | 379 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15566.7 | 114 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24.5 | 10 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.025 | 114.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3260.49 | 129.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3070.8581 | 281.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 170.25 | 227 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 211.8333 | 41 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 564.2633 | 139.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 72.8333 | 46 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 88.8333 | 41 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.9766 | 59.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 118.73 | 114.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 770.4999 | 201 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6.6533 | 49.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 609.4916 | 119.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 435946.9662 | 673 | 1 | 1 | 1100-Waterwall (Furnace wall) | U1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 448.0016 | 89.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 519.3333 | 76 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 139.345 | 89.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2415.6066 | 139.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2350.15 | 427.3 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1689.4166 | 209 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1100 | Waterwall (Furnace wall) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 137.25 | 54.9 | 1 | 1 | 1100-Waterwall (Furnace wall) | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 176.4 | 1.8 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 16620 | 22.16 | 1 | 1 | 1105-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2664.9333 | 92 | 1 | 1 | 1105-Generating tubes | U1-Forced - Immediate | 100-Fossil-Steam
1105 | Generating tubes | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1637.1666 | 209 | 1 | 1 | 1105-Generating tubes | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 442 | 60 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 881.8333 | 55 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 89.5 | 30 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9460.7499 | 195 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1135.35 | 87 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3599.1667 | 50 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 111.5833 | 65 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D1-Forced - Immediate | 100-Fossil-Steam
1110 | Cyclone furnace (in cyclone area only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 929.1666 | 125 | 1 | 1 | 1110-Cyclone furnace (in cyclone area only) | D2-Forced - Delayed | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4732.0833 | 25 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1168.3333 | 25 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3416.985 | 24.3 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1120 | Convection pass wall | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2073.3333 | 40 | 1 | 1 | 1120-Convection pass wall | D1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 24502.1 | 497 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U2-Forced - Delayed | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20327.3 | 497 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | U1-Forced - Immediate | 100-Fossil-Steam
1130 | Boiler screen; wing wall; or slag screen (water tubes only) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1000.2349 | 239.1 | 1 | 1 | 1130-Boiler screen; wing wall; or slag screen (water tubes only) | D3-Forced - Postponed | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 30906.1626 | 33.01 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 39561.62 | 357.7 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 45.3942 | 11.59 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 294.7999 | 201 | 1 | 1 | 1140-First superheater | U1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 371.1667 | 5 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 65.9333 | 23 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 213.7 | 6 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 610.8 | 6 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1280.24 | 24.62 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 373.4867 | 4.4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 25.4602 | 10.99 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 100-Fossil-Steam
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 88.4 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 247.9333 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 244 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 687.75 | 21 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 287.9333 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 160.5333 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 306.9333 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1140 | First superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 14.2667 | 4 | 1 | 1 | 1140-First superheater | D1-Forced - Immediate | 800-Miscellaneous
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.05 | 39 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.5333 | 4 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 265.4667 | 44 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 86439.2 | 668 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.6 | 34 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9694.2 | 151 | 1 | 1 | 1150-Second superheater | U1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 258.9533 | 2.8 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 24324.7664 | 427 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17320.5 | 270 | 1 | 1 | 1150-Second superheater | U2-Forced - Delayed | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1.8 | 9 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 20074.25 | 35 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0.7333 | 44 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.65 | 19 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.0333 | 34 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20.3 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.4667 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50 | 24 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 501.3333 | 40 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 99.6333 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15.4 | 44 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 45.0333 | 14 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 104.8833 | 29 | 1 | 1 | 1150-Second superheater | D1-Forced - Immediate | 100-Fossil-Steam
1150 | Second superheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 143.5 | 12.3 | 1 | 1 | 1150-Second superheater | D3-Forced - Postponed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1378.0667 | 7 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3135 | 209 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3159 | 9 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1016.6 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 51127.5 | 401 | 1 | 1 | 1160-First reheater | U1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 911.5 | 6 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 819.9333 | 98 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 99.8667 | 8 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1497.5333 | 7 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 878.8166 | 67 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2506.85 | 277 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10640.9333 | 28 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 989.76 | 10.31 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 811.0666 | 158 | 1 | 1 | 1160-First reheater | D2-Forced - Delayed | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4423.4667 | 22 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 690.3333 | 5 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1160 | First reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 229.25 | 21 | 1 | 1 | 1160-First reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 75.4 | 26 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5.1 | 9 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.3333 | 20 | 1 | 1 | 1170-Second reheater | D2-Forced - Delayed | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 734.825 | 39.9 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1742.965 | 39.9 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 52.8 | 12 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 54.8167 | 11 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1143.8 | 39.9 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 137.5 | 66 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3443.4167 | 35 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 427.5183 | 19.9 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1170 | Second reheater | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 197.0667 | 16 | 1 | 1 | 1170-Second reheater | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3340 | 417.5 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 6.8333 | 41 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2142.25 | 209 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 8308.3332 | 250 | 1 | 1 | 1180-Economizer | U1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 16 | 16 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5225 | 209 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1180 | Economizer | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3540 | 150 | 1 | 1 | 1180-Economizer | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 65.8 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 20 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1294.9 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 36286.1795 | 814.2 | 1 | 1 | 1190-Other tube slagging or fouling | U2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1675.2 | 279.2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 97.9167 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 150.7333 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1226.6666 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.4167 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1746 | 120 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 65.55 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 27.6 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 67.6666 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 183.6667 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 614.4833 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 383.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3459.5 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6602.88 | 14.48 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 165 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 413.2667 | 4 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 529.8333 | 4.4 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1716.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2340 | 13 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 839.6667 | 22 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 80.5 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 189.5667 | 22 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1115.4999 | 291 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1368.9 | 304.2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3338.65 | 21 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 39.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 140.25 | 17 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2966.1333 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 159.5833 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 501 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 561.6 | 27 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1701.5948 | 239.1 | 1 | 1 | 1190-Other tube slagging or fouling | D3-Forced - Postponed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1058.8 | 264.7 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 3772.7467 | 12.7 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1296 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 80.75 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 163.1 | 42 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 503.25 | 33 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 542.85 | 47 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168604.3328 | 770 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 48.3333 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 286.6167 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 319.55 | 21 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 770 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 209.5 | 15 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 760 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 24 | 16 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 49.1333 | 22 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 195 | 26 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 198.65 | 29 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1440.2 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2079 | 270 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 127.4 | 42 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 286.2333 | 31 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 70.5333 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 192.5 | 42 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 284.8 | 24 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5176 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 807 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 552.6733 | 63.77 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 77.6667 | 5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1290 | 30 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19.1667 | 23 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 19.6333 | 38 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 25.8333 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 106.6667 | 20 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 261.3333 | 70 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2637.3983 | 5.9 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 645 | 107.5 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1606.7333 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3247.4167 | 35 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 55438.3328 | 740 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 942.6 | 314.2 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 50112 | 270 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 225 | 25 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 290.7 | 27 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 330.8666 | 28 | 1 | 1 | 1190-Other tube slagging or fouling | D2-Forced - Delayed | 100-Fossil-Steam
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 474.6 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 934.2 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 1460.7 | 18 | 1 | 1 | 1190-Other tube slagging or fouling | U1-Forced - Immediate | 650-Fluidized Bed
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 12.2917 | 12.5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1190 | Other tube slagging or fouling | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1393.6583 | 20.5 | 1 | 1 | 1190-Other tube slagging or fouling | D1-Forced - Immediate | 800-Miscellaneous
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1398.7 | 394 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1108 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 121.6 | 15.2 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 200 | 75 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 728.3333 | 115 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 39.5 | 15.8 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1662 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 966.4667 | 10.9 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D1-Forced - Immediate | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2013.5831 | 365 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2488.3832 | 277 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D2-Forced - Delayed | 100-Fossil-Steam
1200 | Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | Boiler | Boiler Tube Fireside Slagging or Fouling | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1700 | 425 | 1 | 1 | 1200-Operation at reduced power to avoid slagging or fouling except waterwalls (furnace walls) (use codes 1100 to 1190 to report power reductions for slag accumulation or slag removal) | D3-Forced - Postponed | 100-Fossil-Steam
1300 | Water side fouling | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 5827.2 | 72 | 1 | 1 | 1300-Water side fouling | U2-Forced - Delayed | 852-CC steam units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 1877.3333 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U2-Forced - Delayed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 2036 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Summer | 980 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U2-Forced - Delayed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Off-Peak | 1402 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 77415.8925 | 333.33 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 2226 | 40 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U3-Forced - Postponed | 100-Fossil-Steam
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 6338.75 | 253.55 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | U1-Forced - Immediate | 850-Combined Cycle Block
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 9574.9099 | 111.9 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 852-CC steam units
1305 | Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 4251.4052 | 16.93 | 1 | 1 | 1305-Fireside cleaning (which requires a full outage) Use code 1200 for cleanings that cause deratings. | D1-Forced - Immediate | 852-CC steam units
1330 | Slag fall damage | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 611.24 | 103.6 | 1 | 1 | 1330-Slag fall damage | D1-Forced - Immediate | 850-Combined Cycle Block
1330 | Slag fall damage | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 21073.9666 | 103.6 | 1 | 1 | 1330-Slag fall damage | D1-Forced - Immediate | 850-Combined Cycle Block
1330 | Slag fall damage | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1152.9 | 61 | 1 | 1 | 1330-Slag fall damage | D1-Forced - Immediate | 850-Combined Cycle Block
1330 | Slag fall damage | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 24220 | 280 | 1 | 1 | 1330-Slag fall damage | U1-Forced - Immediate | 850-Combined Cycle Block
1330 | Slag fall damage | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2641.8 | 103.6 | 1 | 1 | 1330-Slag fall damage | D1-Forced - Immediate | 850-Combined Cycle Block
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 312302.6 | 86.2 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 38.3333 | 20 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 121.6667 | 20 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | D1-Forced - Immediate | 100-Fossil-Steam
1340 | Tube modifications (including addition and removal of tubes) | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 19224 | 267 | 1 | 1 | 1340-Tube modifications (including addition and removal of tubes) | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 792.05 | 31 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 2117.164 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 6324.9211 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22691.0832 | 245 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U2-Forced - Delayed | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 43746.2082 | 317.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 727.5 | 15 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 1704.7846 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3624.7915 | 317.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 54235.7995 | 783 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 9820.58 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 130476.0416 | 147.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 12695.3333 | 139 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 20.1938 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16424.125 | 147.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 70.147 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 154.1108 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 749.7916 | 147.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17917.5832 | 317.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 249889.5832 | 237.5 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 21.2566 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 93.5293 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 628.1345 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 12.754 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9309.9332 | 292 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 3663.5865 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 3903.7868 | 63.77 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 100-Fossil-Steam
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 777.6667 | 20 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 506.7833 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 800-Miscellaneous
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 107.4315 | 42.13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 440.9167 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Off-Peak | 4951.25 | 85 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 4502.5833 | 71 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Summer | 104 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 492.9167 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 5220.4695 | 80.13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 24 | 3 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 4717.95 | 71 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 850-Combined Cycle Block
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 7884.7465 | 67.19 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 15610 | 223 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 851-CC GT units
1350 | Other miscellaneous boiler tube problems | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 5756.0175 | 49.05 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 852-CC steam units
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 2684.1 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 11.7 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 69.1167 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 95.0667 | 8 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 108.3333 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 1858.7833 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 1860.95 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Summer | 2856 | 51 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 291.9 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Summer | 3416.6167 | 13 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 1427.7 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 108.3 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | TRE | Winter | 2045.1 | 18 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | D1-Forced - Immediate | 860-Co-generator Block
1350 | Other miscellaneous boiler tube problems | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Coal | CC | 860 | Co-generator Block | WECC | Off-Peak | 3468 | 51 | 1 | 1 | 1350-Other miscellaneous boiler tube problems | U1-Forced - Immediate | 860-Co-generator Block
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 14573.2998 | 654 | 1 | 1 | 1360-Boiler drains system | U3-Forced - Postponed | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6075.9999 | 336 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3516.75 | 45 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 9978.233 | 467 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 100-Fossil-Steam
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 73315.5 | 370 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2660 | 760 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 2799.3331 | 760 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1444 | 380 | 1 | 1 | 1360-Boiler drains system | D1-Forced - Immediate | 850-Combined Cycle Block
1360 | Boiler drains system | HRSG Boiler | Miscellaneous HRSG Boiler Tube Problems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 400.9332 | 248 | 1 | 1 | 1360-Boiler drains system | SF-Startup Failure | 851-CC GT units
1360 | Boiler drains system | HRSG Boiler | Miscellaneous Boiler Tube Problems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Winter | 1277.4666 | 26.8 | 1 | 1 | 1360-Boiler drains system | U1-Forced - Immediate | 862-CoG steam units
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.3333 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 35.65 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 101.0167 | 29 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134.805 | 17.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 692.6666 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 819 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1689.5 | 310 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 28004.1666 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 645.9166 | 115 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6609.9 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 87413.3333 | 32 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 89.65 | 11 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 179.7999 | 87 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21981.6 | 103.2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.3 | 17.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.6333 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 480 | 96 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1238.9 | 95.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6678.75 | 65 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 607.0498 | 513 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 16.2667 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 71968 | 13 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 6.2737 | 3.19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3361.2663 | 508 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 75 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 157.0832 | 325 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 296.1 | 94 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1242 | 103.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1980 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.8 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.5 | 10 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 291.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 400 | 100 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3279.9999 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 872.9999 | 270 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 481.6666 | 85 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 337171.9998 | 474 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.8 | 23 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1144 | 208 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 675.4333 | 46 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2544.1664 | 355 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31719.7997 | 417 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.25 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 714 | 102 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 188.65 | 23.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 365.8333 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 692 | 40 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17885 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 217 | 108.5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14486.6666 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 391.6028 | 52.33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 42 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 91694.9999 | 180 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 143146.6664 | 352 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.8 | 12 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.75 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 672 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6104 | 112 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 172.15 | 33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5296.6665 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 70928 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19953.3332 | 292 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.5 | 30 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 69.1667 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1374.3332 | 155 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 16.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 120.5 | 24.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1878.9333 | 26 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 166.1367 | 25.3 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1893.1332 | 292 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 176 | 132 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 396.6665 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1780.3 | 93.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1898.9 | 111.7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88 | 22 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 192 | 90 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 881.6 | 110.2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1268.5 | 43 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 189458.4 | 36 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30 | 4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1076.0259 | 324.43 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1081.6 | 128 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 17526.9999 | 255 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 43775.5795 | 757.8 | 1 | 1 | 1400-Forced draft fans | U3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 268.9167 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 79.1 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.8333 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 317.85 | 39 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 780.4983 | 22.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2394 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16869.116 | 36.24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 33.3 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4289.5 | 115 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 177.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 48 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 75 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 183.4 | 42 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 189 | 28 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1817.3567 | 22.1 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47731.8 | 316 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5598.9864 | 344.2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.9167 | 5 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 88519 | 410 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 209.9999 | 252 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 327.25 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 526.85 | 257 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 60 | 2 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 422.5 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 788.6667 | 14 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1288.75 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1093.1333 | 38 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4847.5 | 350 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 88.1999 | 189 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 63568.7 | 78 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 444 | 185 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 391.55 | 191 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 58080.1333 | 61 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56.35 | 49 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.0833 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 156.4333 | 247 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 239.6 | 24 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 274.3333 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 421.6665 | 220 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 147735 | 294 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1037.7 | 115.3 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 323.9166 | 115 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81.0667 | 38 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 239.6667 | 20 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400.5 | 54 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 46 | 15 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3728.75 | 157 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 97701.1 | 157 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 288 | 36 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 35627.9426 | 334.43 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 120.75 | 9 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 780.9999 | 165 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1779.1666 | 50 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 178.5 | 51 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 499.4 | 33 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1307.6 | 42 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2229.9667 | 19 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4321.3332 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 40048.0833 | 157 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 4150.476 | 314.43 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 55175.4166 | 25 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 148920 | 17 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2317.2498 | 465 | 1 | 1 | 1400-Forced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 91.1166 | 77 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1530 | 300 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.5833 | 35 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 43.75 | 21 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 483 | 161 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2904.7 | 46.85 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 36267 | 330 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 248.45 | 3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2174.6665 | 280 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5178.1332 | 152 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 261.3333 | 40 | 1 | 1 | 1400-Forced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1368 | 570 | 1 | 1 | 1400-Forced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 512445.3997 | 876 | 1 | 1 | 1400-Forced draft fans | U3-Forced - Postponed | 100-Fossil-Steam
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 28.3125 | 37.75 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 29.1667 | 7 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 800-Miscellaneous
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5088.7 | 67.4 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 161420.6666 | 170 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 1798.0316 | 67.3 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 77850.2 | 419 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1400 | Forced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 41471 | 113 | 1 | 1 | 1400-Forced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 222 | 37 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 236.4333 | 41 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27 | 5 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 588 | 196 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3406.6664 | 400 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 561 | 170 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 86.8833 | 13 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.4998 | 255 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7.3667 | 2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 21.9 | 6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10817 | 580 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1988 | 42 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9661.8999 | 318 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 17024.9999 | 180 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 755.6499 | 381 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 140.7 | 18 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 202.5 | 225 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 218.1965 | 195.4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2.1 | 3 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1593.75 | 375 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 56 | 28 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20.3 | 2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1759.333 | 455 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 94.3333 | 10 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1172.6 | 33 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23.8 | 6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 7428.3599 | 185.4 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 6075.4781 | 334.43 | 1 | 1 | 1401-Forced draft fan dampers | SF-Startup Failure | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 45.5 | 91 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 70.8333 | 106.25 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6688 | 57 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 288.3766 | 145.4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 7930.8167 | 11 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2 | 2 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 256.4699 | 185.4 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.6 | 39 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 310.7166 | 103 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16.4 | 6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 794.7333 | 26 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 570 | 114 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 484.0666 | 212 | 1 | 1 | 1401-Forced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 28.3333 | 50 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 64.9999 | 195 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 673.55 | 57 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 17.6 | 6 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7.5 | 5 | 1 | 1 | 1401-Forced draft fan dampers | D1-Forced - Immediate | 650-Fluidized Bed
1401 | Forced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | TRE | Winter | 636.9999 | 105 | 1 | 1 | 1401-Forced draft fan dampers | U1-Forced - Immediate | 650-Fluidized Bed
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4343.7499 | 375 | 1 | 1 | 1407-Forced draft fan lubrication system | SF-Startup Failure | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 43575.35 | 61 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 425.9999 | 180 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 6946 | 151 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 17524.2833 | 61 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4698.1331 | 766 | 1 | 1 | 1407-Forced draft fan lubrication system | U1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 171.9998 | 240 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110.2545 | 236.26 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6360.4164 | 355 | 1 | 1 | 1407-Forced draft fan lubrication system | D1-Forced - Immediate | 100-Fossil-Steam
1407 | Forced draft fan lubrication system | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 246.25 | 25 | 1 | 1 | 1407-Forced draft fan lubrication system | U2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2.033 | 40.66 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2646.4666 | 212 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44431.2329 | 662 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 2128.3333 | 50 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4494.6 | 227 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6660.3165 | 187 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2266.95 | 107.95 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 122.6666 | 230 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 469.2 | 6 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 659.3166 | 179 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16993.1666 | 110 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6866.2 | 66 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10934.6664 | 472 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5955 | 397 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 131614.9999 | 75 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 4298.9332 | 188 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 425001.5 | 415 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 17510 | 170 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 25706.6666 | 320 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 76200 | 120 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 243.1 | 187 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13643.1 | 93 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 13458.6666 | 206 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17091.4 | 97 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 30492 | 99 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 33199.9997 | 480 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2225.75 | 307 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46485.9 | 162 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 163190.1666 | 326 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 37750.59 | 20.7 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 88615.9666 | 97 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14352 | 460 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 66.3 | 2.21 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5129.92 | 111.52 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 131090.75 | 433 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 236.0166 | 49 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 640 | 25.6 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25527.7 | 66 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 3496.9085 | 178.87 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50004.65 | 661 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.5203 | 40.66 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2 | 2 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35595.7313 | 240.81 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31639.7332 | 472 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | SERC | Winter | 162 | 40 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 699.6 | 212 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1063.2332 | 382 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 329274.0832 | 295 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 405 | 20 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 41933.101 | 58.87 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 141595.0832 | 295 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 4773.6 | 351 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 350.5333 | 44 | 1 | 1 | 1410-Forced draft fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 60749.6665 | 620 | 1 | 1 | 1410-Forced draft fan motors | SF-Startup Failure | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7372 | 80 | 1 | 1 | 1410-Forced draft fan motors | U1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1118.8833 | 187 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8 | 2 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1287.96 | 107.33 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3640 | 140 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4834.8667 | 34.7 | 1 | 1 | 1410-Forced draft fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1410 | Forced draft fan motors | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10098 | 99 | 1 | 1 | 1410-Forced draft fan motors | D3-Forced - Postponed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 142 | 40 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1135.97 | 103.27 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 474.1333 | 112 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 901335.7331 | 386 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 150 | 75 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D2-Forced - Delayed | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1208.68 | 53.6 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 15278.9 | 91 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 610 | 305 | 1 | 1 | 1411-Forced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1411 | Forced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 555.6331 | 422 | 1 | 1 | 1411-Forced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 240.1666 | 110 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2207.3497 | 393 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 594388.9164 | 785 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 681 | 113.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 8557 | 430 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1215.4999 | 330 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1383.1999 | 156 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1262.4997 | 750 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 30837.1346 | 148.78 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 370 | 100 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1289.75 | 385 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 584250.3332 | 385 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11999.1664 | 385 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6087.4661 | 832 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 624 | 320 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 6240.75 | 785 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2088.75 | 15 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D2-Forced - Delayed | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 280.8332 | 337 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | D1-Forced - Immediate | 100-Fossil-Steam
1412 | Forced draft fan drives (other than motor) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 1402.9166 | 32.5 | 1 | 1 | 1412-Forced draft fan drives (other than motor) | U1-Forced - Immediate | 650-Fluidized Bed
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2418.2199 | 225.3 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 989.2333 | 50.3 | 1 | 1 | 1413-Forced draft fan couplings | D1-Forced - Immediate | 100-Fossil-Steam
1413 | Forced draft fan couplings | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37021.1249 | 330.3 | 1 | 1 | 1413-Forced draft fan couplings | U3-Forced - Postponed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 267.6665 | 292 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 641.6666 | 175 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2383.8 | 9 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 512.1333 | 46 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 244.9999 | 420 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16.8667 | 4 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 61.6667 | 10 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1170.7662 | 682 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 130 | 325 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 28 | 40 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 108.9 | 18 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1131.4881 | 334.43 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3108 | 420 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 452.6 | 292 | 1 | 1 | 1415-Forced draft fan controls | U2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 810 | 450 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4966.4 | 256 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 19.7 | 6 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 794 | 397 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 146.2832 | 131 | 1 | 1 | 1415-Forced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 10769.6 | 254 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5538 | 520 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 13.9999 | 210 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9451.1999 | 198 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3833.6665 | 434 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 2139.1666 | 85 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.25 | 5 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 342.9997 | 420 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 17.75 | 15 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2 | 20 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 74.2 | 7 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7822.5 | 350 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 26.1333 | 56 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2247.4664 | 448 | 1 | 1 | 1415-Forced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1415 | Forced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 73.3333 | 20 | 1 | 1 | 1415-Forced draft fan controls | D1-Forced - Immediate | 800-Miscellaneous
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20.1667 | 10 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12602.3333 | 14 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3282.1665 | 470 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 426.6667 | 32 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 717.3333 | 160 | 1 | 1 | 1420-Other forced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 16114.9999 | 330 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20508.8833 | 41 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18539.52 | 90.88 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 244.5 | 45 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25524.586 | 42.04 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 27941.3331 | 320 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 39075.3999 | 296.4 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0 | 0 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1750.1 | 473 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14.6666 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13490.8 | 24 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13653.7167 | 19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 268.75 | 75 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 212.8037 | 9.43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 23413.5477 | 34.43 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116 | 40 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 699.924 | 49.64 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1224.2333 | 19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 492944.9999 | 450 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1628.4833 | 199 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 889.8666 | 188 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 954.9996 | 573 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 575 | 25 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6233.3331 | 425 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1587.04 | 99.19 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1836.2667 | 11 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9342.06 | 247.8 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 623.1 | 46.5 | 1 | 1 | 1420-Other forced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1420 | Other forced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Off-Peak | 1611.1266 | 26.8 | 1 | 1 | 1420-Other forced draft fan problems | U1-Forced - Immediate | 862-CoG steam units
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 84.4999 | 195 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 44 | 220 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 20396.05 | 659 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 99.5 | 30 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 98.6666 | 185 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 100-Fossil-Steam
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 817.5499 | 249 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 670 | 268 | 1 | 1 | 1421-Secondary air fans/blowers | U1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Summer | 5.24 | 2.62 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 650-Fluidized Bed
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 738.9 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1421 | Secondary air fans/blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Off-Peak | 4915.2 | 18 | 1 | 1 | 1421-Secondary air fans/blowers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1253.3333 | 80 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | U1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9293.3332 | 328 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 100-Fossil-Steam
1422 | Secondary air fan/blower motors - single speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 619.4667 | 23 | 1 | 1 | 1422-Secondary air fan/blower motors - single speed | D1-Forced - Immediate | 800-Miscellaneous
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 173.55 | 267 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 325.2 | 542 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 689.6717 | 22.9 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1234 | 617 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 582 | 582 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1423 | Secondary air fan/blower motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 85.5 | 342 | 1 | 1 | 1423-Secondary air fan/blower motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1013.8833 | 127 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 609.75 | 271 | 1 | 1 | 1424-Secondary air fan/blower controls | D1-Forced - Immediate | 100-Fossil-Steam
1424 | Secondary air fan/blower controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 2997 | 111 | 1 | 1 | 1424-Secondary air fan/blower controls | U1-Forced - Immediate | 650-Fluidized Bed
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 209.7333 | 52 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22985.4166 | 275 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2834 | 30 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 2811.555 | 145.3 | 1 | 1 | 1430-Air supply ducts from FD fan | U1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3617.25 | 21 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 12711.1832 | 493 | 1 | 1 | 1430-Air supply ducts from FD fan | SF-Startup Failure | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10 | 30 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 72795.8 | 42 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 153.9 | 57 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1430 | Air supply ducts from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3568.6 | 42 | 1 | 1 | 1430-Air supply ducts from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1395 | 45 | 1 | 1 | 1431-Air supply dampers from FD fan | D1-Forced - Immediate | 100-Fossil-Steam
1431 | Air supply dampers from FD fan | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 4068.8981 | 334.43 | 1 | 1 | 1431-Air supply dampers from FD fan | SF-Startup Failure | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7.9167 | 5 | 1 | 2 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 27 | 5 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 714.8 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.25 | 1 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8.1667 | 5 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9.7333 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 778.5333 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 11.5 | 10 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 138.9333 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 139.8667 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 156.6667 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7.1 | 3 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 115.0833 | 5 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 18.4167 | 5 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 19.6667 | 10 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 159.7333 | 8 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0.3 | 6 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 125.0667 | 7 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6 | 9 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 138.8333 | 7 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 272.7333 | 4 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 14784 | 352 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1432 | Air supply duct expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 48818.7 | 378 | 1 | 1 | 1432-Air supply duct expansion joints | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 723.6 | 108 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 153.2667 | 44 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 482.5 | 75 | 1 | 1 | 1440-Air supply dampers | D2-Forced - Delayed | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 533.75 | 35 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 100-Fossil-Steam
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2625.6832 | 257 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 650-Fluidized Bed
1440 | Air supply dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1335.0332 | 242 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 650-Fluidized Bed
1440 | Air supply dampers | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 873 | 18 | 1 | 1 | 1440-Air supply dampers | D1-Forced - Immediate | 850-Combined Cycle Block
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 31.5 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14.25 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18.7833 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 118.5167 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 177.6 | 24 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2370.6663 | 508 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 167.5 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 778.3933 | 10.6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9.85 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 67.65 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 31705.9166 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3557.1666 | 70 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 47905.4132 | 296.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 38.6667 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 76.8 | 16 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 397.0167 | 7 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 18263.5931 | 596.2 | 1 | 1 | 1450-Other air supply problems | SF-Startup Failure | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 302.295 | 6.3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8985.1666 | 65 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9985.0666 | 92 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 246664 | 88 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 597.375 | 442.5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1730 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.9 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 287.9 | 6 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1598.0065 | 396.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 85576 | 76 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 227262.9333 | 64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 683.26 | 50.8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 495 | 180 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22.4 | 3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 300.5983 | 5.3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2207.3333 | 28 | 1 | 2 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 56 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 265.65 | 33 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 453.7333 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 17296 | 184 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 546 | 56 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 52.5 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 68.5667 | 11 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 130 | 13 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 235688.6666 | 92 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2196.9999 | 156 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3100 | 20 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 20.2 | 101 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 741.0333 | 47 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 55.5 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 431.85 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2843.5 | 47 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 95832.2333 | 89 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 98396 | 34 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 363 | 55 | 1 | 1 | 1450-Other air supply problems | D2-Forced - Delayed | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 49.5 | 9 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 349.2 | 291 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 41 | 10 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 121.1333 | 23 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 5027.75 | 105 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 49172.63 | 96.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234.95 | 127 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4677.1266 | 216.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23286.1566 | 31.3 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.7333 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 383.8667 | 8 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 92.4666 | 76 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1233 | 54 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 80917.8666 | 69.2 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 41.25 | 15 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 371 | 106 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2229.3333 | 160 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 283.5833 | 5 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1041.8333 | 47 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 46462.5 | 45 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 100-Fossil-Steam
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 0.32 | 0.64 | 1 | 1 | 1450-Other air supply problems | D1-Forced - Immediate | 650-Fluidized Bed
1450 | Other air supply problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 1465 | 293 | 1 | 1 | 1450-Other air supply problems | U1-Forced - Immediate | 650-Fluidized Bed
1451 | Fluidized Air Fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 298.08 | 24.3 | 1 | 1 | 1451-Fluidized Air Fan | U1-Forced - Immediate | 650-Fluidized Bed
1451 | Fluidized Air Fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 2216.6666 | 266 | 1 | 1 | 1451-Fluidized Air Fan | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 161.3333 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174.1666 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 250 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 312.5 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 318.75 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 449.75 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1077.7083 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5195.008 | 13.44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.1737 | 6.59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 16 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28.6 | 6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 84.5167 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 92.95 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 151.2 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.825 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 168 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 210.6 | 81 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 242.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 261.5667 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.35 | 10.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 398.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 424.4333 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 490 | 147 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 550.6666 | 140 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 566 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 701 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 966.425 | 14.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6120 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7557.6 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40642.0667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 65.45 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170.5 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 796.5133 | 152.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 936.4333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1120.6666 | 82 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4062.5 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1654.6667 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1959.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3721.3 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 437.25 | 53 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 919.0166 | 67 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1278.3499 | 111 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1696.6333 | 46 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6671.6333 | 71 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 86 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 202.6667 | 32 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 424.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 660.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 662.15 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 1021.45 | 93 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 19 | 38 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 18 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 564.4 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 806 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2433.8333 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2866.6783 | 19.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3195.8333 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 16.8 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.8 | 4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 25.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.2367 | 6.62 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 103.4 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 124.7 | 43 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 210.6333 | 142 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 223 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 279.9297 | 390.6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 322.3833 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 374.7332 | 292 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 463.5167 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 476.0833 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 494.6665 | 560 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 497.8333 | 145 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 516 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 560 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 615.9166 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 919.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1153.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1206.2 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 128790 | 360 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 218.5333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1086.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2512.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5717.95 | 217 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 17.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 75.9998 | 240 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 270.6665 | 280 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 28717.75 | 313 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 311.5667 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 366.6 | 18 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1404.9333 | 41 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 20.8833 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 125.6667 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 326.2 | 28 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 335.6 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 436.15 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 604.2 | 57 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.8 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 208.5333 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 338.1 | 49 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 479.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12091.6665 | 250 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1136.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2160.8 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11212.22 | 26.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.568 | 3.32 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.9333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 126.6333 | 58 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 155 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 264.3333 | 244 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 286.7 | 61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 349.8666 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 685.5333 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 738.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 990.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 993.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1679.04 | 5.28 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 4370.5831 | 293 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12813.6666 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14311.5 | 290 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 313.5 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 340 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 492.3032 | 261.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 635.8333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2680.7667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.1667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 5124.9999 | 150 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 342 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 558 | 135 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 542.05 | 37 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 50.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 57.2 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 959.5333 | 74 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 981.1166 | 43 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24751.5 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44.7333 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50.7167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 101.1833 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 193.0667 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 102.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 167.8333 | 201.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 2295.5833 | 163 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6490 | 118 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22.55 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 53.6667 | 23 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 71.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 74 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 209 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 274.4 | 112 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 365.05 | 147 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 670 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 704.6 | 271 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11044.8 | 78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 180.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1410 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2079.2 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 3890.1333 | 56 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 14.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 894.9 | 23.55 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2582.9333 | 232 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 79.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 109.6333 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 239.2 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1738.0666 | 116 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1760.9833 | 67 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2716 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3383.2167 | 47 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4873.45 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 57.8 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 221.65 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 310.9333 | 53 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 529.9 | 42 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12.9167 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 299.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 755.3 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8901 | 345 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3835 | 118 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1556.3329 | 644 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7096.5 | 570 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1659794.75 | 635 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2120.5332 | 448 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 58.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1491.5 | 95 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3354.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 34013.7499 | 75 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.8895 | 13.97 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.1 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 123.7332 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 128.9666 | 146 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 424 | 265 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 673.7498 | 231 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1098.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2519 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 47.3667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 196.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 462.7333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2185.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 423.0167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 349.1667 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1029.9167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7887 | 60 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 28 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 41 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 43.8667 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 163.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 375.0666 | 58 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 809.8333 | 43 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1106.4166 | 71 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1166.9 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1371.4833 | 71 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 89.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 165.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 191.3333 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 255.6833 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 319.6 | 102 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 635.1166 | 53 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3307.5 | 27 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4052.8 | 298 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 137.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 212 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 253.4833 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 422.9333 | 122 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 424.6999 | 93 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 879 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 917.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2638.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6695.4833 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 28925.7333 | 118 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 12 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 40.194 | 3.78 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 45 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 46 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 85.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 98.1332 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 134.4 | 64 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 138.7 | 146 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 141 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 192.5 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 204.7833 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 323.3999 | 126 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 330 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 363.5999 | 108 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 368.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 418.5333 | 86 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 557.7 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 584.5332 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1098 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5742.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 40.4166 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 707.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 876.375 | 13.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 417.1999 | 168 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 62.5 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2473.3332 | 280 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6284.3 | 197 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 614.4166 | 101 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 133.45 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 156.6667 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 312 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 320.25 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1350.9 | 79 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2523 | 60 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 346.2 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5396.2499 | 225 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12.9167 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 95.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 100 | 100 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175.5667 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 246.2183 | 9.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 999.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1196.9666 | 149 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1670.8332 | 250 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1919.5833 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 5007.9166 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5369.65 | 33 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.4667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24.2533 | 13.6 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 36 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.75 | 205 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 101.9333 | 11 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.825 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 134.9 | 114 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 154 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 180 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 183 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 247.8 | 17.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 375.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1351.7332 | 137 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1420 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1440.3998 | 312 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2910.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3600 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8858.75 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 640.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2478.5866 | 226.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60.6667 | 26 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 1188.2666 | 128 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 201.6333 | 46 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 799.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 24.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 60 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 96 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 107.85 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 129.5 | 74 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.9667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 287.4666 | 28 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 422.4 | 48 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 962.7833 | 61 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1456.3333 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1470.9333 | 64 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 292.3833 | 53 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3422.2 | 71 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16322.7998 | 258 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13652.2331 | 841 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9999 | 165 | 1 | 1 | 1455-Induced draft fans | U2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.3 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 116.6667 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 179.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 338.983 | 473 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3155.3 | 278 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21816.6665 | 425 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 64 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 147.3333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 225 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 278 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 368 | 184 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 802.9165 | 235 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 816.2833 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 890.9998 | 243 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1050 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1081.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14853.6667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 99.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 13978.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 5507.3333 | 220 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 214 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 31.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 386.5333 | 52 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.7333 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 469.7666 | 34 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1824 | 38 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3323.4 | 174 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 206.1896 | 63.77 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11.9 | 17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 47.5 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 130.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 606.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 950 | 190 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3007 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5478.6 | 138 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 28665.15 | 59 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.75 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.3333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.5 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.5 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 187.2 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.6 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 319.6 | 94 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 491.8666 | 136 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 745.7331 | 329 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1028.9999 | 126 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1257.0833 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 10.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 7307.7333 | 31 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 304010 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 230.2667 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 233.3332 | 280 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1004.4 | 186 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8673.3332 | 200 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2577.75 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5207.0833 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11.8 | 2 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 58.05 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 73.2 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 113.85 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 157.3 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 506.25 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1026.1333 | 64 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1500.8666 | 188 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36456 | 49 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 272.35 | 39 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 359.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 12981 | 60 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4645.2 | 294 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4121.9998 | 540 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 150 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 445 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 720.5 | 262 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2407.1666 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4955.5167 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10133.3332 | 125 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 52312.5 | 310 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 13.4167 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.0667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 21.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.85 | 27 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 38.4 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54.1333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.4 | 18 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 341.5 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 354 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 367.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1398.4 | 92 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1541.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6443.5 | 70 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8978.1833 | 61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39312.9332 | 292 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 62 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 274.1665 | 175 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 29.25 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 813.4 | 42 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 38.8667 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1548.3 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10 | 5 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 48.2667 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 80.85 | 9 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 167.6 | 24 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 249 | 36 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 355.95 | 27 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 420.9 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1026.95 | 69 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1291.3 | 111 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5927.2333 | 82 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6348.75 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 35.5 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 188.65 | 33 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 198.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 262.8333 | 38 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8182.9 | 22 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 176.5 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 217 | 62 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 230.04 | 19.17 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 269.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 906.7431 | 391.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 909.4667 | 1.9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 7659.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2.09 | 11.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.1075 | 3.39 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13.9283 | 13.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.2917 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.9192 | 10.45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 165.5417 | 13.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 177.55 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 198.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 208.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 215.35 | 17.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 236.55 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 269.1666 | 34 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 394.0666 | 92 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 444.9333 | 47 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 534.6 | 59.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 564.3 | 22 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1047.375 | 31.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1719.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2135.0666 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4661.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 595.8333 | 110 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1686.75 | 45 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 269.55 | 27 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4236.6666 | 82 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5909.4 | 147 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 10380.1999 | 213 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 0 | 74 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 219.0167 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 631.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1414.0333 | 118 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 2967.35 | 51 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 367.2333 | 46 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3677.2 | 634 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 538 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 969.6 | 144 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5008.6666 | 55 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.0733 | 4.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.5833 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.3333 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 60.8 | 76 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 67.008 | 6.98 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 102.8 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 155 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 163.3333 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 172.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 298.4666 | 148 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 486.9833 | 61 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1378 | 530 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2103.8 | 67 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 20091.5 | 65 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 948.5 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 196.9 | 3 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 80.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 748.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1733 | 30 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 59.8 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 64.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 95.25 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 138.5 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 431.6167 | 29 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 632.5 | 50 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 135.7 | 23 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3550.15 | 37 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7622.1667 | 38 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20.4167 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.2666 | 104 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 88.6667 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 146.25 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 287.5832 | 203 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1550 | 310 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1560.4665 | 178 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2500 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11211.9666 | 118 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2.8213 | 3.68 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4.2613 | 7.52 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32.8333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.2 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74.6666 | 40 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 78.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 203.7 | 194 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 213.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 301.1166 | 89 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 575.7666 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 717.6 | 156 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 734.4 | 108 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1341.3999 | 114 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2768.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4559.6833 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 8200 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 121.3333 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 433.3333 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4181.9999 | 180 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 76726.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1055.55 | 9 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 207.4 | 68 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 38.1333 | 13 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 56.4 | 12 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 67.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 92.0833 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 99.1667 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 110.1833 | 11 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 196.2667 | 16 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 279.4167 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 590.9833 | 59 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1612.9166 | 79 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31042.5 | 45 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 74.9667 | 26 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9718.125 | 547.5 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 199.9999 | 240 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 778 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1940.4 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3037.815 | 62.7 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3130 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9732.8333 | 46 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 32081.1333 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.2 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 112 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 847.9333 | 11.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17280 | 24 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 350.55 | 57 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45709.9999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4466.6666 | 200 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 243 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 298.0833 | 35 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 69835.6399 | 319.2 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 58.2666 | 46 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 107.5 | 25 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1359.1667 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4672.35 | 81 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 17.9 | 6 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 39.3333 | 8 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 46.75 | 15 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 275 | 44 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 413.8666 | 64 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1373.3333 | 80 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 33890.85 | 49 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 600 | 150 | 1 | 1 | 1455-Induced draft fans | D3-Forced - Postponed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 0 | 0 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 31.4167 | 29 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 120.1667 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 369.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3.23 | 11.4 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 18.3333 | 50 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.75 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 46.2 | 36 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.4166 | 25 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.4 | 12 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 82.2488 | 34.51 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 118.25 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 152.0833 | 73 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 159.7333 | 16 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 195.5 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 203.4 | 54 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 285.6667 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 350.2083 | 12.5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 392 | 30 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 568 | 284 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 704.3333 | 20 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 935 | 85 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1197.35 | 77 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 11259.7167 | 19 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 67.2 | 14 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 92 | 60 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 135.2 | 13 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1654.9333 | 8 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2405.3332 | 176 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65502.4999 | 210 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 83.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 114471.7999 | 177 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 3960.8666 | 76 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.9833 | 7 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 194.3667 | 17 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 357.5833 | 35 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 403 | 93 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 821.1 | 69 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 991.2 | 63 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 99.6667 | 20 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 8179.2 | 64 | 1 | 1 | 1455-Induced draft fans | D2-Forced - Delayed | 100-Fossil-Steam
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 400.3999 | 168 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 650-Fluidized Bed
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Summer | 139.75 | 19.5 | 1 | 1 | 1455-Induced draft fans | U1-Forced - Immediate | 800-Miscellaneous
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 4075.75 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 28.3333 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 14.9999 | 90 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 127.75 | 21 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 54.2667 | 44 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5664 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 122.1667 | 5 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 51.3333 | 88 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 2073.4999 | 429 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 382 | 15 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1455 | Induced draft fans | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 3.3333 | 10 | 1 | 1 | 1455-Induced draft fans | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.0833 | 95 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 115.2 | 128 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 75 | 100 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 19.2666 | 68 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1911.65 | 221 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3357.9998 | 276 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 398.25 | 45 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 193.05 | 99 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 596.9332 | 242 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 84 | 60 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 26055.7498 | 315 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 42120.6667 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.8167 | 13 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2244 | 66 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2379.75 | 45 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 24 | 8 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 488.4 | 222 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 301.9999 | 120 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3925 | 10 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 16812.8 | 96 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14.4 | 96 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 175.1498 | 339 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 29573.5998 | 336 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1764 | 441 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 175.3333 | 40 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1076.1333 | 56 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 882.6664 | 331 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 19386.55 | 129 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 513.7 | 467 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 11.2 | 84 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 385.3998 | 246 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 69.1667 | 25 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 383.0499 | 141 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1265 | 230 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1828.1666 | 70 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 139.75 | 129 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3342.7332 | 266 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 124285 | 350 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1860 | 186 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2854.3795 | 757.8 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 550.5 | 45 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2464.7833 | 41 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 476.2498 | 225 | 1 | 1 | 1456-Induced draft fan dampers | U1-Forced - Immediate | 100-Fossil-Steam
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 3135.5165 | 419 | 1 | 1 | 1456-Induced draft fan dampers | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1456 | Induced draft fan dampers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 2100 | 90 | 1 | 1 | 1456-Induced draft fan dampers | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 552.5 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 720 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 637.5 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.9999 | 180 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1844.4666 | 146 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 551.25 | 175 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1070.9998 | 540 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10122.278 | 897.1 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1140.8332 | 185 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 894.6 | 284 | 1 | 1 | 1457-Induced draft fan lubrication systems | D2-Forced - Delayed | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3157.4995 | 757.8 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1890 | 300 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 61327.75 | 319 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5437.5 | 250 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3979.3996 | 606 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41161.938 | 897.1 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 446.35 | 79 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 761.9559 | 439.59 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6853.35 | 427 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1110.6663 | 595 | 1 | 1 | 1457-Induced draft fan lubrication systems | U1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2178 | 120 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2320 | 290 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 16967.4999 | 150 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 282.1925 | 457.61 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1195.8333 | 175 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 7166.5332 | 236 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 594.0432 | 254.59 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 100-Fossil-Steam
1457 | Induced draft fan lubrication systems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 150.6 | 50.2 | 1 | 1 | 1457-Induced draft fan lubrication systems | D1-Forced - Immediate | 650-Fluidized Bed
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3391.4998 | 630 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.7167 | 19 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 50.7167 | 17 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17.7667 | 13 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2723.85 | 27 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1729.2 | 18 | 1 | 1 | 1460-Induced draft fan fouling | D3-Forced - Postponed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 157.4999 | 270 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.6167 | 13 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 437.3333 | 20 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3354.3 | 27 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 399.6665 | 220 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 863.985 | 23.9 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13070.62 | 103.9 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27514.8666 | 71 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 15741 | 53 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1676.6667 | 20 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1815.9 | 18 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1668.3333 | 100 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 174906 | 820 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31.9 | 22 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1677.3333 | 20 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2966 | 40 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 182 | 20 | 1 | 1 | 1460-Induced draft fan fouling | D3-Forced - Postponed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25.65 | 19 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 191.0667 | 4 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1174.1333 | 16 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10.8333 | 10 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 612.6666 | 40 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 929.215 | 13.9 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 909.3329 | 620 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 365.8667 | 14 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16390.7394 | 136.23 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1939.9999 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D2-Forced - Delayed | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 291.3333 | 40 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190.6665 | 220 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 521.3333 | 10 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1036 | 20 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1168 | 120 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1460 | Induced draft fan fouling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 394.8833 | 29 | 1 | 1 | 1460-Induced draft fan fouling | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1173 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2199.6499 | 111 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 7905 | 31 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4465.2 | 244 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 23102.7333 | 247 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3.1333 | 4 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1000.1 | 73 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1006.1332 | 176 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1028.5 | 170 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 243.6 | 168 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 624.2333 | 122 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 803 | 73 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1957.4999 | 405 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2520.4666 | 28 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6183.1 | 242 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 58728.7499 | 225 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 813.1665 | 410 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1433.7 | 531 | 1 | 1 | 1470-Induced draft fan motors and drives | SF-Startup Failure | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 13708.9164 | 355 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 242.9166 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 280.5 | 102 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1119.9999 | 168 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.3233 | 140.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 303.75 | 145.8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 37144.9999 | 276 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 688.6163 | 523 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 563.75 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 453.3333 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 695.3 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 13627.5 | 158 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 499.7 | 526 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 301.1666 | 65 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 418.2 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3078.4166 | 53 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4635 | 300 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.8 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 53.7 | 18 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5643.3829 | 593 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 695 | 139 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 959.4998 | 303 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 708.8666 | 62 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1224 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1765.9999 | 120 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2047.5 | 273 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9698.5 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 100639.0666 | 104 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 8547.6833 | 43 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1359.2332 | 242 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 59.0183 | 20.83 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 112.5 | 25 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 720.3 | 42 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4678.8999 | 213 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1254.3332 | 355 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 175 | 125 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 252.0833 | 55 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 13593 | 115 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 899.5 | 257 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 3858.3333 | 250 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3902.85 | 531 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9286.6666 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 36.75 | 63 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9102.9332 | 251 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10897.8 | 246 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2274.1333 | 208 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4216.8 | 251 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 14620.5999 | 246 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 16.25 | 13 | 1 | 2 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 36.4833 | 11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 42.6667 | 16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 51573.3332 | 200 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 416.1 | 146 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4029.1999 | 168 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3472.9998 | 345 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29.1667 | 35 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 98.4 | 48 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 398.35 | 257 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8256 | 256 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.4 | 12 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 27.3333 | 10 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 250.25 | 91 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8777.73 | 190.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 3513.2625 | 28.39 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 116.9 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2810.1333 | 44 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 244.1166 | 151 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 678.15 | 33 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1964.25 | 81 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1293.3332 | 388 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 93.2167 | 47 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 60.5 | 33 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 841.5333 | 97.1 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 49388.1665 | 395 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 14 | 6 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 34.5 | 9 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Off-Peak | 49.5 | 22 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1429.0166 | 179 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 3252.9166 | 37 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 1094.5832 | 355 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 852.5 | 15 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 11289.6666 | 110 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31833 | 90 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 88.04 | 440.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 162.1166 | 71 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 23.1 | 11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 86.9 | 11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.6666 | 40 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 279.9997 | 420 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 98.3333 | 100 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 30816 | 240 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 858.6665 | 184 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 312.6832 | 257 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1316.25 | 351 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 576.5864 | 455.2 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 811.8 | 123 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4211.3833 | 41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8746.5 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 390 | 260 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 9196 | 121 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1923.7498 | 243 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 6678 | 252 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 11 | 11 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 22.2083 | 2.05 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 135.8 | 21 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 485.1667 | 41 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 881.6666 | 230 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1719.4666 | 248 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 11755.5 | 51 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3385.5998 | 276 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 328.5 | 219 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 7.4667 | 16 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 8 | 8 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2798.05 | 523 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2679.7 | 422 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 100-Fossil-Steam
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 498.6 | 83.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 132.3 | 44.1 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 650-Fluidized Bed
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 18.85 | 19.5 | 1 | 1 | 1470-Induced draft fan motors and drives | U1-Forced - Immediate | 800-Miscellaneous
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 174816.9499 | 231 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 590035 | 398 | 1 | 1 | 1470-Induced draft fan motors and drives | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 2691.6665 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2035.8 | 234 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 847.1 | 394 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 985 | 394 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 2816 | 176 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3302.9332 | 352 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1470 | Induced draft fan motors and drives | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Winter | 763705 | 190 | 1 | 1 | 1470-Induced draft fan motors and drives | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 784 | 120 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6541.6582 | 255.7 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 8375 | 335 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3602.3999 | 342 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11820.25 | 65 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 617.5 | 475 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 24111 | 90 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 148.7499 | 255 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3325.883 | 431 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2097.3329 | 605 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8064 | 128 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 429 | 165 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4042.5 | 245 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 434.4999 | 165 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6891.885 | 107.1 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 17056.963 | 419.09 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 31990 | 10 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7330.5829 | 605 | 1 | 1 | 1471-Induced draft fan motors - variable speed | SF-Startup Failure | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3050 | 122 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 15012.8812 | 135.17 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 284.1666 | 62 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1329.265 | 114.1 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 539.2949 | 206.1 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12054 | 105 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2579.492 | 174.29 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5069 | 185 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4474.5 | 471 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6554.1665 | 605 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25672.9662 | 658 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7369.1666 | 185 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11142.2499 | 105 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 454.6366 | 241.4 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 23306.56 | 336.8 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2142.2498 | 285 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 38.3332 | 230 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 100-Fossil-Steam
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Summer | 164.45 | 19.5 | 1 | 1 | 1471-Induced draft fan motors - variable speed | U1-Forced - Immediate | 800-Miscellaneous
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3038.9332 | 352 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1471 | Induced draft fan motors - variable speed | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 3400 | 170 | 1 | 1 | 1471-Induced draft fan motors - variable speed | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1138.8 | 104 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 217046.6666 | 80 | 1 | 1 | 1472-Inducted draft fan coupling | D1-Forced - Immediate | 100-Fossil-Steam
1472 | Inducted draft fan coupling | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 14083.5 | 246 | 1 | 1 | 1472-Inducted draft fan coupling | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 273.9166 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 702.9 | 99 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3893.9998 | 531 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176.6667 | 50 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23009.9999 | 90 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 65630.1333 | 112 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 81.3333 | 10 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2121.7499 | 135 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5939.5999 | 186 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7209 | 135 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 390.8666 | 164 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 622.05 | 99 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1219.1666 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1558.5499 | 219 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1801.8 | 143 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4350 | 145 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.9745 | 5.79 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.285 | 26.7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 227.7999 | 201 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 429 | 55 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1811.25 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 44.8333 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5564.25 | 45 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 524.7999 | 192 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35554.1662 | 742 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.526 | 5.54 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 426.25 | 55 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 434 | 10 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 755.0832 | 221 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3503.25 | 45 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5427.6666 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 504.0833 | 23 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1082.9999 | 180 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 20255.6666 | 140 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 370.5 | 114 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 177.3284 | 379.99 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 290.26 | 252.4 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1335 | 60 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 4 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 724.5 | 161 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 277.5 | 185 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 819.9999 | 300 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 243.95 | 123 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4939.1332 | 164 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 175 | 50 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 742 | 371 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 1332.3332 | 140 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3456.5 | 155 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.6666 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 621.4666 | 158 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3903.2499 | 195 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 142.9333 | 16 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 74617.6665 | 226 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 219 | 109.5 | 1 | 2 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 281.9166 | 85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 312.99 | 104.33 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 395.25 | 85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 219.3332 | 280 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1219.5333 | 44 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 92.9333 | 17 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 836.4 | 164 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1096.95 | 213 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4635.8999 | 162 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5238.0832 | 239 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.0983 | 36.7 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1634.6333 | 178 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1442 | 280 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 31845.5833 | 95 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 136.95 | 99 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1131.9 | 42 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2669 | 85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3427.3333 | 53 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 108.3333 | 25 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1257.6666 | 70 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 663 | 221 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6953.25 | 635 | 1 | 1 | 1475-Induced draft fan controls | SF-Startup Failure | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 72 | 72 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 130.8333 | 25 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 972.8 | 57 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 296718.2498 | 285 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 163.1373 | 49.94 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 657.4333 | 163 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12010.1998 | 333 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 388.5 | 21 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 37 | 370 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4184.8331 | 422 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 514 | 20 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 244.5833 | 25 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 370.5 | 285 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 393.7499 | 135 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 573.4999 | 186 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2731.2499 | 285 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3978 | 68 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2253.1833 | 31 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 70224.75 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 10.9999 | 330 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1006.2 | 26 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 105353.4166 | 115 | 1 | 1 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10855.4329 | 611 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 225.3998 | 276 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1089.8499 | 213 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 689.5833 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1760 | 55 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4214.0831 | 305 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 0 | 0 | 1 | 4 | 1475-Induced draft fan controls | D3-Forced - Postponed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 535 | 535 | 1 | 1 | 1475-Induced draft fan controls | U1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 425.6 | 266 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.0417 | 3.85 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 172 | 86 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 187.5 | 50 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1026 | 76 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3454.7499 | 195 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 15496.35 | 51 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 129753 | 39 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1526.8 | 22 | 1 | 1 | 1475-Induced draft fan controls | D2-Forced - Delayed | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 9766.05 | 213 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 26430.8333 | 115 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 131 | 131 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 339.99 | 113.33 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2781.25 | 125 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24815.1332 | 292 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 445.3567 | 31.4 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 100-Fossil-Steam
1475 | Induced draft fan controls | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 86.4 | 43.2 | 1 | 1 | 1475-Induced draft fan controls | D1-Forced - Immediate | 650-Fluidized Bed
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4438.885 | 66.7 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5845.2333 | 82 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3899.4 | 388 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 42920 | 200 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 183.5616 | 45.7 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3141.5 | 305 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1476 | Induced draft fan speed changer | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 125 | 125 | 1 | 1 | 1476-Induced draft fan speed changer | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 260.6999 | 198 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 457.14 | 17.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 773.9999 | 216 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23203.7666 | 104.6 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 589.2999 | 213 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1762.2 | 198 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 22.8666 | 49 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 210 | 52.5 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106758.4099 | 151.8 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22.75 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1099.0167 | 47 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 10639.8 | 257 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 601.3333 | 41 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4796.6666 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 15624 | 21 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2276.8333 | 190 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 984.2 | 57 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1089 | 55 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1739.5 | 42 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 7859.4832 | 203 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 254.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 20159.5 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 215 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 36471.6 | 216 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 505 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 664.2 | 36.9 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1327.0833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 837.0665 | 292 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3386.7513 | 66.04 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 378 | 24 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 4022.7 | 318 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 34.9999 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1009.0666 | 176 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3213.3333 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 106687.1331 | 278 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 300.8333 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 438.6666 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 36559.3333 | 61 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 860.8833 | 157 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1121.9999 | 198 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 443.3331 | 380 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 258.3333 | 100 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 105 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 765.6 | 87 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 166.3666 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4517.2497 | 855 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2149.3333 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4677.75 | 165 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 200 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1854.4167 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1000 | 200 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1194.3 | 27 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1300 | 260 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4199 | 51 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1457.8999 | 183 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4025.7332 | 277 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1291.9998 | 510 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 12 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6055.3 | 57 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15664.5 | 18 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1843.2 | 27 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 4151.3333 | 52 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 262776.25 | 145 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1954.1666 | 335 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 256.3183 | 45.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 247 | 247 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 305 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 348 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3181.7665 | 180.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5467 | 308 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 795 | 53 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 196 | 280 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 753.6 | 471 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2790.3 | 393 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12 | 60 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 38726.0998 | 243 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80 | 30 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 212.5 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 292.98 | 17.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 429.1667 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 457.2 | 27 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 704.0833 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1290.3 | 430.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2681.6667 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4071.0833 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 12558 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 489.2499 | 309 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5838.6663 | 580 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14.5833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 199.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1817.9166 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.2166 | 137 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 96.1 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 213.75 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 547.7382 | 247.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2885.4666 | 152 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15973.8716 | 205.1 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 7863.6666 | 62 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1621.2666 | 293 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 361.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1584 | 48 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 319 | 29 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3327.3333 | 70 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 6742.6666 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 15842.25 | 135 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1305 | 290 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 18599.5833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27772.2833 | 61 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 171 | 342 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 692.1832 | 349 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1310.6999 | 306 | 1 | 1 | 1480-Other induced draft fan problems | D2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4914.5833 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 29664.75 | 185 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 123708.6666 | 245 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 305 | 60 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 797.4167 | 35 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 920.1832 | 137 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4484.6666 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4720 | 590 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 267.5 | 150 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 717.5 | 175 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 892.1665 | 265 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 68.1332 | 292 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1497.25 | 565 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 45938.0832 | 427 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1795.1265 | 591.8 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 155.2 | 12 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 18226.6666 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2660 | 25 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3650 | 125 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 11582.455 | 347.3 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3.3333 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 949.05 | 27 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1085.4 | 268 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13424.6666 | 40 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 806.4 | 336 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 22895 | 241 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 573.0666 | 28 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1752.75 | 41 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4025 | 50 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66215 | 410 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2791.6663 | 625 | 1 | 1 | 1480-Other induced draft fan problems | U2-Forced - Delayed | 100-Fossil-Steam
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 450 | 37.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 468.75 | 37.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 624 | 26 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 266.25 | 37.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | PC | 650 | Fluidized Bed | RFC | Off-Peak | 2959.4666 | 31 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Off-Peak | 28437.4997 | 525 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 43.34 | 43.34 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | NPCC | Summer | 2054.375 | 37.5 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 10713.6 | 99.2 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 782.8333 | 24.4 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 650-Fluidized Bed
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Winter | 628.9383 | 25.9 | 1 | 1 | 1480-Other induced draft fan problems | U1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 80.6667 | 20 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 800-Miscellaneous
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 216 | 54 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 5.1667 | 10 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1480 | Other induced draft fan problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 405 | 54 | 1 | 1 | 1480-Other induced draft fan problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6252.4 | 42 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29949.5 | 42 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 991.7 | 47 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9648.8596 | 577.2 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 688.2167 | 17 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 382.3333 | 37 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 143 | 11 | 1 | 1 | 1487-Air heater (tubular) | D2-Forced - Delayed | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 21517.9999 | 84 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 12085.5 | 42 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 52.5 | 15 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 91 | 14 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1827.7996 | 577.2 | 1 | 1 | 1487-Air heater (tubular) | U1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3088.45 | 57 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 105 | 15 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 568.75 | 39 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 832 | 52 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 696.5 | 42 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 98 | 14 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 993.3 | 42 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6363.1998 | 291 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 30.4 | 8 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 69.3333 | 13 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 144.45 | 27 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3482.9666 | 77 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1487 | Air heater (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 88 | 8 | 1 | 1 | 1487-Air heater (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 185.4999 | 105 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 13103.5998 | 492 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.15 | 11 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.5 | 18 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.9166 | 25 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.1 | 66 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 249.3333 | 85 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9853.5996 | 654 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 79 | 15.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 537.3332 | 520 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 56.6666 | 170 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 16.0333 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112 | 64 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 19.3667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 8001.9162 | 655 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 20468.75 | 655 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5200.75 | 293 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 80970.533 | 431 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 406.5098 | 230.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1140.4165 | 425 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6637.3166 | 71 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3931.71 | 74.7 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 22.4 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 51.6666 | 31 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 70 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 234 | 65 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 45.2 | 24 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6924.7499 | 315 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 15730.9162 | 655 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 810.9 | 54 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4851.4666 | 112 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 228.34 | 93.2 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 668 | 80 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1245.1666 | 155 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1962.5 | 47.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 133.3932 | 235.4 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 19.2 | 16 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 120.6 | 54 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 135.6666 | 74 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 158.6666 | 80 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1161.75 | 45 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 79.2 | 48 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 98.05 | 53 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 44 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 29269.4997 | 855 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9473.6666 | 293 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 45 | 22.5 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 163.5433 | 114.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 393.9166 | 145 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 16520.4999 | 282 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 115.2666 | 52 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8237.58 | 230.1 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 12.6667 | 38 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 105.1166 | 53 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 790.4 | 52 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4540.6399 | 230.1 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 20.3667 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 52 | 60 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 74.7333 | 59 | 1 | 2 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 87.55 | 51 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 92.2667 | 32 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121 | 55 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 6.7833 | 11 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 50 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 3600 | 480 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13150.2932 | 251.6 | 1 | 1 | 1488-Air heater (regenerative) | U3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3607.5 | 481 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 95.3333 | 52 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5947.7733 | 151.6 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 672.2332 | 301 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 9.6 | 16 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 112.5 | 45 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 191.5333 | 68 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 262.55 | 89 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 345.6 | 96 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 69244.8164 | 869 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1313.6166 | 293 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7429.395 | 830.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2464.9998 | 255 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3642.4999 | 186 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 69.3 | 54 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 138.0166 | 49 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 88.0833 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 21210 | 505 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2594.5966 | 295.4 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 92807.0832 | 361 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 137.6667 | 35 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 808.8333 | 115 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 88.4 | 52 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99 | 60 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 124.8833 | 59 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 119.1667 | 50 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.9 | 111 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 755.0833 | 205 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2461.6 | 51 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 11.0833 | 19 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 26.0666 | 68 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 43.0167 | 29 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 54.3333 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 71 | 60 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 159 | 53 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 400.4 | 154 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 7.15 | 11 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.8348 | 230.1 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42978.105 | 687.1 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1209.8332 | 427 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4887.5 | 230 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6859.125 | 502.5 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1816.6665 | 500 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 695.3664 | 362.8 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3567.57 | 32.73 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 30.1 | 43 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 82.1666 | 58 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64 | 32 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 801.9 | 198 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 58805.28 | 757.8 | 1 | 1 | 1488-Air heater (regenerative) | SF-Startup Failure | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 216443.9997 | 765 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5338.9999 | 285 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 238.3333 | 52 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 566.8166 | 71 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 7.3333 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 53.9 | 66 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 111.1 | 66 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 261.25 | 75 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 140.8333 | 65 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 2.8167 | 13 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 285 | 380 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 90370.3332 | 361 | 1 | 1 | 1488-Air heater (regenerative) | U2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 20.8333 | 10 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 91.2 | 72 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 31.9667 | 14 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 39 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 56376 | 783 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 904.7499 | 105 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9353.55 | 491 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.5866 | 130.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 370.5 | 617.5 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17460.1333 | 136 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 84.4999 | 195 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 218.1965 | 195.4 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 20826.75 | 105 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 5.95 | 21 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 34.1 | 22 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 48.8 | 24 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 66.3 | 34 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 72.5 | 58 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 25.8 | 36 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1444.8499 | 111 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4374.9165 | 235 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 138.7732 | 130.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 954.615 | 830.1 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3348.8 | 91 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 10650.4998 | 255 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2130.5666 | 161 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 41.85 | 27 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 159.25 | 65 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 40 | 20 | 1 | 1 | 1488-Air heater (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 107.3798 | 230.1 | 1 | 1 | 1488-Air heater (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47605.6662 | 1317.5 | 1 | 1 | 1488-Air heater (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1488 | Air heater (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Winter | 275.7333 | 88 | 1 | 1 | 1488-Air heater (regenerative) | D1-Forced - Immediate | 650-Fluidized Bed
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 189117.85 | 181 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 19752.2333 | 101 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52685.4163 | 475 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U2-Forced - Delayed | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1135.3833 | 121 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6240 | 20 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5214.1 | 69 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 293849.4 | 101 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 338.3331 | 290 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 371382.2499 | 141 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 399440 | 80 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 897.4166 | 121 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1489 | Air heater (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 12750.375 | 702.5 | 1 | 1 | 1489-Air heater (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 27518.1333 | 74 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 887.4999 | 213 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4337.5 | 125 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1492 | Air heater fouling (tubular) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 7155.8 | 74 | 1 | 1 | 1492-Air heater fouling (tubular) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 40.5583 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 169.83 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 272.405 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2294 | 31 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1777.2 | 12 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19.8333 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 59.1583 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 86.645 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 631.4367 | 18.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1170 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 300 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2615.6329 | 599 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.405 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 166.185 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 424 | 106 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2703 | 53 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 473.8 | 10.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.345 | 23.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 296.2367 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 410.685 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1171.9167 | 35 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3117.3333 | 28 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10146.1 | 24.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 260.3333 | 20 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9874.6666 | 115 | 1 | 1 | 1493-Air heater fouling (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.18 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.675 | 38.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 260.4717 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 273.0383 | 28.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 17759.0833 | 65 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2673 | 11 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.9 | 10.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270 | 30 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6917.5 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 131.085 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150806.25 | 105 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 796.25 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1049.6 | 12.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1285 | 5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2762.85 | 11.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3275.4 | 31.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 29.4517 | 43.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 563.49 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 300 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 894.4 | 17.2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 106001.25 | 115 | 1 | 1 | 1493-Air heater fouling (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2.715 | 0.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 23.095 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 31.0033 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.065 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 53.9983 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 352.5217 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360.8917 | 3.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 676.83 | 23.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 686.6583 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.325 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 22.0666 | 33.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 61.3517 | 28.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 75.4167 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1204.065 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2149.1817 | 28.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1932.6167 | 19 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 405.6 | 31.2 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 17.78 | 38.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 33.75 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 216.135 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 221.1717 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 634.4166 | 115 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1129.815 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4248.3 | 51 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 828.3333 | 10 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 600.4167 | 13.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 829.885 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1042.0367 | 27.8 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 137.5 | 12.5 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1854.6666 | 40 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13892.9166 | 25 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2044.75 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 22237.7 | 10.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1365.1 | 18.7 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42.1666 | 115 | 1 | 1 | 1493-Air heater fouling (regenerative) | D3-Forced - Postponed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 139.725 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 624.105 | 8.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1138.4567 | 50.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14677.8333 | 115 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 14793.25 | 15 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112 | 16 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 211.75 | 33 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11768.1666 | 245 | 1 | 1 | 1493-Air heater fouling (regenerative) | U1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46.585 | 23.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.2833 | 18.1 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6870.8 | 19.3 | 1 | 1 | 1493-Air heater fouling (regenerative) | D2-Forced - Delayed | 100-Fossil-Steam
1493 | Air heater fouling (regenerative) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 18768 | 34 | 1 | 1 | 1493-Air heater fouling (regenerative) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10071.9 | 62 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 380.6 | 132 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1420.25 | 15 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34268.5663 | 487 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | U3-Forced - Postponed | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6763.1666 | 62 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1996.8 | 312 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3280.9 | 86 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 300.6 | 167 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | U1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 39750 | 250 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1847.3333 | 20 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9395 | 20 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2618.6666 | 64 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 100-Fossil-Steam
1495 | Other air heater fouling (heat pipe; plate-type) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 64 | 15 | 1 | 1 | 1495-Other air heater fouling (heat pipe; plate-type) | D1-Forced - Immediate | 800-Miscellaneous
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 775.9998 | 291 | 1 | 1 | 1500-Air heater soot blowers | D1-Forced - Immediate | 100-Fossil-Steam
1500 | Air heater soot blowers | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 31701.6331 | 682 | 1 | 1 | 1500-Air heater soot blowers | U2-Forced - Delayed | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 220 | 20 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 307.9167 | 25 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 959.6667 | 20 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.6267 | 8.2 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 102.1767 | 15.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120.8 | 15.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122640 | 14 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 486.6166 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11.5383 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50.1666 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 173.075 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 119329.3329 | 620 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 150.5 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 146.4866 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.5883 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 358.625 | 15.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 125.625 | 20.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 548.3216 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 599.5833 | 25 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.5933 | 5.2 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 215.215 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 270.9 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 239.8333 | 10 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2879.6667 | 20 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 353.675 | 30.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.465 | 20.1 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1510 | Flue gas ducts (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 4784.5833 | 25 | 1 | 1 | 1510-Flue gas ducts (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 101470.4165 | 325 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 266.658 | 126.98 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2939.5831 | 425 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8887.9999 | 240 | 1 | 1 | 1512-Flue gas expansion joints | U1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 369.8999 | 162 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 545 | 15 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6 | 6 | 1 | 1 | 1512-Flue gas expansion joints | D1-Forced - Immediate | 100-Fossil-Steam
1512 | Flue gas expansion joints | Boiler | Boiler Air and Gas Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 98565.0332 | 361 | 1 | 1 | 1512-Flue gas expansion joints | U2-Forced - Delayed | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 14692.5333 | 56 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 636.18 | 41.4 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 33045.75 | 27 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 21886.5833 | 89 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1126.8 | 31.3 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4984.6833 | 73 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 60765.1666 | 95 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 406.4 | 254 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | U1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 54524.4 | 36 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1520 | Flue gas dampers (except recirculation) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4918.95 | 51 | 1 | 1 | 1520-Flue gas dampers (except recirculation) | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 604.2407 | 6.28 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 140282.8666 | 68 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 98020.25 | 69 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22777.6898 | 647.4 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 35 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 117.5 | 30 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1068.75 | 225 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1305.25 | 69 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 386.5458 | 10.15 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 40319.4167 | 35 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 16838.4999 | 255 | 1 | 1 | 1530-Other flue gas problems | U1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 916.57 | 45.3 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 97.4167 | 35 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1530 | Other flue gas problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 192.6999 | 123 | 1 | 1 | 1530-Other flue gas problems | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 328.5 | 18 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1904 | 272 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1259 | 60 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 110427.6 | 72 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2449 | 31 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 29146 | 26 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5797.4499 | 141 | 1 | 1 | 1535-Flue gas recirculating fan | U1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2789.5833 | 125 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1008.5 | 10 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2275 | 26 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1535 | Flue gas recirculating fan | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3886.6667 | 16 | 1 | 1 | 1535-Flue gas recirculating fan | D1-Forced - Immediate | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 115128.0666 | 116 | 1 | 1 | 1550-Flue gas recirculation fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 50 | 50 | 1 | 1 | 1550-Flue gas recirculation fan motors | D2-Forced - Delayed | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 277 | 277 | 1 | 1 | 1550-Flue gas recirculation fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1550 | Flue gas recirculation fan motors | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 204488 | 96 | 1 | 1 | 1550-Flue gas recirculation fan motors | D1-Forced - Immediate | 100-Fossil-Steam
1555 | Flue gas recirculation fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 960 | 480 | 1 | 1 | 1555-Flue gas recirculation fan controls | SF-Startup Failure | 100-Fossil-Steam
1555 | Flue gas recirculation fan controls | Boiler | Boiler Air and Gas Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 400.8332 | 325 | 1 | 1 | 1555-Flue gas recirculation fan controls | SF-Startup Failure | 100-Fossil-Steam
1570 | Flue gas recirculation ducts | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 16176.8 | 146 | 1 | 1 | 1570-Flue gas recirculation ducts | U1-Forced - Immediate | 100-Fossil-Steam
1580 | Flue gas recirculation dampers | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 249.1666 | 65 | 1 | 1 | 1580-Flue gas recirculation dampers | D2-Forced - Delayed | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 32 | 30 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1260.6667 | 20 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.3333 | 20 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 110 | 40 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.3333 | 20 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 100-Fossil-Steam
1590 | Stacks (use code 8430 for stack problems due to pollution control equipment) | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 744.5805 | 363.21 | 1 | 1 | 1590-Stacks (use code 8430 for stack problems due to pollution control equipment) | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1554.5832 | 325 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 781.9998 | 345 | 1 | 1 | 1591-Stack damper and linkage | D1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2063.4665 | 584 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 850-Combined Cycle Block
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 31.5 | 126 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 468.2999 | 126 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1591 | Stack damper and linkage | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 2510.5332 | 152 | 1 | 1 | 1591-Stack damper and linkage | U1-Forced - Immediate | 851-CC GT units
1592 | Stack damper linkage motors | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 648.7399 | 195.6 | 1 | 1 | 1592-Stack damper linkage motors | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 625.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3292.6665 | 220 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 41.6933 | 42.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.4133 | 42.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 37530.2667 | 8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 43.7167 | 8.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 222 | 6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 231.92 | 8.92 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 260 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 361 | 14.44 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1526.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2906.75 | 10.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63.98 | 9.14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 100 | 6.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 90 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1771.7498 | 285 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 246.3998 | 231 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3255 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 10117.9167 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2238.3333 | 50 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 390.3167 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 593.9533 | 5.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2396.8166 | 31 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 640 | 16 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 911.645 | 42.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 10.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 259.94 | 6.34 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 412.92 | 44.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 110 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 765.6 | 9.57 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13249.5 | 21.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 289585.0332 | 158 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1599 | 195 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 184.8 | 231 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 133 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1165 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 865.15 | 121 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 784.4667 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 140 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1012.6665 | 280 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.3 | 243 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Off-Peak | 19.343 | 40.02 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 208 | 20.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 432 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 911.5167 | 13 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 153 | 15.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 191.04 | 5.97 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 273 | 19.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 742.4433 | 9.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3777.0833 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 197.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1253.3333 | 40 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 228 | 19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9851.2167 | 23.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 120 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 384.25 | 7.25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2604.8998 | 342 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 146.6667 | 44 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 185.8533 | 42.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 171711.4664 | 352 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 17.875 | 3.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 221.95 | 9.65 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 826.2 | 34 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1401.4 | 24.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 280 | 7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1188.28 | 9.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3985.2 | 8.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 169.3999 | 231 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8331.25 | 155 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.16666 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 152.65 | 2.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 358.05 | 10.23 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 457.95 | 21.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 843.8583 | 77.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 55 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 590.52 | 4.44 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 977.73 | 8.97 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1489.53 | 12.11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 156 | 3.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 384.8 | 14.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5524.8667 | 14 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3513.6663 | 508 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 160.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2616.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 344.3533 | 109.9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1002.1666 | 70 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2879 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 254.6 | 12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 50 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6354.92 | 48.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.06 | 5.74 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1210.3 | 9.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 728.2 | 33.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 780 | 80 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 24.1173 | 4.76 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 117.04 | 5.32 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 5275.6666 | 98 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 101.01 | 4.81 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 283.2 | 4.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1683.36 | 20.04 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2038.5567 | 10.6 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5134 | 15.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 655.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1358.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5201 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.03 | 9.29 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4068.225 | 12.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 56 | 11.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 171 | 9 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 460.9 | 8.38 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1228.3 | 7.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 87.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 15274.6 | 53 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12.75 | 3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 526.25 | 25 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 712.25 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 400 | 5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 831.6 | 23.1 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 62 | 6.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 108 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 64 | 2 | 2 | 2 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 116.87 | 4.03 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 539.92 | 15.88 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1666.5 | 16.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1717.7 | 19.3 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.5833 | 175 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 535.2 | 223 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 202 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3798.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58.4667 | 4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25200 | 35 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 513.8 | 36.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1364 | 60 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 360.8 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 281.6 | 12.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2278 | 8.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 63 | 3.15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 83.98 | 6.46 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 248.04 | 6.89 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1996.75 | 14.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1243.1 | 20.05 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 200.1999 | 78 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 810.6667 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1136.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 88.319 | 23.87 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 1086.6533 | 11.95 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 600 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1064.24 | 21.2 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1332 | 12 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 100.8 | 2.24 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 472.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13123.9998 | 255 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 32440.2166 | 109 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 261.9 | 32.4 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2262.3333 | 20 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 896.5333 | 8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2788.8 | 16.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 171.8333 | 10 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D2-Forced - Delayed | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 166.6 | 147 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Summer | 20.01 | 40.02 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 100-Fossil-Steam
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 650 | Fluidized Bed | SERC | Winter | 513.2332 | 173 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 843.3332 | 460 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Off-Peak | 232.2665 | 268 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 650-Fluidized Bed
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 94.3667 | 19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 126.3 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 150.9 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 50.9667 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 0 | 0 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 37.2167 | 11 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 55.4167 | 19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 57.3167 | 19 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Off-Peak | 265.25 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 0 | 0 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 137.4 | 18 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 149.25 | 15 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 800-Miscellaneous
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 19902.5 | 419 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 976 | 64 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 3870.75 | 65 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 850-Combined Cycle Block
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 427.9999 | 160.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 4094.3332 | 355 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 49651.2 | 28.8 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 556.2 | 206 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1526.5 | 355 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 851-CC GT units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 288.9 | 107 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 423.9999 | 159 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 524.4 | 72 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | U1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | HRSG Boiler | HRSG Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 18446.8 | 10.7 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 852-CC steam units
1599 | Other miscellaneous boiler air and gas system problems | Boiler | Boiler Air and Gas Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | NPCC | Summer | 272.25 | 247.5 | 1 | 1 | 1599-Other miscellaneous boiler air and gas system problems | D1-Forced - Immediate | 860-Co-generator Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 674.6664 | 460 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 26.1333 | 16 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 275.9 | 31 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30613 | 230 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 566.95 | 51 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 65.25 | 435 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 87.6 | 109.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 807.85 | 151 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.15 | 63 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 7.6666 | 115 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 54.9999 | 165 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 723.7998 | 564 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1085.5166 | 31 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 36.5 | 109.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1341.6665 | 250 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5105.3332 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 329.25 | 45 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 648.55 | 21 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 73.8 | 108 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 80.3 | 109.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9.0393 | 77.48 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1659.9996 | 600 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 94.6666 | 80 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4110 | 600 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 584.1998 | 276 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 91.4466 | 94.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 23.45 | 21 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138442.4995 | 810 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 18117 | 610 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U3-Forced - Postponed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2467.3167 | 46.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3680 | 320 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 87600 | 10 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 92.1667 | 35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2697.0665 | 416 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 1699.9998 | 510 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 185.85 | 63 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 444.8 | 139 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 57.8833 | 151 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 310.3331 | 380 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 691.39 | 406.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 657.4981 | 406.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 539.7498 | 255 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 602.6 | 524 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 67.2 | 64 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 547.0832 | 325 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 1286.285 | 42.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 47.4999 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Winter | 95 | 114 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1011.3328 | 740 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 304.4998 | 315 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 302.0025 | 30.15 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 115.2883 | 22.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 242.8333 | 31 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 962.5231 | 406.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 993.3 | 94.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1352.4 | 552 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 32.6625 | 30.15 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | TRE | Winter | 253.7499 | 105 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 1389.8666 | 64 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 800 | Miscellaneous | SERC | Summer | 379.1665 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 800 | Miscellaneous | RFC | Winter | 112.5 | 90 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 800-Miscellaneous
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 256351 | 389 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 665.5333 | 119.2 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 225.3333 | 208 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 1096.5 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 69.872 | 349.36 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 691.8499 | 303 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 931.515 | 477.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 2173.3666 | 113 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 117.15 | 213 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 14.3332 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 471.2332 | 134 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 668.1665 | 190 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 2327.6456 | 282.71 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 112.9699 | 260.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 12346.4332 | 173 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1011.75 | 285 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D3-Forced - Postponed | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 239.8666 | 257 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 72978.8331 | 314 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 72.8333 | 46 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 97.0665 | 208 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 420.3332 | 260 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 334.95 | 231 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 1265.3332 | 260 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 754.5998 | 231 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 5302.45 | 173 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 5043.75 | 75 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 106.6666 | 200 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 347.1999 | 186 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1104.9 | 174 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 25.815 | 172.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 210.8066 | 122.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 82.5999 | 177 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 2082.1666 | 155 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 285 | 57 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 528.9999 | 345 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 21293.2999 | 199.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 57 | 57 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 76.95 | 57 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 3478.7665 | 238 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 152.775 | 145.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 638.6333 | 238 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 1368.5 | 238 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1564.9899 | 169.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 269.7 | 174 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 1212.1999 | 174 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 170.1333 | 32 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U2-Forced - Delayed | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 17.2833 | 17 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 428.6332 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 967.98 | 189.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 3113.9166 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 347.9166 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 104.38 | 122.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 385.6999 | 174 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U3 | Forced - Postponed | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 17214.7499 | 189 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U3-Forced - Postponed | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 619.9166 | 215 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 59.1666 | 177.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 5672.9165 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 895.3332 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 1261.6 | 152 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1141.8667 | 16 | 2 | 2 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3729.9666 | 149 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 131.9432 | 172.1 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 506.7699 | 162.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 2060.55 | 241 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 307.7333 | 16 | 2 | 2 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 490.4 | 16 | 2 | 2 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 172.5666 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1644.85 | 67 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 1275.95 | 151 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 207.7 | 67 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 650.4 | 162.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 7219.0499 | 171 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 1003.86 | 202.8 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 562.4 | 19 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 413.38 | 187.9 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 26.25 | 175 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 1060.4 | 241 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 8311.3999 | 174 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 179.9499 | 183 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 1861.2 | 310.2 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 160.8333 | 50 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 361.25 | 85 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 2573.7332 | 194 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 167 | 167 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 68.6166 | 179 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 173.7 | 54 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 55.6166 | 71 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 56.8 | 71 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 1130.0666 | 67 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 875.5833 | 95 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 2338.6666 | 160 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 42.4999 | 102 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 149.8333 | 145 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 352 | 88 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 181.2166 | 131 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 1376.55 | 161 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 920 | 160 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 78.6 | 393 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1294.85 | 141 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 708.4 | 161 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 492.5 | 150 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 912.6332 | 131 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 681.615 | 137.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 609.6 | 96 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 558 | 90 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 83.3266 | 172.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Summer | 1221.9166 | 170.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 164.2666 | 176 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 383.3333 | 250 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 1036 | 35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Winter | 1437.3332 | 280 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 35.5833 | 35 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 490.1 | 78 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 9199.4166 | 101 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D3-Forced - Postponed | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 219.3 | 102 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 34.4667 | 44 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 941.6333 | 41 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 205.8 | 84 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 18.855 | 125.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 865.2 | 216.3 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 186.0832 | 203 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 96.3699 | 125.7 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 290.3832 | 131 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 73.6 | 92 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 306.7333 | 172 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1228.4 | 148 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 128.8166 | 131 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 10701.5 | 170 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 103.1799 | 92.4 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 434.6999 | 162 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 94.0333 | 26 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 53.25 | 213 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 31.4166 | 145 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4585.5999 | 96 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 254.6133 | 123.2 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 397.8332 | 155 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 120.7499 | 315 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 216.4165 | 265 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 35.2 | 44 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 393.75 | 157.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 38.4 | 72 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 3727.4832 | 149 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 4010.5833 | 95 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 93.2833 | 29 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 285.2333 | 86 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 852-CC steam units
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 149 | 74.5 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | SF-Startup Failure | 860-Co-generator Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 566 | 40 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | D1-Forced - Immediate | 860-Co-generator Block
1700 | Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 566.4866 | 79.6 | 1 | 1 | 1700-Feedwater controls (report local controls --- feedwater pump; feedwater regulator valve; etc. --- with component or system) | U1-Forced - Immediate | 861-CoG GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.6666 | 46 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 109.0667 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.3333 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 262.15 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 121.6667 | 20 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 136.9 | 37 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 370.8333 | 50 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1646.7998 | 552 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2379.8 | 652 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 211.25 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 187.4667 | 38 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 147.6 | 24 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 99.2 | 31 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 180.7667 | 22 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1107 | 27 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 124.6 | 89 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 912 | 95 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1955.7666 | 46 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 760.5333 | 32 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 694.5 | 18 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 414.05 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 37.4 | 11 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 105074.2 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 331.4166 | 97 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 446.7166 | 49 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 112 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 2656.1998 | 342 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 81.3167 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1529.55 | 27 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 52.1166 | 59 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 169.8667 | 26 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4680.93 | 33.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3048.8333 | 22 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 45882.6666 | 40 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 481.3333 | 19 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1406.3 | 41 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 785.3998 | 306 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2265.9998 | 660 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2872.4999 | 450 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 297.6 | 31 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2307.75 | 45 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 11.5 | 23 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 26.45 | 23 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.9333 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2827.5 | 290 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 349.9998 | 300 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 740.1333 | 244 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 4083.1332 | 292 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 256.25 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 7311.8666 | 122 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 90.1 | 51 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 283.2667 | 14 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 97.0833 | 25 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 200 | 12 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 518.4 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 210.4666 | 28 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 485.45 | 19 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2615.6666 | 76 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1986.3 | 27 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3405.35 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 7481.7663 | 577 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 303.3332 | 325 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 68.25 | 45 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.4 | 341 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 377.4333 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 112.6667 | 20 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1900 | 50 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 317.3332 | 224 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 248 | 96 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 774.9 | 54 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2472 | 48 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 175.9999 | 192 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3484.9998 | 246 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | SF-Startup Failure | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122.6667 | 16 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 229.5666 | 194 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 200230 | 40 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 96.25 | 21 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 289.4999 | 90 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 4759.4994 | 855 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 50.7 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 359.6 | 24 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 33.3333 | 20 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 101890 | 40 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1044.65 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1024.7666 | 71 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 218.3333 | 50 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1648.8499 | 147 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2867.262 | 6.78 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 47.8333 | 14 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 162.6 | 12 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 1870 | 33 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 3155.4833 | 43 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Winter | 64.3167 | 17 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D2-Forced - Delayed | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 218.1666 | 170 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 376.8332 | 170 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 450.7996 | 552 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 459.1166 | 169 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 100-Fossil-Steam
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.2 | 3.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.3 | 3.1 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 10.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 16 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 171.2 | 21.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.8 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21.6 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 56.4 | 4.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 19.8 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 72 | 4.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 159.8 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.2 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14.8 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 1349.3333 | 92 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.3 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 17.5 | 3.5 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 36 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 151.9 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.7 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 7 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 16.4 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 36.9 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 42.9 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 11.4 | 3.8 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 13.6 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 48 | 4.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 17 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3 | 3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.2 | 3.2 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.8 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | PC | 650 | Fluidized Bed | SERC | Winter | 6317.3333 | 92 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.9 | 3.3 | 1 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.2 | 3.2 | 1 | 4 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 4 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 88.8 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 9.3 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 21 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.6 | 4.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 115.2 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 23.8 | 3.4 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 14.4 | 3.6 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 15.6 | 3.9 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 41 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 15.5 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 42 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 75.6 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 151.7 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.2 | 3.1 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 16 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 20.4 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.4 | 3.2 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.3 | 3.3 | 2 | 7 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 30.6 | 3.4 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.4 | 3.2 | 2 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.4 | 3.4 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 6.6 | 3.3 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 44 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.4 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3 | 3 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.6 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.6 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 22.2 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 7.2 | 3.6 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.6 | 3.3 | 1 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 66.6 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 9.9 | 3.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 41.8 | 3.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 9.6 | 3.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 12.4 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 24.5 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.1 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 56 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 4.5 | 4.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 8.4 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 15.6 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 28.7 | 4.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 32.4 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.4 | 3.4 | 1 | 3 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 13.2 | 3.3 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 21 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.5 | 3.5 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 17 | 3.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 33.6 | 4.2 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 136 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 5.1 | 5.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 27.2 | 3.4 | 1 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 3.3 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 3.1 | 3.1 | 2 | 6 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 29.6 | 3.7 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 36 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.6 | 3.3 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.4 | 3.7 | 2 | 2 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 13.2 | 3.3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 26.4 | 4.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 6.2 | 3.1 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 14 | 3.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 21.6 | 3.6 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 39 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Off-Peak | 46.2 | 15.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 3.1 | 3.1 | 2 | 8 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Winter | 1.75 | 3 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 11.7 | 3.9 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Winter | 40 | 4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 650-Fluidized Bed
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 19936 | 448 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 299.925 | 193.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 416.025 | 193.5 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1286.8531 | 360.8 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 105.75 | 15 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 850-Combined Cycle Block
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 245.9266 | 199.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 219.7328 | 227.31 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 375.1999 | 168 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 250.7499 | 177 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | U1-Forced - Immediate | 851-CC GT units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 202.9999 | 210 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 176.3166 | 71 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 149.3166 | 105.4 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1710 | Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 722.1499 | 303 | 1 | 1 | 1710-Combustion/steam condition controls (report local controls --- burners; pulverizers; etc. --- with component or system) | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 72.1 | 206 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4.11 | 0.3 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 3734.4999 | 165 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 196.8 | 123 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 153.3332 | 230 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1588.6833 | 199 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 71.55 | 95.4 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 974.3999 | 261 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1716.6664 | 412 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 37.87 | 0.3 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 112.8333 | 135.4 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 33081.55 | 176.2 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 88.45 | 61 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 150 | 72 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 534.9999 | 300 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 478.3666 | 254 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 10733.8 | 51 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 50.1166 | 97 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 896.1 | 206 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 5374.7662 | 766 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 100-Fossil-Steam
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 27.727 | 79.22 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5954.85 | 297 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 58.0946 | 79.22 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 197.1 | 81 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 369.8666 | 152 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 130.9633 | 20.2 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 850-Combined Cycle Block
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 143.8666 | 166 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 436.3333 | 238 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 20.9 | 19 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 38.95 | 19 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 184.575 | 160.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | SF-Startup Failure | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 311.805 | 159.9 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 57.6666 | 173 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 110.49 | 38.1 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 22.3999 | 168 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 313.4998 | 342 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 575.1665 | 238 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 521.25 | 139 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 99.0166 | 228.5 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 604.8 | 189 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 133.45 | 157 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 224.6832 | 221 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 25.3 | 23 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 851-CC GT units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Summer | 130.1332 | 128 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 36.9 | 18 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 51.3 | 81 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1067.5332 | 268 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 397.8 | 51 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 190.9499 | 171 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 293.3333 | 160 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 386.6666 | 160 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 19.8 | 18 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 487.5 | 130 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 34.6666 | 104 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 852-CC steam units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | WECC | Summer | 309.8666 | 166 | 1 | 1 | 1720-Desuperheater/attemperator controls | U1-Forced - Immediate | 861-CoG GT units
1720 | Desuperheater/attemperator controls | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Summer | 225.8666 | 121 | 1 | 1 | 1720-Desuperheater/attemperator controls | D1-Forced - Immediate | 862-CoG steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 117.7 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 38.7499 | 75 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 1413.1666 | 122 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 208.65 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 136.2999 | 174 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 329.5833 | 175 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1833.4996 | 570 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 376.2833 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 130.1833 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 187.25 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 816.6666 | 100 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 5023.2 | 78 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 417.9998 | 570 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 165.85 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 238.9666 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 908.8331 | 410 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.5 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 334.6833 | 46.7 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 51.7166 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1791.7666 | 98 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | SF-Startup Failure | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 62.4166 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 340.6166 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 545.16 | 46.2 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 778.333 | 467 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 456 | 570 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.0833 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 583.75 | 467 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 242.9166 | 275 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1056.733 | 524 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1261.7283 | 122.3 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 4126.4665 | 374 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U3-Forced - Postponed | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 744.6332 | 502 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 16036.6664 | 680 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65.9833 | 107 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 240.5 | 78 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 166.25 | 175 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 100-Fossil-Steam
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 800 | Miscellaneous | SERC | Summer | 851.6666 | 350 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 800-Miscellaneous
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 18 | 90 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 39.0133 | 53.2 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 117.6 | 48 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 4828.5 | 522 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 153.1 | 122.48 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 21750.3 | 507 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 32.6667 | 35 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 114.6666 | 215 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 850-Combined Cycle Block
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3398.0166 | 67 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 201.1666 | 71 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 325.5 | 35 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 994.2999 | 183 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 795.3 | 241 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 3275.19 | 144.6 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 74.55 | 71 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 693.5332 | 206 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 75.1583 | 155.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 510.9249 | 160.5 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 79.2833 | 71 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 289.8332 | 185 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 851-CC GT units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 573.3 | 26 | 1 | 2 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 394.5 | 90 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 150.1665 | 265 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 16897.9499 | 81 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 456.4 | 84 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 426.4 | 82 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 506.1499 | 159 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 149.1 | 71 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 531.3 | 161 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 306.3666 | 91 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 892.6667 | 26 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 112.8 | 72 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 32.5867 | 20.8 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 337.1333 | 52 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 73.9499 | 153 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1653.6666 | 82 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | D1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 86.25 | 115 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 852-CC steam units
1740 | Boiler drum gage glasses/level indicator | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 82.5 | 165 | 1 | 1 | 1740-Boiler drum gage glasses/level indicator | U1-Forced - Immediate | 861-CoG GT units
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63644.2533 | 106.31 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 84.7 | 77 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2224.4 | 536 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 3473.75 | 397 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 9438 | 121 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 71.7317 | 22.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 189.0667 | 16 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12.9999 | 156 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 153.9997 | 420 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 269.4666 | 344 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2166.75 | 107 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 90.4499 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 462 | 420 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 238.4665 | 292 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 514.6666 | 80 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6471.8999 | 243 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 134.25 | 179 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72705 | 1110 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 105.6 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 985.8333 | 169 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1295 | 740 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 4429 | 515 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 7.6667 | 23 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 55.5 | 92.5 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 358.3333 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 210 | 120 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 720 | 60 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2264.1666 | 275 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 615.0667 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2312.2666 | 299 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 3495.9998 | 552 | 1 | 1 | 1750-Burner management system | SF-Startup Failure | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 599.3331 | 580 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 9.2 | 23 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 103.9999 | 240 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 223.945 | 447.89 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 587.3333 | 40 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2200 | 100 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1019.6665 | 380 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 1019.6666 | 230 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5219.3 | 114 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1581.9167 | 41 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2132 | 82 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 679.9998 | 300 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 269.9665 | 178 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 597.7999 | 147 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 20860.45 | 67 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 970.4085 | 208.69 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1285.4666 | 311 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2880 | 480 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1019.1333 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 31.85 | 49 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 55.5833 | 23 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 99.1666 | 170 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 730.3998 | 528 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 81921.5831 | 595 | 1 | 1 | 1750-Burner management system | U2-Forced - Delayed | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 5.6 | 24 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 111.6499 | 231 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 16.8667 | 23 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 59.25 | 79 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 68.8 | 86 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 766.6664 | 400 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.7333 | 38 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 26.8667 | 26 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 617.8 | 4 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 845 | 169 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 324.375 | 25.95 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6660 | 1110 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16520.5829 | 635 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2244.7996 | 552 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 231.55 | 33 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 2911.6667 | 20 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2454.3328 | 740 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1073 | 740 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 100-Fossil-Steam
1750 | Burner management system | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Off-Peak | 1472.0966 | 42.1 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 650-Fluidized Bed
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 87.9666 | 182 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 196 | 40 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 14.07 | 60.3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 156.6666 | 40 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 28.42 | 30.45 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1997.28 | 175.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 117.4 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 214.1306 | 54.44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 820.5466 | 63.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 11608.9599 | 163.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 392.4666 | 168.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 585.04 | 49.44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 928.1066 | 158.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1254.92 | 183.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 18852.4166 | 168.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 99.704 | 49.44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 9718.76 | 183.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 193.3333 | 16 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1.875 | 12.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 9047.14 | 48.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 161 | 23 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 367.63 | 58.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 128.2 | 12 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1277.22 | 25.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2792.12 | 23.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3.125 | 12.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 18.87 | 10.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2581.6833 | 38.2 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 93.7333 | 76 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 136.272 | 53.44 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 850-Combined Cycle Block
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 76.65 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 778.425 | 160.5 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 77 | 21 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 37.6 | 47 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 851-CC GT units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Summer | 41.85 | 31 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 35.2667 | 23 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 920.4 | 72 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 98 | 24.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 169 | 65 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 501.6 | 114 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 182.25 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 475.1999 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 212.7999 | 114 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 285.7166 | 79 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1243.35 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 13.8833 | 24.5 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 63.25 | 33 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 313.1999 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 174.605 | 14.1 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 553.5 | 81 | 1 | 1 | 1750-Burner management system | U1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 37.4 | 33 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 239.1667 | 41 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 419.7666 | 49 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 812.25 | 57 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 26.2 | 3 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 109.25 | 57 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 5.5533 | 11.9 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 494.1667 | 25 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 771.15 | 159 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 852-CC steam units
1750 | Burner management system | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Winter | 70.25 | 15 | 1 | 1 | 1750-Burner management system | D1-Forced - Immediate | 862-CoG steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 206.6667 | 20 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 449.5833 | 25 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 936.0662 | 739 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | SF-Startup Failure | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20206.3166 | 151 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 221.7833 | 7 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D2-Forced - Delayed | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1591.38 | 757.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 57.1666 | 70 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 19 | 15 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D2-Forced - Delayed | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 344.7833 | 151 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 11715 | 213 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4147.9998 | 510 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5070 | 650 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 1029.5165 | 223 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 350.74 | 98.8 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 222.74 | 103.6 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 979.9998 | 735 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 6584.7791 | 616.36 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2005.0585 | 362.36 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 500.65 | 93 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1437.0166 | 151 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 17394.6666 | 176 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 801.2333 | 86 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 19422.7499 | 171 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 740.05 | 361 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 142.61 | 219.4 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 1227.6499 | 129 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 78.845 | 121.3 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 16383.4998 | 465 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U2-Forced - Delayed | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 112.9333 | 154 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 366.0666 | 68 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 17952 | 176 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | SERC | Summer | 383.5999 | 84 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 861-CoG GT units
1760 | Feedwater instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | SERC | Summer | 463.3999 | 84 | 1 | 1 | 1760-Feedwater instrumentation (not local controls) | U1-Forced - Immediate | 861-CoG GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 212.333 | 455 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1152.5333 | 8 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2568.4166 | 119 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1490.3395 | 757.8 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 8607 | 151 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 42 | 84 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 64.05 | 18.3 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2696.4 | 37.8 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3030.7332 | 538 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 2.35 | 47 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 14.7333 | 68 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 599.45 | 315.5 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 72.8 | 208 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 345.627 | 203.31 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | SF-Startup Failure | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 499.7999 | 153 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 359.1 | 378 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 529.2 | 378 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 87.8333 | 34 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 37.8 | 378 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 77.5 | 30 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 239.3999 | 378 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 2683.8 | 378 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 64.5833 | 25 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 162.639 | 95.67 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | SF-Startup Failure | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 594.5332 | 182 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 41.7 | 417 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 861 | CoG GT units | SERC | Off-Peak | 761.5999 | 84 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U2-Forced - Delayed | 861-CoG GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 11.5332 | 173 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | U1-Forced - Immediate | 861-CoG GT units
1761 | Combustion /Steam condition instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 6.0666 | 91 | 1 | 1 | 1761-Combustion /Steam condition instrumentation (not local controls) | D1-Forced - Immediate | 862-CoG steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10933.3328 | 800 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 172.9 | 91 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 100-Fossil-Steam
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Winter | 259.5 | 18 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 650-Fluidized Bed
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 47.3333 | 71 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 850-Combined Cycle Block
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 47.15 | 23 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 2628.9999 | 165 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 396.6666 | 170 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 103.5 | 138 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 851-CC GT units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 429.2332 | 158 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 452.6832 | 173 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 1510.0333 | 89 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 93 | 90 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | U1-Forced - Immediate | 852-CC steam units
1762 | Desuperheater/attemperator instrumentation (not local controls) | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 82.5 | 66 | 1 | 1 | 1762-Desuperheater/attemperator instrumentation (not local controls) | D1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 44.9166 | 77 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 223.8666 | 146 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 1427.7666 | 295.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 63.3333 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 283.3333 | 40 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 167.4 | 31 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4064.5 | 739 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6264.9999 | 300 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1045.4332 | 158 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 190.19 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 529.5 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1813.55 | 437 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 4698.933 | 536 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1609.2 | 596 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 31013.5825 | 1265 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 2595.4997 | 435 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 718.25 | 169 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11896.59 | 162.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5449.9998 | 654 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 970.7833 | 157 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1108 | 554 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 446 | 446 | 1 | 2 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7111.7998 | 243 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 25826.1999 | 417 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 391 | 230 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 69 | 10 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 112.95 | 7.53 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 146.6666 | 80 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1204.2 | 446 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4009.25 | 35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 49.5 | 15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 122.6666 | 80 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2310.3499 | 147 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 194.6666 | 80 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 900.3333 | 73 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 410.22 | 4.77 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 211.3331 | 634 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7537.4996 | 1350 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 282.2665 | 292 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 368.1 | 54 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17914.9998 | 300 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 529.2 | 49 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U2 | Forced - Delayed | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Summer | 105.105 | 42.9 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U2-Forced - Delayed | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1112.4 | 824 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 632.4 | 527 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 262.5 | 75 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1980 | 30 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5761.5831 | 595 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14799.9162 | 1317.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 593.6 | 112 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 542.7 | 30.15 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 270.15 | 180.1 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 389.9999 | 180 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 153.6 | 256 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 2253.3 | 174 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 587.681 | 148.78 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1499.9999 | 144 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 191.6665 | 500 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 237.6 | 72 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 316.3999 | 339 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29539.9998 | 300 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 262608.2492 | 1257 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 91.7476 | 148.78 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6552 | 240 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Oil | DI | 100 | Fossil-Steam | NPCC | Summer | 7906.17 | 374.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 190.9998 | 573 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 21031.2997 | 438 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 312.6666 | 56 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 2836.3332 | 508 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 318.6 | 108 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 9892.855 | 730.1 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 60.9666 | 31 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 726.6 | 21 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 19836 | 152 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 7394.3704 | 333.33 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 100-Fossil-Steam
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 388.1666 | 85 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 650-Fluidized Bed
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 578424 | 264 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Summer | 42779.9 | 419 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | WECC | Summer | 472.355 | 25.35 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 1584 | 352 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 357.42 | 103.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 320.6499 | 159 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9423.9663 | 538 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 11.7999 | 177 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 6590.7731 | 611.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 2078.08 | 611.2 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 12.0417 | 42.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 3656.2165 | 259 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 3328.1325 | 172.89 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 204.9999 | 300 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 27.5474 | 330.57 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 74.1999 | 318 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 127.7733 | 103.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 600.0165 | 259 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 850-Combined Cycle Block
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 78.4 | 196 | 1 | 1 | 1799-Other boiler instrumentation and control problems | SF-Startup Failure | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 119.7 | 126 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 53.6666 | 46 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 77.4666 | 83 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 121.9999 | 183 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 1018.7332 | 259 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 102.6 | 102.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 265.9999 | 168 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 509.9999 | 180 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 1145.7 | 342 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 223.2532 | 209.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 1888.875 | 328.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 838.0933 | 210.4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 997.1498 | 231 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3.6666 | 55 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 1311.4999 | 183 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 64.24 | 64.24 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 77.8166 | 161 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 67.2 | 168 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 884.1183 | 201.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 81.9 | 126 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 427.35 | 231 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 851-CC GT units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 350.4 | 72 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 223.39 | 223.39 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 57.475 | 60.5 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 2656.2499 | 375 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 957.5332 | 271 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 101.4799 | 141.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Winter | 1698.1332 | 128 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5.6667 | 20 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 81.705 | 125.7 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 1317.5085 | 20.57 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 21.6667 | 4 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 703.8333 | 41 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 55.6 | 139 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 931.9798 | 285.3 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | HRSG Boiler | HRSG Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 51.6 | 86 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 852-CC steam units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | RFC | Summer | 729.8333 | 145 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | RFC | Winter | 76 | 95 | 1 | 1 | 1799-Other boiler instrumentation and control problems | D1-Forced - Immediate | 860-Co-generator Block
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 1117.0533 | 79.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 1327.9933 | 79.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | SERC | Summer | 3774.4 | 84 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 124.7066 | 79.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 351.5666 | 79.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1799 | Other boiler instrumentation and control problems | Boiler | Boiler Control Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Summer | 4232.0666 | 79.6 | 1 | 1 | 1799-Other boiler instrumentation and control problems | U1-Forced - Immediate | 861-CoG GT units
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26639.5 | 30 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1800 | Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Summer | 21619.4999 | 315 | 1 | 1 | 1800-Major boiler overhaul (720 hours or longer) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 650-Fluidized Bed
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 308.6232 | 420.85 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1566.6666 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1150 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1537.5 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 891.75 | 435 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U1-Forced - Immediate | 100-Fossil-Steam
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 32.2 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 660 | 55 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 117.6833 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 1148.85 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 139.5333 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1274.4 | 27 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 157.8666 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 700 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 8819.65 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1126.6167 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2978.15 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 109.7666 | 37 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 2475.2 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | U2 | Forced - Delayed | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 7479.4883 | 25.9 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | U2-Forced - Delayed | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2199.6333 | 22 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2460.6167 | 23 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 236.6 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 2230.6666 | 28 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 127.05 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 274.4 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 984.1667 | 25 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 4010.65 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 141.1667 | 35 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 461.3 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1007.65 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 473.7166 | 43 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1801 | Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 285.6 | 21 | 1 | 1 | 1801-Minor boiler overhaul (less than 720 hours) (use for non-specific overhaul only; see page B-1) | D1-Forced - Immediate | 800-Miscellaneous
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2438.975 | 7.35 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 124 | 80 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 100-Fossil-Steam
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1480 | 20 | 1 | 1 | 1810-Other boiler inspections | D1-Forced - Immediate | 800-Miscellaneous
1810 | Other boiler inspections | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 1756.9583 | 74.5 | 1 | 1 | 1810-Other boiler inspections | U1-Forced - Immediate | 860-Co-generator Block
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 648.27 | 7.35 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | D1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 13628.5333 | 98 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 257.625 | 22.9 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1811 | Boiler Inspections - problem identification/investigative | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46619.5829 | 635 | 1 | 1 | 1811-Boiler Inspections - problem identification/investigative | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 6970.061 | 63.77 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5749.9383 | 97.1 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6991.2 | 97.1 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 4996.3795 | 63.77 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 15378.0665 | 434 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U2-Forced - Delayed | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 15641.1916 | 97.1 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 1047.9536 | 63.77 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | U1-Forced - Immediate | 100-Fossil-Steam
1812 | Boiler Inspections - scheduled or routine | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 2031.6667 | 20 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 800-Miscellaneous
1812 | Boiler Inspections - scheduled or routine | HRSG Boiler | HRSG Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 233927.05 | 66.5 | 1 | 1 | 1812-Boiler Inspections - scheduled or routine | D1-Forced - Immediate | 850-Combined Cycle Block
1820 | Chemical cleaning/steam blows | Boiler | Boiler Overhaul and Inspections | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 80.1666 | 65 | 1 | 1 | 1820-Chemical cleaning/steam blows | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 89.8999 | 93 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 985.5 | 146 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1081.1999 | 153 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1242 | 207 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1484.8166 | 143 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1647.9165 | 175 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3274.89 | 126.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6126.45 | 237 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 265.2 | 104 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 4979.3333 | 154 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 47.9833 | 1 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 143.55 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 888.8499 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 65.25 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 607.2 | 69 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1134.3332 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 78988.8166 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 50.4998 | 303 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 281.2 | 148 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1206.5 | 254 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1074.5 | 307 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2600.5332 | 212 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3411.8105 | 183.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 707.85 | 143 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1094.1332 | 176 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 6786 | 90 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1134.9999 | 150 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 1390.75 | 15 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 224.4 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 394.0499 | 333 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 882 | 280 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 782.6 | 78 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2243.4666 | 188 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 473.2162 | 275.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1149.8665 | 196 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1603.4999 | 90 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6784.9999 | 276 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 767.2 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3244.7666 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 5866.608 | 333.33 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 137.4998 | 330 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2530 | 220 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7497.975 | 128.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1782.7332 | 242 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 281.25 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 124.9999 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 1560 | 144 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 536 | 268 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 143 | 143 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 167.2665 | 193 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 231.8506 | 133.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1386.5 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 60 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 61.1 | 78 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 189.8666 | 89 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1370.2333 | 202 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 6305 | 325 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2520.35 | 133 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4143.8333 | 115 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 944.6666 | 52 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 142.2666 | 88 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 259.0666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 4416 | 552 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 855.8666 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 267.52 | 133.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 296 | 160 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2564.7 | 103 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2367.75 | 205 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 2689.5999 | 123 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 157.45 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 329 | 141 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 657.7166 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3985.4663 | 568 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 145.75 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 316.54 | 135.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2899.2413 | 117.22 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3705 | 260 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 60.9166 | 43 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3467.6418 | 225.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 6216.6666 | 125 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1075.6832 | 277 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1773.9983 | 105.7 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 236.3092 | 133.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 261.0665 | 178 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3006.4166 | 215 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3017.2498 | 243 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 4336.4 | 148 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 322.6666 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 101.25 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 898.75 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 81.3999 | 132 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4791.6 | 198 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 68.2666 | 128 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2505.75 | 257 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 2672.8 | 104 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 39.1 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 391.95 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 145.1666 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 100.5333 | 26 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 408.0999 | 318 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 858.5999 | 243 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1944 | 243 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6149.1665 | 235 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6155.96 | 183.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11203.6832 | 253 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1968.2 | 78 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 4563.1999 | 192 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 92.7999 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 455.5165 | 181 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19941.85 | 493 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 135004.9997 | 390 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 205.8 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1114.6666 | 176 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 47.6666 | 143 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 353.0999 | 198 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9531.0185 | 183.76 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 948.6 | 93 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3813.3 | 223 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 1902.6999 | 159 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Winter | 6304.1499 | 177 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 115.7333 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 95.7 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 187.5999 | 168 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D2-Forced - Delayed | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 6287.4997 | 375 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Winter | 38016 | 240 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 300.5333 | 98 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 463.2 | 193 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 300.7 | 93 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2115 | 235 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 70 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 552.5333 | 89.6 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 953.7331 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1292 | 152 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3190.9332 | 248 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4304.2176 | 185.66 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1415.7 | 242 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 1538.3333 | 71 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 1519.4 | 142 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 37.5833 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 777.3999 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 74.8 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 108.1666 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 3936 | 164 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | SF-Startup Failure | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 13124.2 | 311 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 124.8 | 208 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 12928.5832 | 167 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 958.7499 | 195 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1570.7 | 226 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1092 | 168 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1150 | 46 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1278.7499 | 225 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 2108.9999 | 180 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 205 | 75 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 108.7999 | 102 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 84 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 851.2075 | 71.43 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 118 | 60 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 6727.7499 | 255 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 303.6 | 276 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1066.8 | 254 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 337.4333 | 53 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 5420.25 | 219 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 233.45 | 87 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 268.8 | 112 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Off-Peak | 283.6333 | 67 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 56.8333 | 55 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 168.0333 | 71 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 197.5999 | 156 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 100-Fossil-Steam
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 7374.0332 | 221 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 650-Fluidized Bed
1850 | Boiler water condition (not feedwater water quality) | Boiler | Boiler Water Condition | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2191.5667 | 22 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 800-Miscellaneous
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 40.3916 | 65.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 386.7732 | 207.2 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 37.4499 | 160.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 30.2416 | 95.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 407.2916 | 195.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | D1-Forced - Immediate | 850-Combined Cycle Block
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 251.35 | 228.5 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 851-CC GT units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 97.9165 | 235 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1850 | Boiler water condition (not feedwater water quality) | HRSG Boiler | HRSG Boiler Water Condition | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 209.6332 | 331 | 1 | 1 | 1850-Boiler water condition (not feedwater water quality) | U1-Forced - Immediate | 852-CC steam units
1900 | Improper balance between tube sections not due to fouling or plugging | HRSG Boiler | HRSG Boiler Design Limitations | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 575.168 | 261.44 | 1 | 1 | 1900-Improper balance between tube sections not due to fouling or plugging | U1-Forced - Immediate | 851-CC GT units
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47.3333 | 40 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 796.25 | 35 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 26 | 4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1311.7267 | 16.4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 108.3333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 240.6667 | 20 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 29.1667 | 5 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 79.8333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 319.8333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1662.8333 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 59.4133 | 44.56 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 4161.5 | 42 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 270 | 60 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 5.6667 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 44.6666 | 40 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2123 | 30 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 14.3333 | 20 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 7179.8333 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1085 | 15 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1305.3333 | 22 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25.2 | 6 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 3959.4667 | 32 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 19.5 | 30 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 159.6667 | 10 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 86453.1 | 27 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 17.4 | 4 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43.75 | 25 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 100-Fossil-Steam
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 22.5 | 90 | 1 | 1 | 1910-Inadequate air not due to equipment problems | D1-Forced - Immediate | 650-Fluidized Bed
1910 | Inadequate air not due to equipment problems | Boiler | Boiler Design Limitations | U1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 19823.9999 | 180 | 1 | 1 | 1910-Inadequate air not due to equipment problems | U1-Forced - Immediate | 650-Fluidized Bed
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24.9999 | 150 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6475.9999 | 240 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 36 | 18 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 8 | 8 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 500 | 100 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 744.8 | 152 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2347.4 | 145.5 | 1 | 1 | 1980-Boiler safety valve test | D1-Forced - Immediate | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140 | 28 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1980 | Boiler safety valve test | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 312 | 78 | 1 | 1 | 1980-Boiler safety valve test | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 110 | 22 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D2-Forced - Delayed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3073.6 | 272 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2635.85 | 119 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2183.6332 | 218 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2807.4666 | 224 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 550.5 | 10 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 397.1333 | 51.8 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 10754.1332 | 128 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 10530.3333 | 70 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 90.96 | 11.37 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D2-Forced - Delayed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2718.7499 | 225 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 192.4999 | 231 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2618.6999 | 261 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2461.25 | 275 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2525.4 | 207 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2294.4 | 192 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 169.2 | 18 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 263.3875 | 55.45 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 323.8998 | 237 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 134.7499 | 231 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 828.2 | 202 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2982.9333 | 238 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 1412.9498 | 231 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 2025.3333 | 98 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2384.8165 | 443 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 9784.8 | 108 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1429.9999 | 120 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2470.9665 | 253 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 2755.5998 | 249 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.6633 | 51.8 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 479.8732 | 127.4 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D1-Forced - Immediate | 100-Fossil-Steam
1990 | Boiler performance testing (use code 9999 for total unit performance testing) | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 3201.7 | 317 | 1 | 1 | 1990-Boiler performance testing (use code 9999 for total unit performance testing) | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2.055 | 6.85 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3535 | 70 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3169.9998 | 600 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1070.6667 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 254.75 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5.01 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 46.8 | 3.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.96 | 0.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5 | 2.5 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.9 | 4.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 4.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.9 | 10.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 38 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.96 | 4.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 50 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 15 | 3.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 10 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 32 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 47.04 | 3.36 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 183.9 | 613 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 367.4666 | 106 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 9312 | 240 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 94.4466 | 91.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 432.0831 | 305 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1110.8333 | 43 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6292.3333 | 43 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 122.6666 | 64 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 188.2165 | 245.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2101.2566 | 337.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 354.85 | 9.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 447.7667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 1140 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 624 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 42.5 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 30 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.9 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.8 | 4.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 3.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.02 | 7.17 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 22.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.5 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 9 | 1 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20.02 | 2.86 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 337.15 | 613 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38808 | 495 | 1 | 1 | 1999-Boiler; miscellaneous | U3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.8533 | 46.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5130 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 428.75 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1092.5 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 529 | 105.8 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 90.25 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 113.625 | 10.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 411.8 | 23.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 200.6083 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 1.8333 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 15 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 43.3333 | 130 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 12 | 4 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 1 | 4 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.9 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 2 | 4 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 3 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 2.2 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.98 | 2.14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 4.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 20 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24 | 4.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.6 | 1.1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 48 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2929.9998 | 600 | 1 | 1 | 1999-Boiler; miscellaneous | D3-Forced - Postponed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 480 | 480 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 669.5166 | 139 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 1846.1165 | 431 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.97 | 13.94 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 215.004 | 16.56 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 374 | 44 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 27.6 | 12 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 384 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 2816.8 | 42 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 292.8 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 95.3333 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 21 | 90 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 6 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.3 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 5.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 7 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49.3 | 2.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10.98 | 1.83 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3954.6666 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 630.75 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Off-Peak | 26.68 | 40.02 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 24.7333 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 58.4767 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 21063 | 68 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 343.7683 | 18.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 615.6333 | 9.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 51.3333 | 110 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 749.1666 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1 | 1 | 5 | 23 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 1.5 | 4 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.01 | 1.67 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 1.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17.01 | 2.43 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 1.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 467.0832 | 475 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3361.75 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 107.0333 | 247 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 2056 | 514 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 29952.3499 | 201 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 712.3 | 10.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 616 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 227.375 | 10.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 396 | 9.6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 40 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 14744 | 57 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8.1 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 19 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27.99 | 9.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 33 | 16.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 38.99 | 5.57 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.99 | 4.33 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18.2 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.97 | 2.71 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7.9166 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 288 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 50.5667 | 8.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 74.4 | 9.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 593.1417 | 10.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 28.5833 | 49 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 8.1943 | 8.06 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14 | 7 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 18 | 3.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.96 | 2.36 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36.96 | 3.36 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 18.25 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 20 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 269.1333 | 44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 38192 | 88 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6770.8333 | 65 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 319.375 | 21.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 529.25 | 21.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1048 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 197.6 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 3 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 3.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.02 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.04 | 2.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2 | 2 | 2 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 767 | 260 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 140.4 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 1228.25 | 51 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1.75 | 0.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5965.5 | 123 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 47114.2665 | 307 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 572.7 | 9.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 536 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 741 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 29960 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 16 | 40 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 24 | 120 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 150 | 150 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 1779.9166 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13.8 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2 | 2 | 6 | 11 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10 | 2.5 | 2 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.04 | 2.16 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 48 | 6 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 49 | 24.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 4.4 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 32803.3329 | 650 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Off-Peak | 835.3667 | 38 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5090.4 | 108 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 17082 | 78 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 122.925 | 9.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 151.125 | 9.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | NPCC | Winter | 1040.9 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 83.1 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Winter | 16.3333 | 70 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 2549.2333 | 31 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11 | 2.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 48.96 | 5.44 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3 | 3 | 4 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 10.8 | 1.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 14.96 | 1.87 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 32 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39 | 3.9 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 40 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 568.1663 | 487 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 15682.5831 | 613 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 276 | 69 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2736.2783 | 120.1 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 1091.8333 | 10 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 237.5 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 495 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 130.4 | 24 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Off-Peak | 44.1 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8.01 | 2.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9 | 4.5 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 17154 | 3.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1 | 1 | 4 | 8 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16.02 | 2.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 27 | 13.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 38.01 | 12.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 677.6667 | 38 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | MRO | Summer | 117.392 | 40.02 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 139.15 | 6.6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 624.1667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 144.375 | 9.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Summer | 1552.5 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 165.5 | 6 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4 | 2 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11.1 | 3.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 17.01 | 5.67 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 40.5999 | 87 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9.1 | 1.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 13 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 22 | 2.2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 23 | 5.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27 | 5.4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 35.01 | 11.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44 | 8.8 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3 | 3 | 3 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 6.99 | 2.33 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 39 | 6.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 43.5 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.25 | 205 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7876.5 | 118 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6.1833 | 5.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 516.6667 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 298.8732 | 141.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 700.3333 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 785.3333 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 89.1417 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 210.975 | 9.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2 | 2 | 2 | 5 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10.8 | 2.7 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11 | 2.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 27.5 | 2.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 28 | 1 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.2 | 5.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 12 | 3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 49.98 | 2.38 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 380 | 475 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 8227.7829 | 587 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 51264 | 712 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2231.2333 | 247 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 337.5665 | 247 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 28.27 | 3.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 157.3 | 242 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 369 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2668.5 | 45 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3862.51 | 140.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 144.57 | 12.2 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 146.025 | 9.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Summer | 923 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 121.125 | 9.5 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Winter | 303.9667 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 1175 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 181.5667 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 421.05 | 7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1 | 1 | 4 | 19 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 8 | 4 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 10 | 2 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 37 | 9.25 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.99 | 1.33 | 1 | 2 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 7.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 16 | 3.2 | 1 | 3 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 24002.3328 | 764 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 545.933 | 431 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Summer | 489.5667 | 38 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 56.8883 | 31.9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 212 | 53 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 21.9733 | 10.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | SERC | Off-Peak | 664.25 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Winter | 2462.5 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 427.5 | 9 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 61.4333 | 38 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 81.6667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 10 | 5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 44.03 | 6.29 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6 | 2 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6.9 | 2.3 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 33 | 6.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 5.01 | 1.67 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 13 | 2.6 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 19 | 4.75 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 1087.75 | 22.9 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 100-Fossil-Steam
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | RFC | Winter | 4196.6666 | 200 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 650-Fluidized Bed
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 222 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 767 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 92.3 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 360 | 24 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 400 | 50 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 28 | 28 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 1286.25 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 51 | 17 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 209.5016 | 37.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 824.0833 | 29 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 425 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 2554.915 | 36.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 96.425 | 20.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 286 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 235 | 47 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 236.6 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 20.5833 | 13 | 1 | 2 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1121 | 59 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 397.5417 | 20.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1400 | 28 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 578.55 | 20.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 66 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 40 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 19.5 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 43.9833 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 110 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 265.6333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 271.9167 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 772.4167 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 18 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 20 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 83.4167 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 375 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1218 | 58 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 42 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 324 | 27 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 275.1667 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 61.75 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 479.72 | 13.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 80.1667 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 283.8333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | WECC | Summer | 454.7667 | 14 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 50 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 452.92 | 13.4 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 460.4167 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 754 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 16.25 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 145.1667 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 168 | 28 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 192 | 32 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 44 | 22 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 91 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1153.35 | 23.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 21 | 21 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 240.5 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 299 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 360 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 861.6833 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 81.25 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 140 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 157.0833 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 18 | 18 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 123 | 41 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 166.8333 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 360 | 30 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 79.3 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 135.8333 | 25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 201.5 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 672.1 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 611 | 13 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 46 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 528.5333 | 16 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 231 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 774.725 | 23.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Off-Peak | 1252 | 24 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Off-Peak | 1586 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 92 | 23 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 604.94 | 20.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Winter | 52 | 26 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Winter | 520.2 | 15.3 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 800-Miscellaneous
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Summer | 2968.978 | 98.04 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 2859.6666 | 92 | 2 | 2 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Oil | DI | 850 | Combined Cycle Block | SERC | Off-Peak | 1808.835 | 112.7 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 379.0879 | 98.04 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 78 | 260 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 322.2397 | 483.36 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1572.7328 | 761 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | SF | Startup Failure | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 539.5999 | 213 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | SF | Startup Failure | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Off-Peak | 88.7499 | 213 | 1 | 1 | 1999-Boiler; miscellaneous | SF-Startup Failure | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 2688.7083 | 86.5 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 850-Combined Cycle Block
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 170.1333 | 58 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 1282.8332 | 179 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 7542.45 | 151 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 1330 | 152 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 7056 | 147 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 85.0666 | 116 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 265.2666 | 92 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 8438.75 | 157 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 31.1665 | 187 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 396.6665 | 175 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 119.3332 | 179 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 19.9499 | 171 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 208.1333 | 223 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 302.9999 | 180 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 273 | 35 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 70.5825 | 156.85 | 1 | 1 | 1999-Boiler; miscellaneous | U2-Forced - Delayed | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 802.9999 | 165 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 851-CC GT units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 16.1666 | 97 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 25.5 | 90 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 587.6666 | 82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 192.6666 | 85 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 504.1332 | 152 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 6443.55 | 129 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 762.106 | 91.82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Winter | 152.932 | 53.04 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 573.125 | 65.5 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 6020 | 112 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Winter | 655.4165 | 325 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 18.3912 | 157.64 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 552.5 | 150 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 3166.5 | 90 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4428 | 20 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5904 | 123 | 1 | 1 | 1999-Boiler; miscellaneous | D2-Forced - Delayed | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 786.6666 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 485.3333 | 80 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 336.6666 | 200 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 617.5664 | 382 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 25.3332 | 152 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 155.2666 | 34 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 403.2 | 27 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 3783.7333 | 56 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 142.6583 | 13.25 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 414 | 90 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 938.9 | 82 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 152.8 | 382 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 207.6375 | 276.85 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 576.8986 | 196.67 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | HRSG Boiler | Miscellaneous (HRSG Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 192.5332 | 152 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 852-CC steam units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 282 | 15 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 861-CoG GT units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 4117.2 | 188 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 861-CoG GT units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 9198.8 | 104 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 861-CoG GT units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 319.6 | 17 | 4 | 4 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 861-CoG GT units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 839.7332 | 188 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 861-CoG GT units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 5218.55 | 59 | 1 | 1 | 1999-Boiler; miscellaneous | D1-Forced - Immediate | 862-CoG steam units
1999 | Boiler; miscellaneous | Boiler | Miscellaneous (Boiler) | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 3312 | 276 | 1 | 1 | 1999-Boiler; miscellaneous | U1-Forced - Immediate | 862-CoG steam units
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 88.596 | 77.04 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 231.695 | 93.3 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 252.5 | 101 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 861.6483 | 120.23 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 526.62 | 175.54 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 40.8047 | 25.24 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 195.3 | 126 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 0.8 | 3.2 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 115.5 | 42 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 56.0667 | 29 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 43.2 | 40.5 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 255.3 | 222 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 3732 | 311 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 53.7333 | 31 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3821.5999 | 204 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 4248.15 | 127 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 5.7815 | 11.19 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 2272.8896 | 255.86 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 837 | 186 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1409.3583 | 159.55 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 51.3333 | 20 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 1938.3333 | 232.6 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 49560.966 | 605.14 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 66 | 30 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 5853.25 | 97.5 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 37.18 | 6.6 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 3245.1999 | 399 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1.98 | 5.4 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 422.9166 | 145 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1.179 | 3.93 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 103.2749 | 182.25 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 42.6067 | 30.8 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2094.1165 | 389 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 51689.4875 | 843.91 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 178 | 89 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 39.0133 | 15.4 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 216 | 216 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 0.48533 | 2.24 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 41.65 | 21 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 117.3233 | 57.7 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1391.1333 | 154 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 798 | 399 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 774.6255 | 156.49 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D1-Forced - Immediate | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 42.1667 | 22 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 65.8333 | 25 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 11.0833 | 5 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D2-Forced - Delayed | 200-Nuclear
2020 | Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | Nuclear Reactor | Core/Fuel | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 572.93 | 28.2 | 1 | 1 | 2020-Control rod pattern changes and control rod repatch. (Preconditioning following a pattern change is to be reported using code 2031.) | D3-Forced - Postponed | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 220.36 | 55.09 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D1-Forced - Immediate | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 642 | 30 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D1-Forced - Immediate | 200-Nuclear
2021 | Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 20532.9666 | 63.8 | 1 | 1 | 2021-Power limited by rod pattern. (If rod pattern is limited by fuel limits; use appropriate code below.) | D1-Forced - Immediate | 200-Nuclear
2062 | Other fuel/core related instrumentation problems | Nuclear Reactor | Core/Fuel | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 102 | 34 | 1 | 1 | 2062-Other fuel/core related instrumentation problems | D1-Forced - Immediate | 200-Nuclear
2062 | Other fuel/core related instrumentation problems | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 177754 | 1240 | 1 | 1 | 2062-Other fuel/core related instrumentation problems | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 58560 | 1220 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 171350.6663 | 1232 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | SF | Startup Failure | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 70188.95 | 1079 | 1 | 1 | 2070-Normal refueling | SF-Startup Failure | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 35241.7996 | 1158 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 417550.6992 | 1218 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2070 | Normal refueling | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 150182.7493 | 1065 | 1 | 1 | 2070-Normal refueling | U1-Forced - Immediate | 200-Nuclear
2071 | Refueling equipment problems | Nuclear Reactor | Core/Fuel | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 268998.7994 | 966 | 1 | 1 | 2071-Refueling equipment problems | U1-Forced - Immediate | 200-Nuclear
2112 | Control rod hydraulic drives | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 81.3833 | 19 | 1 | 1 | 2112-Control rod hydraulic drives | D1-Forced - Immediate | 200-Nuclear
2112 | Control rod hydraulic drives | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 17.5 | 30 | 1 | 1 | 2112-Control rod hydraulic drives | D1-Forced - Immediate | 200-Nuclear
2140 | Control rod drive cooling | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 47.6 | 17 | 1 | 1 | 2140-Control rod drive cooling | D1-Forced - Immediate | 200-Nuclear
2150 | Control rod instrumentation | Nuclear Reactor | Control Rods and Drives | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 37936.1032 | 484.6 | 1 | 1 | 2150-Control rod instrumentation | D2-Forced - Delayed | 200-Nuclear
2151 | Control rod drive controls | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 130 | 8 | 1 | 1 | 2151-Control rod drive controls | D1-Forced - Immediate | 200-Nuclear
2155 | Control rod testing | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 455.62 | 47.96 | 1 | 1 | 2155-Control rod testing | D1-Forced - Immediate | 200-Nuclear
2160 | Other control rod drive problems | Nuclear Reactor | Control Rods and Drives | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 55.44 | 29.7 | 1 | 1 | 2160-Other control rod drive problems | D1-Forced - Immediate | 200-Nuclear
2160 | Other control rod drive problems | Nuclear Reactor | Control Rods and Drives | U3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 92334.9331 | 646 | 1 | 1 | 2160-Other control rod drive problems | U3-Forced - Postponed | 200-Nuclear
2199 | Other reactor vessel problems | Nuclear Reactor | Reactor Vessel and Internals | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 1.0002 | 0.01 | 1 | 1 | 2199-Other reactor vessel problems | D3-Forced - Postponed | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1503.2705 | 43.51 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 13065.02 | 82.69 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 47728.5504 | 639.65 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 129834.6663 | 1088 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 19844.0751 | 127.93 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 476.2085 | 484.28 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 15464.9925 | 314.01 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 724.7247 | 12.28 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 1054.725 | 12.3 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 102496.6662 | 1268 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | U1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 36109.9998 | 690 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 329.8702 | 181.58 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 361.9333 | 178 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 327120 | 752 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 5226.87 | 37.07 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 65664.4098 | 693.15 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 5474.5833 | 175 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 15939.994 | 43.54 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 3972.808 | 81.41 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | D1-Forced - Immediate | 200-Nuclear
2200 | Reactor coolant/recirculating pumps | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 50445.4993 | 1065 | 1 | 1 | 2200-Reactor coolant/recirculating pumps | U1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 424200 | 707 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 198874.25 | 485 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | D1-Forced - Immediate | 200-Nuclear
2210 | Reactor coolant/recirculating pump motors | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 42953.3331 | 850 | 1 | 1 | 2210-Reactor coolant/recirculating pump motors | U1-Forced - Immediate | 200-Nuclear
2220 | Reactor coolant/recirculating pump MG sets | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 168.9499 | 93 | 1 | 1 | 2220-Reactor coolant/recirculating pump MG sets | D1-Forced - Immediate | 200-Nuclear
2220 | Reactor coolant/recirculating pump MG sets | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 133.3333 | 50 | 1 | 1 | 2220-Reactor coolant/recirculating pump MG sets | D1-Forced - Immediate | 200-Nuclear
2265 | Pressurizer (also see codes 2290; 2330; and 2340) | Nuclear Reactor | Reactor Coolant System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 5397.5998 | 468 | 1 | 1 | 2265-Pressurizer (also see codes 2290; 2330; and 2340) | D3-Forced - Postponed | 200-Nuclear
2265 | Pressurizer (also see codes 2290; 2330; and 2340) | Nuclear Reactor | Reactor Coolant System | U3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 124200 | 1150 | 1 | 1 | 2265-Pressurizer (also see codes 2290; 2330; and 2340) | U3-Forced - Postponed | 200-Nuclear
2265 | Pressurizer (also see codes 2290; 2330; and 2340) | Nuclear Reactor | Reactor Coolant System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 91241.8832 | 517 | 1 | 1 | 2265-Pressurizer (also see codes 2290; 2330; and 2340) | D3-Forced - Postponed | 200-Nuclear
2270 | Power operated relief and safety/relief valves | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 9609.906 | 696.37 | 1 | 1 | 2270-Power operated relief and safety/relief valves | D1-Forced - Immediate | 200-Nuclear
2270 | Power operated relief and safety/relief valves | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 870.7284 | 768.29 | 1 | 1 | 2270-Power operated relief and safety/relief valves | D1-Forced - Immediate | 200-Nuclear
2270 | Power operated relief and safety/relief valves | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 93883 | 842 | 1 | 1 | 2270-Power operated relief and safety/relief valves | U1-Forced - Immediate | 200-Nuclear
2270 | Power operated relief and safety/relief valves | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 16513.1632 | 222.95 | 1 | 1 | 2270-Power operated relief and safety/relief valves | D1-Forced - Immediate | 200-Nuclear
2320 | Other reactor coolant valves (including RCS boundary valves in connected systems) | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 8165.6992 | 718.39 | 1 | 1 | 2320-Other reactor coolant valves (including RCS boundary valves in connected systems) | D1-Forced - Immediate | 200-Nuclear
2320 | Other reactor coolant valves (including RCS boundary valves in connected systems) | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 18405.4439 | 407.05 | 1 | 1 | 2320-Other reactor coolant valves (including RCS boundary valves in connected systems) | D2-Forced - Delayed | 200-Nuclear
2370 | Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 42782.2995 | 759 | 1 | 1 | 2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | U1-Forced - Immediate | 200-Nuclear
2370 | Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 6202.2452 | 409.84 | 1 | 1 | 2370-Reactor trip system including sensors; logic; and actuators (includes spurious trips but not valid trips) | D1-Forced - Immediate | 200-Nuclear
2380 | Reactor control system/integrated control system problems | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 44900.55 | 883 | 1 | 1 | 2380-Reactor control system/integrated control system problems | U1-Forced - Immediate | 200-Nuclear
2380 | Reactor control system/integrated control system problems | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 12790.8999 | 222 | 1 | 1 | 2380-Reactor control system/integrated control system problems | D1-Forced - Immediate | 200-Nuclear
2390 | Other reactor coolant system instruments and controls | Nuclear Reactor | Reactor Coolant System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 128967.9992 | 1176 | 1 | 1 | 2390-Other reactor coolant system instruments and controls | U1-Forced - Immediate | 200-Nuclear
2390 | Other reactor coolant system instruments and controls | Nuclear Reactor | Reactor Coolant System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 8056.8999 | 186 | 1 | 1 | 2390-Other reactor coolant system instruments and controls | D1-Forced - Immediate | 200-Nuclear
2399 | Other miscellaneous reactor coolant system problems | Nuclear Reactor | Reactor Coolant System | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 36890.3 | 141 | 1 | 1 | 2399-Other miscellaneous reactor coolant system problems | D2-Forced - Delayed | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 12461.3599 | 127.2 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | U2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 186658.5 | 1218 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | U2-Forced - Delayed | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3.66 | 1.2 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 351.505 | 17.43 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 350.5493 | 16.64 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 2662.7075 | 16.53 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 59.4667 | 16 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2440 | Steam generator chemistry (excluding feedwater chemistry) | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 190.76 | 5.7 | 1 | 1 | 2440-Steam generator chemistry (excluding feedwater chemistry) | D1-Forced - Immediate | 200-Nuclear
2480 | Other blowdown | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | TRE | Off-Peak | 4.5002 | 8.71 | 1 | 1 | 2480-Other blowdown | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 16.62 | 3.6 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 4449.6 | 6.18 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 2235.6393 | 7.94 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 3132.24 | 4.21 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 13111.46 | 93.32 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 5490.72 | 7.38 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 4125.6 | 5.73 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2540 | Other steam valves | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 4270.56 | 5.74 | 1 | 1 | 2540-Other steam valves | D1-Forced - Immediate | 200-Nuclear
2599 | Other steam generator problems | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 9723.3565 | 452.6 | 1 | 1 | 2599-Other steam generator problems | D1-Forced - Immediate | 200-Nuclear
2599 | Other steam generator problems | Nuclear Reactor | Steam Generators and Steam System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 36638.0163 | 1121 | 1 | 1 | 2599-Other steam generator problems | U1-Forced - Immediate | 200-Nuclear
2599 | Other steam generator problems | Nuclear Reactor | Steam Generators and Steam System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 157.762 | 12.12 | 1 | 1 | 2599-Other steam generator problems | D1-Forced - Immediate | 200-Nuclear
2600 | High pressure safety injection; core injection; or core spray pumps (including RCIC) | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 17.8333 | 10 | 1 | 1 | 2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | D1-Forced - Immediate | 200-Nuclear
2600 | High pressure safety injection; core injection; or core spray pumps (including RCIC) | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 6.8333 | 10 | 1 | 1 | 2600-High pressure safety injection; core injection; or core spray pumps (including RCIC) | D1-Forced - Immediate | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 7.0833 | 1 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 28.1333 | 4 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 14400 | 20 | 1 | 1 | 2604-High pressure valves | D1-Forced - Immediate | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 103.1333 | 17 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 17112 | 23 | 1 | 1 | 2604-High pressure valves | D1-Forced - Immediate | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 174.8 | 12 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 72.2667 | 8 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2604 | High pressure valves | Nuclear Reactor | Core Cooling/Safety Injection | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 53.5167 | 19 | 1 | 1 | 2604-High pressure valves | D2-Forced - Delayed | 200-Nuclear
2649 | Other emergency core cooling/residual heat removal system problems | Nuclear Reactor | Core Cooling/Safety Injection | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | MRO | Off-Peak | 5007.7475 | 213.55 | 1 | 1 | 2649-Other emergency core cooling/residual heat removal system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 950.7958 | 291.06 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1748.5795 | 339.53 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 5887.056 | 1051.26 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 639.1699 | 119.1 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 13321.7326 | 1172 | 1 | 1 | 2799-Other containment system problems | U1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 2045.725 | 818.29 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1009.764 | 560.98 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 293.2366 | 131.3 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 436.059 | 969.02 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 154782.1326 | 1172 | 1 | 1 | 2799-Other containment system problems | U1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1710.114 | 600.04 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2799 | Other containment system problems | Nuclear Reactor | Containment System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 4662.1744 | 813.17 | 1 | 1 | 2799-Other containment system problems | D1-Forced - Immediate | 200-Nuclear
2816 | Valves and piping | Nuclear Reactor | Chemical and Volume Control/Reactor Water Cle | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 15321.7997 | 498 | 1 | 1 | 2816-Valves and piping | D1-Forced - Immediate | 200-Nuclear
2816 | Valves and piping | Nuclear Reactor | Chemical and Volume Control/Reactor Water Cle | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 41048.4 | 948 | 1 | 1 | 2816-Valves and piping | U1-Forced - Immediate | 200-Nuclear
2817 | Instruments and controls | Nuclear Reactor | Chemical and Volume Control/Reactor Water Cle | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 318.6667 | 16 | 1 | 1 | 2817-Instruments and controls | D1-Forced - Immediate | 200-Nuclear
2819 | Other CVCS and RWC problems | Nuclear Reactor | Chemical and Volume Control/Reactor Water Cle | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 329.2878 | 52.13 | 1 | 1 | 2819-Other CVCS and RWC problems | D1-Forced - Immediate | 200-Nuclear
2820 | Nuclear closed cooling water pumps | Nuclear Reactor | Nuclear Cooling Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 7517.1766 | 69.4 | 1 | 1 | 2820-Nuclear closed cooling water pumps | D1-Forced - Immediate | 200-Nuclear
2842 | Auxiliary feedwater pump steam turbines (including steam control valves) | Nuclear Reactor | Auxiliary Systems | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 55.9167 | 11 | 1 | 1 | 2842-Auxiliary feedwater pump steam turbines (including steam control valves) | D2-Forced - Delayed | 200-Nuclear
2844 | Auxiliary feedwater valves | Nuclear Reactor | Auxiliary Systems | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 46577.96 | 124.54 | 1 | 1 | 2844-Auxiliary feedwater valves | D3-Forced - Postponed | 200-Nuclear
2849 | Other auxiliary feedwater problems | Nuclear Reactor | Auxiliary Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 6102.7431 | 806.53 | 1 | 1 | 2849-Other auxiliary feedwater problems | D1-Forced - Immediate | 200-Nuclear
2890 | Condenser off-gas system problems | Nuclear Reactor | Auxiliary Systems | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 7994.7399 | 378.3 | 1 | 1 | 2890-Condenser off-gas system problems | D3-Forced - Postponed | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 27592.5 | 325 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 3973.1665 | 310 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1421.2383 | 84.43 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 191676.2666 | 212 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 695.25 | 135 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 136.6667 | 41 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 8688.75 | 175 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 15864 | 480 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 461643 | 741 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 3894.3665 | 247 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2548.5832 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10842.75 | 237 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 3140.25 | 237 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 194.6666 | 160 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 20187.45 | 339 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 10462.0833 | 85 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 28470.6662 | 655 | 1 | 1 | 3110-Condenser tube leaks | SF-Startup Failure | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12463.5666 | 158 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 809.55 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2163.0832 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 2312.0997 | 378 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 5734.9999 | 222 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 10404.2166 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 11523 | 115 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1183.2 | 58 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 68223.6331 | 658 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 9250 | 156.25 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 10947.9998 | 240 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4691.3332 | 155 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1165.7667 | 41 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 707 | 105 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 461.1 | 106 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 7095 | 300 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1172.5 | 175 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 9989 | 105 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16127.0832 | 125 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 133.3333 | 160 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3405.25 | 257 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 8326.5 | 390 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 10239.9998 | 480 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5170.5333 | 247 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2304.4332 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 2874.1166 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4454.6666 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27603.3332 | 325 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 105.9167 | 41 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 184.5 | 41 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5158.5 | 285 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 41944 | 535 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 602.25 | 165 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 25052.1664 | 415 | 1 | 1 | 3110-Condenser tube leaks | SF-Startup Failure | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 7445.5833 | 235 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 82988.3332 | 505 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 112529.7495 | 705 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 658.6666 | 40 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1952.1666 | 85 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 6075.3333 | 104 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 59771.833 | 455 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2237.15 | 101 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 25910.9 | 113 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 57.6 | 108 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1620.1 | 102 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1212.6 | 47 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 4167.5666 | 106 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 10497.5 | 247 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 3576.5832 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 6048.0666 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 656.3667 | 29 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2261 | 323 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9287 | 370 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 3341 | 257 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6425 | 257 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 5083.7499 | 105 | 1 | 1 | 3110-Condenser tube leaks | SF-Startup Failure | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 2439.15 | 101 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 144.565 | 234.43 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 409.2 | 66 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 3895.0666 | 111.5 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5444.9999 | 297 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 10062.5 | 250 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 8440.32 | 537.6 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 19008 | 528 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 1434.8798 | 566.4 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 75449.85 | 397 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 3932.1 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 3760 | 200 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 412.5332 | 272 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8697.6331 | 622 | 1 | 1 | 3110-Condenser tube leaks | SF-Startup Failure | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 7695.9999 | 390 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1773.3 | 257 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2667.6 | 114 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 660 | 220 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 10954.1665 | 250 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 80 | 96 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 11215.9997 | 480 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 107509.6664 | 740 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 438000 | 50 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Summer | 720 | 200 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 368.8532 | 166.4 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 975 | 650 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 54408.7164 | 361 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 100-Fossil-Steam
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 4141.27 | 88.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 22424.5449 | 861.93 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 1334.8 | 47 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 20747.5678 | 860.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 24596.7 | 163 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 99194.0331 | 362 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 1399.3392 | 485.32 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 6258.5532 | 247.7 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1.46 | 14.6 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 1033.9 | 42 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 12865.6 | 187 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | TRE | Off-Peak | 11477.55 | 225.05 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1750.4667 | 30.8 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 919.2968 | 606.13 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 53.5267 | 14.8 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Winter | 221 | 17 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 23513.6 | 176 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 33473.3929 | 719.6 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 842.775 | 15.3 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 7.575 | 90.9 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 4268.2979 | 168.93 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 200-Nuclear
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Gas | GG | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 23729.1 | 138 | 1 | 1 | 3110-Condenser tube leaks | U3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | RFC | Off-Peak | 30929.1831 | 419 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 810-Multi-boiler/Multi-turbine
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2859.5 | 47.5 | 1 | 1 | 3110-Condenser tube leaks | D3-Forced - Postponed | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 9775.5 | 190 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 515.45 | 61 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4015.8333 | 61 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Summer | 14178.2179 | 98.04 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 6496 | 280 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2981.8833 | 61 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 1595.7333 | 187 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 850-Combined Cycle Block
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 3043.1665 | 190 | 2 | 2 | 3110-Condenser tube leaks | U1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 19727.7666 | 173 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 1314.5833 | 25 | 2 | 2 | 3110-Condenser tube leaks | D1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 13897.945 | 191.3 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 14188.545 | 195.3 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 37420 | 200 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 2140.6666 | 169 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 18552.1166 | 163 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 16.0167 | 1 | 2 | 2 | 3110-Condenser tube leaks | D1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 517.4333 | 86 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 857.85 | 21 | 2 | 2 | 3110-Condenser tube leaks | D1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 2126.5833 | 169 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 851-CC GT units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 3513.1 | 86 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 17.2333 | 94 | 1 | 1 | 3110-Condenser tube leaks | D2-Forced - Delayed | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 3039.9998 | 240 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 3715.8665 | 232 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 13471.2 | 72 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 19809.9 | 174 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 4732.5 | 90 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 40679.1 | 462 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 13012.4999 | 225 | 1 | 1 | 3110-Condenser tube leaks | D1-Forced - Immediate | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 15619.75 | 215 | 1 | 1 | 3110-Condenser tube leaks | U2-Forced - Delayed | 852-CC steam units
3110 | Condenser tube leaks | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 2605.1666 | 145 | 1 | 1 | 3110-Condenser tube leaks | U1-Forced - Immediate | 852-CC steam units
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 78107 | 37 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2320 | 20 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1348.2667 | 16 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 54491.4833 | 29 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 100-Fossil-Steam
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 2520 | 10 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 200-Nuclear
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3720 | 5 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 200-Nuclear
3111 | Condenser tube fouling shell side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0 | 0 | 1 | 1 | 3111-Condenser tube fouling shell side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15 | 3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.475 | 117.9 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 296.0833 | 64.6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 305.8666 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 357.3666 | 71 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.6667 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 792 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2252.0167 | 7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 43010 | 110 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 253.5748 | 28.87 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 116.6667 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 350 | 35 | 1 | 2 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 40 | 48 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 44.65 | 57 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 71 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 101.6666 | 100 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 187.5 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 6.05 | 33 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 249.2 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 117 | 3 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 160.8 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 302.25 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2466.2667 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5040 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 2044.9252 | 264.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 63.9667 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 23.4333 | 37 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.75 | 85 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135 | 90 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.8 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 310.1167 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.5166 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1992.4666 | 121 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6136.665 | 64.71 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1592.3966 | 301.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1655.9978 | 314.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 182.5 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 82.8 | 69 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 351.648 | 11.84 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 104.3666 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 192 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 195.4167 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 273.8333 | 31 | 1 | 2 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1831.38 | 117.9 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4304 | 40 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8620.2122 | 253.66 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25285.77 | 41.85 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 183.6368 | 234.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 11.6667 | 7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 600 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 57.236 | 9.84 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 58 | 58 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 28.9333 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.8 | 66 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.65 | 57 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 113.8666 | 61 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 58 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 704.2666 | 76 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 30.3999 | 114 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 71.4 | 63 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 183 | 61 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 277.8 | 36 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 290 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9122.6666 | 160 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 204.0023 | 9.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 114.75 | 85 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 170 | 34 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 78 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 179.6 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 77 | 66 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 209 | 19 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11.2 | 112 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 47 | 9.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 109.0166 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.9167 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 234.75 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 248.5 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 333.5 | 29 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 342 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 445.315 | 120.9 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 595.8 | 36 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 630 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1232.0333 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 183.1667 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 280 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 192375 | 125 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 58.75 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 66.5 | 70 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 113.2 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9.2 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.0833 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 128.7 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 286.1667 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 851.6667 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13558.4 | 96 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 46.24 | 20.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 77.55 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 300.2999 | 198 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 268.1162 | 176.78 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 45 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 63.25 | 69 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 87.0833 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 140.8 | 88 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 202 | 101 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1756.0667 | 4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 39.7833 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 42.5 | 17 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 53 | 10.6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 91 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 100.1 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 226.8166 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 267.9 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 277.3833 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 433.5833 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 622.05 | 13 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 873.052 | 256.78 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 42.75 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 65 | 78 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 75 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 174.5333 | 88 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 28857.5 | 105 | 1 | 1 | 3112-Condenser tube fouling tube side | U1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5720 | 325 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 23.2333 | 41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39 | 13 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 42 | 7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 480 | 4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 728.8666 | 116 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1865.3 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 144.3567 | 25.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 665.5 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 30600 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 33.4665 | 200.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 52.25 | 55 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 70 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 72 | 67.5 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 83.7499 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 123.6 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4.0333 | 121 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 72.2 | 114 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.0833 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 167.3 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 292.25 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 804.95 | 17 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1008 | 28.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1685.5667 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5136.9333 | 118 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 65.49 | 35.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 0 | 0 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 226.1667 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8253.168 | 21.78 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1206 | 160.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1436.7362 | 264.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 56.05 | 57 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 81.3333 | 80 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 135.4666 | 64 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 29.3333 | 110 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 33.6667 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 48.7666 | 133 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 84.2166 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 240 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1378.6667 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 57.95 | 57 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 155.1666 | 95 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 87.75 | 27 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 147.5 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.79997 | 48 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 189.4667 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 216 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 381 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 382.6167 | 11 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 547.5 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 765 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 773.3333 | 50 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1643.7333 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6607.6667 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1496.8933 | 171.4 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 9450 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 12538.383 | 21.78 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7.2 | 27 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 60.45 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 80.9833 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 99.9 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 156 | 30 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 233.7 | 41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 249.1667 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1230.3 | 9 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2427.75 | 27 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4378 | 110 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 115.0166 | 67 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3915 | 145 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 72.01 | 75.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 80.4 | 160.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 67 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 86 | 60 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 129.3333 | 80 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 956.3667 | 13 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1630 | 15 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3.9 | 117 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 12.5666 | 58 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 202.5167 | 29 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 301.0667 | 16 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 341.25 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374 | 44 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 440 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 506.4 | 24 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3292.4325 | 60.69 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4431 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 39.9597 | 184.43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 180.8333 | 35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 7560 | 105 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 111.25 | 75 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1297.2 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 0.41665 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 9 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.5 | 15 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 328.25 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1797.5 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3086.7465 | 28.41 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 5582.1 | 18 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 841.5 | 153 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 100-Fossil-Steam
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0.65 | 0.65 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Winter | 410 | 2 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 0 | 0 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 46.3 | 4.63 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 23 | 1 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 14.89 | 14.89 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 50.8 | 6.35 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 200-Nuclear
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 10.8 | 3.6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 650-Fluidized Bed
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 16 | 3.2 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 650-Fluidized Bed
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Off-Peak | 129511.0999 | 213 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 1092 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 3331.6667 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 62.96 | 4.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 557.75 | 13.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 568.255 | 8.7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 10.935 | 2.7 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 127.9533 | 6.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 24.4 | 4.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1288.8 | 10.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 223.2033 | 5.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 34.0267 | 8.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 955.6633 | 9.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 929.44 | 14.8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 850-Combined Cycle Block
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 180.6333 | 1 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 851-CC GT units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 2578.8 | 63 | 1 | 1 | 3112-Condenser tube fouling tube side | U1-Forced - Immediate | 851-CC GT units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 22.5 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 851-CC GT units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 6135.8 | 22 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 851-CC GT units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 926.6667 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 851-CC GT units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 16.5 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1674.4 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2739.1 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 4.3333 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 6.45 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 29.1667 | 25 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 92.5 | 6 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2582.1333 | 23 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 0.69997 | 42 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 698 | 20 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 91.8667 | 8 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1529.6667 | 10 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2549.15 | 51 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 4601.7166 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 7714.4 | 48 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 229.25 | 15 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 28.9333 | 31 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 4384.5666 | 46 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 4451.1166 | 53 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3957.0667 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 6903.45 | 29 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 4.3333 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 29.75 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1596.4 | 39 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 13.9167 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 5082.5 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 157.25 | 15 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 3827 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 266 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D3-Forced - Postponed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 0.75 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 1051.3333 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 2476.0833 | 43 | 1 | 1 | 3112-Condenser tube fouling tube side | D2-Forced - Delayed | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 355.5 | 45 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 926 | 5 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3112 | Condenser tube fouling tube side | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 1103.2667 | 38 | 1 | 1 | 3112-Condenser tube fouling tube side | D1-Forced - Immediate | 852-CC steam units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1434.5 | 377.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2996.2664 | 424 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 140.7 | 67 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3334.9999 | 348 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2898 | 414 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1272.6 | 404 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 736.5998 | 348 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 1950 | 650 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 80737.3 | 147 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 188.32 | 235.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D2-Forced - Delayed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 165.6666 | 142 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3132 | 783 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2685.3332 | 424 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2989 | 427 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 222.8333 | 35 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 233.5667 | 15.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1740 | 348 | 1 | 2 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 35211 | 330 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3436.2 | 414 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1734.1999 | 348 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 146.25 | 25 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 219.71 | 25.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 278.5 | 30 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 461.5 | 142 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 470.8 | 235.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2396.2166 | 329 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 5286.4331 | 323 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 7434.1332 | 424 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 3200 | 400 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 404.1032 | 235.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 1717 | 404 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 143.2933 | 195.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 14984.6665 | 494 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2253.5997 | 432 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 261.8333 | 10 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2387.3997 | 414 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 544.8 | 72 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4524 | 348 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1548.3 | 397 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 7.1867 | 15.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6045.1666 | 230 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 21.59 | 25.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 341.33 | 235.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 496.85 | 523 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1680.6332 | 254 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 100-Fossil-Steam
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 1.36 | 13.6 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 3.12 | 15.6 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 11.4767 | 2.2 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 22.3 | 6 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 93.61 | 25.3 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 1006.95 | 147 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 12.12 | 2.4 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 1786.9 | 214 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 166.83 | 8.3 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 6.625 | 26.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 23148 | 643 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 204.5333 | 26 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 1053.4999 | 147 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 121.125 | 32.3 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 125.84 | 24.2 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 31734.3998 | 633 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 4.02 | 0.9 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 5.15 | 1.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 282.1867 | 40.7 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 688.45 | 147 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 200-Nuclear
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Other | WD | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 0 | 0 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D3-Forced - Postponed | 810-Multi-boiler/Multi-turbine
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 274.95 | 211.5 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 463.15 | 157 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U1-Forced - Immediate | 850-Combined Cycle Block
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 920.22 | 187.8 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | U2-Forced - Delayed | 851-CC GT units
3113 | Condenser tube and water box cleaning (including circulating water flow reversal) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 5893.3332 | 260 | 1 | 1 | 3113-Condenser tube and water box cleaning (including circulating water flow reversal) | D1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | WECC | Winter | 907.2895 | 37.83 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 650-Fluidized Bed
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 83622.5 | 65 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 13513.6664 | 355 | 1 | 1 | 3114-Air-cooled condenser tubes | U1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1728.6 | 36 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 13144.0833 | 55 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 124.25 | 355 | 1 | 1 | 3114-Air-cooled condenser tubes | U1-Forced - Immediate | 852-CC steam units
3114 | Air-cooled condenser tubes | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 6475.4999 | 270 | 1 | 1 | 3114-Air-cooled condenser tubes | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 2795.9 | 766 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 100-Fossil-Steam
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 12.6667 | 9.5 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 31.5333 | 172 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2.6667 | 8 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3.6 | 9 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 2213.71 | 598.3 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2.3333 | 7 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4.3333 | 10 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 850-Combined Cycle Block
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.55 | 1 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 29.9666 | 62 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 9 | 36 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 11.9 | 7 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.8167 | 23 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 51 | 30 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.1667 | 10 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 18.0167 | 23 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 22.2333 | 46 | 3 | 3 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 8.3333 | 50 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 10.75 | 43 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.8333 | 10 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 125.3333 | 16 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 15.5 | 10 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 47.5 | 95 | 3 | 3 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 117.46 | 167.8 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 142.63 | 167.8 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 851-CC GT units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 60.2 | 86 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0 | 0 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 9.4 | 12 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.75 | 19 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 74.5333 | 86 | 1 | 1 | 3116-Air-cooled condenser fans | U1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.6 | 12 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 11.6 | 24 | 3 | 3 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 830.9166 | 65 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 25 | 50 | 3 | 3 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7.75 | 5 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.1 | 3 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.5833 | 5 | 2 | 2 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 25.5 | 15 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 54.8333 | 7 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 19428.3 | 54 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 11.4667 | 16 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 385 | 55 | 1 | 3 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 37.2667 | 13 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1495 | 65 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.9167 | 5 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.5 | 22 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3116 | Air-cooled condenser fans | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 15.95 | 33 | 1 | 1 | 3116-Air-cooled condenser fans | D1-Forced - Immediate | 852-CC steam units
3117 | Air-cooled condenser fan motors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 8 | 1 | 1 | 1 | 3117-Air-cooled condenser fan motors | D1-Forced - Immediate | 830-Geothermal
3117 | Air-cooled condenser fan motors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 10 | 2 | 1 | 1 | 3117-Air-cooled condenser fan motors | D1-Forced - Immediate | 830-Geothermal
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 82.8 | 41.4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 100-Fossil-Steam
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 41.25 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 100-Fossil-Steam
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8.2333 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 2.8 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 5.6333 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1764 | 140 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 2494 | 40 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 32.6666 | 140 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 1481.6666 | 140 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3.2 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3.9 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 7 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 17.4 | 174 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Winter | 95.6666 | 140 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 828.3332 | 140 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 850-Combined Cycle Block
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 0.9 | 6 | 3 | 3 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.5 | 10 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 5.8 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 11 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 18.1333 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 26.9167 | 19 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.6667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 10.35 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 13 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16 | 40 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 110 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 625 | 100 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 35.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.7667 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.1167 | 11 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.7167 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.5167 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 15.6 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16.5 | 30 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 28.8 | 27 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.9667 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.3333 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.4 | 33 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.7667 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.6 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 9 | 27 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 29.9 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 42.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 106.4 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 452.2 | 42 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.8333 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.1667 | 14 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 12 | 36 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 66.6 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 42.5 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 148.1333 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.8333 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 5.95 | 17 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 46.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 0 | 0 | 3 | 4 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.3333 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.6333 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.5 | 10 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 10.75 | 43 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 22.1 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.1333 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.3333 | 10 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.8667 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 5.5167 | 1 | 3 | 3 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 15.6 | 12 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 20.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 27.5 | 33 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 55.2 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.9167 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.5333 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.4833 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.3 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.0667 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.05 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 25.1667 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 31.8167 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 67.25 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 417.95 | 39 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 2.5667 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 25.8 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 49.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 55.7667 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 1.2667 | 4 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 7.3333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.5 | 17 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 8.5333 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 12.65 | 33 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16.2 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 4306.6666 | 200 | 1 | 1 | 3118-Other Air-cooled condenser problems | U2-Forced - Delayed | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 72.6 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.6667 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 12.9 | 43 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 29.6 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3.6833 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.3333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 9.6 | 36 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 13.3333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 17 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 38.3333 | 46 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 41.0167 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 41.4 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 50.3333 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 66 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 20 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 31.7333 | 14 | 3 | 3 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 530.9332 | 176 | 1 | 1 | 3118-Other Air-cooled condenser problems | U3-Forced - Postponed | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 250.3167 | 23 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 0.73333 | 4 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 4.6 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 6.3333 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 7.2333 | 14 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 11.9 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 16.6666 | 40 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 22.7333 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 57.1667 | 14 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 851-CC GT units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 450 | 45 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0.66666 | 5 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 21.0833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 180 | 45 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 337.5 | 50 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 495 | 45 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 1265 | 55 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 8 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 9.4333 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 16.6 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 20 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 270 | 45 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0.86667 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.8333 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.6667 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.9333 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6.5 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 14.8 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 21.6 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 45.6 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 294 | 49 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.1667 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.1 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6.3333 | 19 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 12.5833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 13.8667 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1550.4 | 72 | 1 | 1 | 3118-Other Air-cooled condenser problems | U1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 210 | 42 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.65 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7 | 21 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 10.6333 | 11 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 28.8 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 55 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.0833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.3833 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7.8 | 6 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.1333 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.1 | 6 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.15 | 7 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6 | 18 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 8.3333 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 45.2833 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0 | 0 | 3 | 14 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.75 | 5 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.4 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.5 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 13.6167 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 14.1667 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Summer | 110.6666 | 40 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 225 | 45 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.6 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.5 | 6 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4 | 8 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 8.25 | 15 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 8.5333 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 10.3333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 15.1 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 15.6 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 22.2 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.2 | 9 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.3333 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.7333 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.25 | 5 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.2 | 3 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 8 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 9.2 | 24 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 301.6666 | 100 | 1 | 1 | 3118-Other Air-cooled condenser problems | D3-Forced - Postponed | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 420 | 60 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.8 | 8 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.5333 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.4 | 2 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6.6 | 22 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 6.6667 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 10 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Summer | 105.1333 | 38 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3.6667 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.0667 | 19 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 12.75 | 9 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 13.4333 | 13 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 13.6 | 6 | 3 | 3 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 21.4 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 58.6667 | 16 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2.2667 | 17 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 5.5 | 22 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 24.8333 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 21551.25 | 75 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0.8 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 2 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 23.0833 | 5 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 455 | 65 | 1 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 0.31667 | 1 | 2 | 2 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 1.1 | 6 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.0833 | 1 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 4.6 | 12 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 7.6667 | 20 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 10.4 | 8 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3118 | Other Air-cooled condenser problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 33 | 10 | 1 | 1 | 3118-Other Air-cooled condenser problems | D1-Forced - Immediate | 852-CC steam units
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 1352.8167 | 47 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1092 | 78 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.02 | 5.43 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 374.17 | 5.27 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 197.03 | 10.37 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 858480 | 98 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Off-Peak | 4390.05 | 259 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 286.1667 | 17 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2756.4717 | 32.9 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73.95 | 4.93 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3119 | Other condenser tube casing or shell and internal problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 246.74 | 3.38 | 1 | 1 | 3119-Other condenser tube casing or shell and internal problems | D2-Forced - Delayed | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 19697.9999 | 180 | 1 | 1 | 3120-Tube sheets | D1-Forced - Immediate | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 11569.0663 | 493 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 156 | 18 | 1 | 1 | 3120-Tube sheets | D1-Forced - Immediate | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 23069.1 | 393 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 100-Fossil-Steam
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 13543.2 | 228 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 851-CC GT units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 13602.6 | 229 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 851-CC GT units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 4376.3333 | 190 | 2 | 2 | 3120-Tube sheets | U1-Forced - Immediate | 851-CC GT units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 8166.6665 | 196 | 2 | 2 | 3120-Tube sheets | U1-Forced - Immediate | 851-CC GT units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5435.8666 | 236 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 852-CC steam units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 9874.9998 | 237 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 852-CC steam units
3120 | Tube sheets | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 13988.7 | 235.5 | 1 | 1 | 3120-Tube sheets | U1-Forced - Immediate | 852-CC steam units
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 81544.9998 | 282 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 23625 | 525 | 1 | 1 | 3121-Expansion joint | D1-Forced - Immediate | 100-Fossil-Steam
3121 | Expansion joint | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | SERC | Off-Peak | 24480 | 102 | 1 | 1 | 3121-Expansion joint | U1-Forced - Immediate | 650-Fluidized Bed
3122 | Gaskets and seals | Balance of Plant | Condensing System | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4747.05 | 99 | 1 | 1 | 3122-Gaskets and seals | U3-Forced - Postponed | 100-Fossil-Steam
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 39353.6 | 416 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 100-Fossil-Steam
3122 | Gaskets and seals | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | MRO | Summer | 3615.722 | 324.28 | 1 | 1 | 3122-Gaskets and seals | D1-Forced - Immediate | 200-Nuclear
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 20.7 | 27 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 830-Geothermal
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 106.65 | 27 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 830-Geothermal
3122 | Gaskets and seals | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 104.6332 | 146 | 1 | 1 | 3122-Gaskets and seals | U1-Forced - Immediate | 851-CC GT units
3122 | Gaskets and seals | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 58.4083 | 81.5 | 1 | 1 | 3122-Gaskets and seals | D1-Forced - Immediate | 852-CC steam units
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6885 | 510 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 100-Fossil-Steam
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 2911.75 | 613 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 100-Fossil-Steam
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3977 | 410 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 100-Fossil-Steam
3123 | Hot well | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 3.575 | 1.1 | 1 | 1 | 3123-Hot well | D1-Forced - Immediate | 650-Fluidized Bed
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | RFC | Summer | 112.75 | 45.1 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 650-Fluidized Bed
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 72.5332 | 256 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 850-Combined Cycle Block
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 200.5332 | 256 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 850-Combined Cycle Block
3123 | Hot well | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Summer | 204.8 | 256 | 1 | 1 | 3123-Hot well | U1-Forced - Immediate | 850-Combined Cycle Block
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 145.6667 | 23 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 60 | 16 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 500 | 250 | 1 | 1 | 3124-Tube sheet fouling | D3-Forced - Postponed | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 344 | 16 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 284.9998 | 225 | 1 | 1 | 3124-Tube sheet fouling | D3-Forced - Postponed | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 419.9998 | 225 | 1 | 1 | 3124-Tube sheet fouling | D3-Forced - Postponed | 100-Fossil-Steam
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 416 | 26 | 2 | 2 | 3124-Tube sheet fouling | D1-Forced - Immediate | 851-CC GT units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 7784.8333 | 65 | 1 | 1 | 3124-Tube sheet fouling | U1-Forced - Immediate | 851-CC GT units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 544 | 34 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 852-CC steam units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 23.4667 | 44 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 852-CC steam units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 10299.5666 | 37 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 852-CC steam units
3124 | Tube sheet fouling | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 389.1667 | 50 | 1 | 1 | 3124-Tube sheet fouling | D1-Forced - Immediate | 852-CC steam units
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5025.5331 | 356 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 5812.5 | 625 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | SF-Startup Failure | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 18211.6665 | 446 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U2-Forced - Delayed | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5160 | 5 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 100-Fossil-Steam
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 28.91 | 5.9 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 180.2 | 17 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 333.71 | 22.1 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 108.96 | 45.4 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 256.85 | 33 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 20.995 | 5.1 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | D1-Forced - Immediate | 200-Nuclear
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1507.7333 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 79.2 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 5734.6666 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 4222.5333 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 523.6 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3129 | Other condenser casing or shell and internal problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 8296.9333 | 88 | 1 | 1 | 3129-Other condenser casing or shell and internal problems | U1-Forced - Immediate | 850-Combined Cycle Block
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 2225.2833 | 73 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 652.9333 | 59 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 100-Fossil-Steam
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 92.5 | 15 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 24546.69 | 580.3 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 44.8333 | 10 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 3.2035 | 192.22 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Off-Peak | 3951.6096 | 202.82 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 200-Nuclear
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 135.8 | 42 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 830-Geothermal
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 1045.74 | 180.3 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 850-Combined Cycle Block
3130 | Air ejectors | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 207.1875 | 276.25 | 1 | 1 | 3130-Air ejectors | U1-Forced - Immediate | 850-Combined Cycle Block
3130 | Air ejectors | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 67.8 | 9 | 1 | 1 | 3130-Air ejectors | D1-Forced - Immediate | 852-CC steam units
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 438.75 | 225 | 1 | 1 | 3131-Air ejector piping and valves | SF-Startup Failure | 100-Fossil-Steam
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 4602.5 | 526 | 1 | 1 | 3131-Air ejector piping and valves | SF-Startup Failure | 100-Fossil-Steam
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 96.2667 | 8 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 650-Fluidized Bed
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 71.1964 | 427.18 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 118.8 | 66 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 258.4167 | 35 | 1 | 1 | 3131-Air ejector piping and valves | U1-Forced - Immediate | 851-CC GT units
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 65.4 | 26.16 | 3 | 3 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 851-CC GT units
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 115 | 46 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 852-CC steam units
3131 | Air ejector piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | SERC | Summer | 1 | 4 | 1 | 1 | 3131-Air ejector piping and valves | D1-Forced - Immediate | 862-CoG steam units
3132 | Inter and after condensers | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 13253.8332 | 283 | 1 | 1 | 3132-Inter and after condensers | D3-Forced - Postponed | 100-Fossil-Steam
3132 | Inter and after condensers | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 432 | 80 | 1 | 1 | 3132-Inter and after condensers | D1-Forced - Immediate | 852-CC steam units
3132 | Inter and after condensers | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 113.5833 | 235 | 1 | 1 | 3132-Inter and after condensers | U1-Forced - Immediate | 852-CC steam units
3132 | Inter and after condensers | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 1124.3665 | 178 | 1 | 1 | 3132-Inter and after condensers | U1-Forced - Immediate | 852-CC steam units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 1478.4665 | 268 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 1558.25 | 271 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10416.3665 | 422 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 619.6666 | 110 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1698.0948 | 501.9 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 432 | 240 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 693.1833 | 199 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8974.6665 | 635 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 60 | 240 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 837.0833 | 49 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2774.3333 | 29 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 100-Fossil-Steam
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 31.3333 | 40 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 377.1 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 29.3333 | 32 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 32.8 | 16 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 39.9667 | 22 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 104.4 | 72 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 12.4 | 8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 74.9 | 42 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 10.5 | 30 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 29.25 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 536.4 | 27 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 272 | 48 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 22.6667 | 17 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 48.5333 | 32 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 830-Geothermal
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 98.3333 | 25 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 90.525 | 106.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 199.6 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 793.76 | 96.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 517.1666 | 72.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 653.125 | 62.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1358.53 | 43.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 100.725 | 39.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 429.975 | 94.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1149.6 | 95.8 | 1 | 2 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1496.34 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 272.8583 | 68.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 100 | 62.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 380.4583 | 57.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 128.25 | 67.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1103.9583 | 87.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 490 | 73.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 170.1166 | 86.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 653.35 | 89.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 586.8 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 948 | 94.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 171.5 | 58.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 195.6 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 183.75 | 52.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 580.8 | 96.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 115.6 | 57.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 125.875 | 47.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 250.6766 | 95.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 305 | 91.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 684.6 | 97.8 | 1 | 2 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1004.3033 | 95.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 394 | 98.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 418.95 | 73.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 556.6666 | 83.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 111.1666 | 57.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 161.37 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 289 | 57.8 | 2 | 2 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 496.4166 | 92.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 698.6 | 99.8 | 1 | 2 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 998 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 3078 | 19 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 533.4166 | 86.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 91.0416 | 57.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 332.45 | 91.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 555.75 | 97.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 647.5 | 92.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 635.36 | 60.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 696.6666 | 104.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 87.2083 | 57.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 262.0833 | 42.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 591 | 98.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1197.6 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 65.8 | 65.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 598.8 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 25.5 | 42.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 135.2 | 84.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1463.7333 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 199.6 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 586.8 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 68.7083 | 42.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 261.1433 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 582.1666 | 99.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 293.4 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 575 | 57.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 882 | 37.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 57.9667 | 23.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 48.125 | 52.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 561 | 93.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 679.875 | 92.5 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 782.4 | 97.8 | 1 | 1 | 3133-Vacuum pumps | D3-Forced - Postponed | 850-Combined Cycle Block
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 2808.3999 | 168 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 851-CC GT units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 6806.7999 | 168 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 851-CC GT units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 80.3 | 146 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 851-CC GT units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 2557.8666 | 218 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 852-CC steam units
3133 | Vacuum pumps | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 44.825 | 81.5 | 1 | 1 | 3133-Vacuum pumps | D1-Forced - Immediate | 852-CC steam units
3133 | Vacuum pumps | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 91.8333 | 190 | 1 | 1 | 3133-Vacuum pumps | U1-Forced - Immediate | 852-CC steam units
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 198 | 88 | 1 | 1 | 3134-Vacuum pump piping and valves | D1-Forced - Immediate | 100-Fossil-Steam
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 543.75 | 375 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 17605.7333 | 184 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 100-Fossil-Steam
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 150.3667 | 26 | 1 | 1 | 3134-Vacuum pump piping and valves | D2-Forced - Delayed | 100-Fossil-Steam
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 112.5 | 27 | 1 | 1 | 3134-Vacuum pump piping and valves | D1-Forced - Immediate | 830-Geothermal
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 94.7 | 3 | 1 | 1 | 3134-Vacuum pump piping and valves | D1-Forced - Immediate | 830-Geothermal
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 594.5 | 290 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 885.7933 | 51.7 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1729.6013 | 537.7 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 14939.6683 | 84.7 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 1164.0581 | 340.7 | 1 | 1 | 3134-Vacuum pump piping and valves | D1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 643.6613 | 551.71 | 1 | 1 | 3134-Vacuum pump piping and valves | U1-Forced - Immediate | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 38228.7033 | 51.7 | 1 | 1 | 3134-Vacuum pump piping and valves | U2-Forced - Delayed | 850-Combined Cycle Block
3134 | Vacuum pump piping and valves | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 21.75 | 26.1 | 1 | 1 | 3134-Vacuum pump piping and valves | SF-Startup Failure | 852-CC steam units
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 290 | 87 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 67.2 | 112 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 415.9999 | 312 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 237.9666 | 59 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 28.8 | 54 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 231.2 | 34 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 100-Fossil-Steam
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 376.2 | 27 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | U1-Forced - Immediate | 830-Geothermal
3135 | Vacuum pump motor and auxiliaries | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 1049.4 | 18 | 1 | 1 | 3135-Vacuum pump motor and auxiliaries | D1-Forced - Immediate | 830-Geothermal
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 162.4957 | 10.01 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 100-Fossil-Steam
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 190 | 95 | 1 | 1 | 3139-Other air extraction system problems - general | D1-Forced - Immediate | 100-Fossil-Steam
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Winter | 2414.85 | 51 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 100-Fossil-Steam
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 51.2333 | 58 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 830-Geothermal
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Off-Peak | 182 | 280 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 850-Combined Cycle Block
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | NPCC | Winter | 3283.165 | 81.3 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 850-Combined Cycle Block
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 1131.6 | 164 | 1 | 1 | 3139-Other air extraction system problems - general | U2-Forced - Delayed | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 3739.2 | 164 | 1 | 1 | 3139-Other air extraction system problems - general | U2-Forced - Delayed | 851-CC GT units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 2805 | 255 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 852-CC steam units
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 4184.5999 | 294 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 860-Co-generator Block
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | MRO | Summer | 6762 | 294 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 860-Co-generator Block
3139 | Other air extraction system problems - general | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 862 | CoG steam units | TRE | Winter | 207.74 | 66.3 | 1 | 1 | 3139-Other air extraction system problems - general | U1-Forced - Immediate | 862-CoG steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 352.5 | 352.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 1522.05 | 219 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.55 | 21 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 67.41 | 10.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 107.7133 | 10.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 114.8 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 176 | 16 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 435.4666 | 92 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 954.8 | 62 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1096.095 | 42.9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1274 | 39 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16093 | 385 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 39.1 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 395.4166 | 65 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 3734.6666 | 80 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Off-Peak | 22 | 44 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 52.1333 | 34 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 168.9333 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 477.9 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 155.75 | 35 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 203.7333 | 16 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1367.6 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18856 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 38203 | 92 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 37.2 | 1.55 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Summer | 13.9333 | 44 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 13276.6666 | 140 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 133.35 | 12.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 143.7333 | 49 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 240 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 925.4667 | 44 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 86402.4333 | 61 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 4.75 | 95 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 234.3167 | 17 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 634.1333 | 116 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 282.6666 | 160 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 725.9998 | 360 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.6667 | 29 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 32.1167 | 41 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 445.0833 | 49 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 15.4 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 31.6667 | 50 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 156.8 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 231 | 21 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 278.1 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 1011.7333 | 11.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 7654.1665 | 250 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 62491 | 836 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 1079.9997 | 405 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 507.6085 | 447.89 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 25.1667 | 10 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 323.9166 | 65 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 30.4 | 16 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 62 | 31 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 119 | 34 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 196 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 843.15 | 219 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1341.0666 | 188 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 128.8 | 16 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 202.4 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 228.3667 | 26 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 282.75 | 29 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 295 | 25 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | NPCC | Winter | 81.6 | 1.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 989.4 | 582 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 1219.7499 | 105 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 27 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 38.4 | 64 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 24788.8332 | 170 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 46 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 118 | 59 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 121.55 | 10.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 202.5 | 45 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 811.5666 | 194 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 94.4 | 12 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 96.3667 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 45.8333 | 110 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 523.6 | 84 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 84 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 224.8333 | 190 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 615.2667 | 44 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 639.5333 | 53 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2830.1 | 91 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 366 | 73.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 115.6833 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 217.4666 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1125.6667 | 22 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 5634.3666 | 24.4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 8886.25 | 75 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 87.8106 | 77.48 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 64.0166 | 167 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 418.0305 | 447.89 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 3549.5333 | 148 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 81.3833 | 19 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 223.0667 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 461.55 | 51 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3246.25 | 53 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 163.9 | 22 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 60557.4666 | 92 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4542.2664 | 836 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 749.2333 | 169 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 74 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 65.25 | 45 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 557.3333 | 190 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 700.1165 | 353 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 989.7333 | 104 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1383.6332 | 206 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 193.5833 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 216.9667 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 305.9 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 592.1666 | 95 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Off-Peak | 268.305 | 178.87 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 45.45 | 20.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 66.6667 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 184.5 | 54 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 360.9666 | 49 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 538.45 | 89 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 2973.1833 | 229 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3436 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 81803.3332 | 194 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3.15 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 140.75 | 15 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 160.9333 | 17 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 268.3333 | 100 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 1003.1666 | 65 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 20123.1083 | 34.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 135 | 60 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D2-Forced - Delayed | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Off-Peak | 222.1666 | 62 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18.6333 | 26 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 74.9 | 10.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 585 | 54 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 684.3666 | 49 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 6281.2 | 41 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 181.3167 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 306.6666 | 40 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 101.25 | 45 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D2-Forced - Delayed | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 40582.3331 | 422 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 93.8666 | 128 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 200.4 | 24 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 630 | 54 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1669.3333 | 64 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 39.2 | 21 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 80.1 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 155.7333 | 16 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 204.5 | 15 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 208.9167 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 273.75 | 45 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D2-Forced - Delayed | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4144.75 | 702.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Summer | 161.975 | 104.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 27.8667 | 44 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 66.34 | 10.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 315.25 | 39 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 491.4 | 54 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 576.95 | 33 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 74.25 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 6842.5 | 35 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 49.0666 | 64 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 161.1 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 319.3 | 62 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 657.4166 | 49 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 7863.6 | 36 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 88.9166 | 55 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25691.9582 | 157.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 281829.5328 | 836 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 3881.1666 | 290 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1207.5 | 575 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 5213.25 | 105 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5.0333 | 15.1 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 180.6 | 84 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 574 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1004.7666 | 86 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1778.4666 | 74 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2184 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 283.2833 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 313.1833 | 23 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 10210.6667 | 32 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 18407.7 | 101.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 183.882 | 96.78 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | SERC | Winter | 12000 | 75 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 100-Fossil-Steam
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 187281.985 | 278.3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 200-Nuclear
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 7.8 | 3.9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.6 | 3.3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 85.1 | 3.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 75.6 | 4.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 162 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 309 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 6.2 | 3.1 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 64.6 | 3.4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | BM | 650 | Fluidized Bed | WECC | Off-Peak | 172.825 | 9.3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 39.6 | 3.3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | TRE | Summer | 16 | 3.2 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 650-Fluidized Bed
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | WECC | Summer | 56.98 | 25.9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 800-Miscellaneous
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | BM | 800 | Miscellaneous | SERC | Off-Peak | 333.125 | 19.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 800-Miscellaneous
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 9 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 4.5 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 5136.3 | 39 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 92.4 | 42 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 58.8 | 42 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 17.1 | 27 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 52.7333 | 14 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 830-Geothermal
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 15 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 72 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 27 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 84 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 114 | 38 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 4489.9998 | 300 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 26 | 13 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 44 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 72 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 1114.0252 | 941.43 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | SF-Startup Failure | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 416.2665 | 223 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 18 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 39 | 13 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 56 | 7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 180 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 158.0998 | 306 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 242.0332 | 274 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 34 | 85 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1503.0833 | 85 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 72 | 12 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 11554.3 | 22.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 792 | 240 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 1343 | 85 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 48 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 97.8833 | 7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 71.55 | 71.55 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Summer | 1978.7332 | 268 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 167.7332 | 272 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 24 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 40 | 8 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 64 | 8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 39 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 168 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 13 | 13 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 88 | 11 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 224 | 28 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 597.4 | 206 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 12 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 54 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 799.3333 | 220 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Off-Peak | 8.6666 | 260 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 144 | 18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 107.8 | 308 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 6 | 3 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 9 | 3 | 1 | 3 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 58.5 | 9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 84 | 7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 91 | 13 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 3009.9999 | 300 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1959.1 | 602.8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 742.3333 | 85 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 217 | 31 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 123.78 | 123.78 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 850-Combined Cycle Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 82.8333 | 99.4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 622.4999 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 31871.25 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 695.5666 | 77 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 82.1666 | 98.6 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 33.0666 | 248 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 880.1333 | 184 | 2 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 31953.7499 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 4192.3499 | 171 | 2 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 20.6666 | 248 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 255.7499 | 247.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 115.3165 | 187 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 140.85 | 187.8 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U2-Forced - Delayed | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 722.6166 | 191 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 18.7499 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 41.2499 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 155.3666 | 59 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 56.25 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 204.9333 | 232 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 22.5 | 225 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 837.1083 | 155.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 299.2499 | 189 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 106.05 | 9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 43.0733 | 99.4 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Summer | 790.4583 | 155.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Winter | 42.7266 | 98.6 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 270.6665 | 232 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 787.55 | 57 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 932.7166 | 191 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 851-CC GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 3.6667 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Off-Peak | 194.7096 | 89.18 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 468.8 | 96 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 4092 | 186 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 415.5333 | 46 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 89.6999 | 234 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 196.6666 | 236 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 1114.5166 | 233 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 34660.2 | 244 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 5.6667 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 142.2499 | 170.7 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 2142.3 | 9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 131.9666 | 107 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 74.1665 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 4.3333 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 363.2 | 96 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 641.55 | 47 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 229.2 | 382 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 3878.9 | 158 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 210.7499 | 252.9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 884.1066 | 109.6 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 35.6 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 25.65 | 171 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 250.9831 | 407 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 109.0916 | 123.5 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 231.6532 | 190.4 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 1312.9664 | 331 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Winter | 117.25 | 335 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 3 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 216.9999 | 186 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 572.7498 | 237 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 306.3667 | 26 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 1841.0167 | 13 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Winter | 468.7333 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | D1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 447.3649 | 204.9 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5235.9 | 186 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Winter | 6.3333 | 20 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 99.3 | 331 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 109.5899 | 252.9 | 1 | 2 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 852-CC steam units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Summer | 390.5039 | 221.04 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 860-Co-generator Block
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 2391.1333 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 861-CoG GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | WECC | Off-Peak | 1664.3 | 178 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 861-CoG GT units
3149 | Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | WECC | Off-Peak | 2450.3 | 214 | 1 | 1 | 3149-Loss of vacuum not attributable to a particular component such as air ejectors or valves; or high back pressure not attributable to high circulating water temperature; or vacuum losses from a known cause. | U1-Forced - Immediate | 862-CoG steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 3185.25 | 465 | 1 | 1 | 3150-Hot well level controls | SF-Startup Failure | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 7911.2 | 66 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 394.1666 | 110 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 855 | 475 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 295.8333 | 250 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 100-Fossil-Steam
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | WD | 650 | Fluidized Bed | SERC | Summer | 23.8 | 102 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 650-Fluidized Bed
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 22.5 | 90 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | MRO | Summer | 586.6666 | 160 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 162 | 72 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 1954.8 | 12 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 111.8 | 13 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 87.0833 | 5 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 151.4833 | 61 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 996 | 72 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 830-Geothermal
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Winter | 832.4332 | 221 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 851-CC GT units
3150 | Hot well level controls | Balance of Plant | Condensing System | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 772.2 | 156 | 1 | 1 | 3150-Hot well level controls | U2-Forced - Delayed | 851-CC GT units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 2321.9999 | 405 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 392 | 280 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | NPCC | Winter | 482.1332 | 128 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 725.4 | 186 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6.5333 | 49 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 12.8 | 24 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 852-CC steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 10351.5999 | 168 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 861-CoG GT units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Off-Peak | 9469.5999 | 168 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 861-CoG GT units
3150 | Hot well level controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 15.1666 | 91 | 1 | 1 | 3150-Hot well level controls | D1-Forced - Immediate | 862-CoG steam units
3150 | Hot well level controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Off-Peak | 11287.4666 | 176 | 1 | 1 | 3150-Hot well level controls | U1-Forced - Immediate | 862-CoG steam units
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 55.9 | 43 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 100-Fossil-Steam
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Off-Peak | 204.5175 | 30.15 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 100-Fossil-Steam
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 904.4 | 532 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 100-Fossil-Steam
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 47.25 | 27 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 830-Geothermal
3151 | Vacuum pump and air ejector controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 268.3332 | 161 | 1 | 1 | 3151-Vacuum pump and air ejector controls | U1-Forced - Immediate | 852-CC steam units
3152 | Air-cooled condenser controls | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 376.6832 | 233 | 1 | 1 | 3152-Air-cooled condenser controls | U1-Forced - Immediate | 850-Combined Cycle Block
3152 | Air-cooled condenser controls | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 65.76 | 54.8 | 1 | 1 | 3152-Air-cooled condenser controls | D1-Forced - Immediate | 850-Combined Cycle Block
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Other | WD | 100 | Fossil-Steam | SERC | Summer | 22.2817 | 4.61 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1436.458 | 492.5 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 100.8332 | 242 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 14261.42 | 99.8 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 100 | Fossil-Steam | WECC | Off-Peak | 342.8332 | 242 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 100-Fossil-Steam
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 494.9 | 42 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 830-Geothermal
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Winter | 10.35 | 207 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 850-Combined Cycle Block
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 591.25 | 43 | 1 | 1 | 3159-Other condensing system controls and instruments | D1-Forced - Immediate | 850-Combined Cycle Block
3159 | Other condensing system controls and instruments | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 42.9167 | 20.6 | 1 | 1 | 3159-Other condensing system controls and instruments | U1-Forced - Immediate | 852-CC steam units
3170 | Condenser inspection (use code 3110 to report looking for tube leaks) | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 4100.4164 | 325 | 1 | 1 | 3170-Condenser inspection (use code 3110 to report looking for tube leaks) | D2-Forced - Delayed | 100-Fossil-Steam
3180 | Major condenser overhaul | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 36994.1833 | 49 | 1 | 1 | 3180-Major condenser overhaul | U1-Forced - Immediate | 852-CC steam units
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 0.69333 | 10.4 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 22.1667 | 5 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 45.0667 | 8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 50.2 | 12 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 26.6 | 7 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 55.5 | 10 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10741.9999 | 393 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 175 | 30 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 77 | 35 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 43.8 | 9 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4652.343 | 59.94 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 32.8 | 8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 47.6 | 24 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 44.5 | 10 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 67.8667 | 8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 111.8333 | 22 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 115.25 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60.3 | 9 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 65.1933 | 25.4 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 168.4867 | 25.4 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5.39 | 15.4 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 12099.2 | 398 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 29 | 5 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 23.25 | 15 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 34.5333 | 8 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 144 | 30 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D3-Forced - Postponed | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 487.05 | 9.55 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 58.3333 | 7 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 77.25 | 9 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 77.7 | 9 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 122.6503 | 85.57 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3186 | Auxiliary Condenser and Associated Equipment | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 27.3 | 7 | 1 | 1 | 3186-Auxiliary Condenser and Associated Equipment | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 481.4166 | 53 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 113449.0997 | 762 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 26.6666 | 64 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D2-Forced - Delayed | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | NPCC | Summer | 2298.7333 | 16.4 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 368.3333 | 50 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1269.7916 | 62.5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 275.5 | 57 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D2-Forced - Delayed | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | OS | 100 | Fossil-Steam | RFC | Off-Peak | 84 | 30 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 469.3332 | 352 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 53 | 53 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 123.6666 | 53 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 139.2405 | 132.61 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 20449 | 422.5 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 100-Fossil-Steam
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 5840.0999 | 243 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 200-Nuclear
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 248227.4659 | 1099 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 200-Nuclear
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 26592.3 | 567 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 200-Nuclear
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | TRE | Off-Peak | 448 | 256 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 294 | 35 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Off-Peak | 448 | 35 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | D1-Forced - Immediate | 850-Combined Cycle Block
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 217.0666 | 148 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 325.8499 | 147 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 8156.4 | 168 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 851-CC GT units
3190 | Air leakage (for losses not attributable to previously noted equipment related codes) | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Summer | 436.3665 | 247 | 1 | 1 | 3190-Air leakage (for losses not attributable to previously noted equipment related codes) | U1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 21.1 | 10.55 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16.8 | 2.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 76.7997 | 9.62 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3063.9666 | 34 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 15.63 | 5.21 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D2-Forced - Delayed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 75137.1828 | 749 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 54.6667 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1531.6 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 60 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 290.625 | 46.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 365.3333 | 32 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 520.625 | 52.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 60.71 | 4.67 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 90.8667 | 29 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 224 | 42 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 297.5 | 42 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 593.2 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5.5467 | 10.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 255.925 | 43.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 276.4 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 348 | 43.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 362.5 | 43.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 6035.2 | 656 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1972.1998 | 342 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 352.4495 | 72.67 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 939.6 | 54 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 322 | 28 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 2.5 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 97.5 | 26 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 126.5333 | 26 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 147 | 12 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 74.3 | 7.43 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 95.3166 | 43 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D2-Forced - Delayed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4039 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 138.32 | 17.29 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 332.5 | 42 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 468 | 12 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 4443.6333 | 22 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 11.7 | 54 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 34.93 | 4.99 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 170.8667 | 44 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 794 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 64 | 20 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 168 | 28 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 1643.2498 | 315 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 72.8 | 104 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 76.44 | 12.74 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9.0333 | 2 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 43.8333 | 10 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 103.3333 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 594.825 | 51.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 83.8666 | 34 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 10 | 10 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 32.6333 | 22 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 204.75 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 329.4666 | 28 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 334.4 | 32 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 842.7665 | 262 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 8.1 | 54 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5 | 2.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 51.9167 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 5750.7867 | 29.6 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D2-Forced - Delayed | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 0.99999 | 15 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5.8333 | 2 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 53.5333 | 22 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 133.3 | 62 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 238.3333 | 50 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 353.6 | 104 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2441.6 | 64 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 24.96 | 10.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 303.775 | 43.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 588 | 73.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 24 | 15 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 161 | 42 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1725.6 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 81.5833 | 11 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 88.6667 | 8 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 100 | 25 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 277.2 | 22 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 6707.25 | 165 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 13.6 | 24 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 5.1333 | 15.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 4.25 | 17 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5.3667 | 14 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 73.3 | 14.66 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 241.3667 | 26 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 86.6192 | 10.85 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 628.2666 | 62 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 0.58331 | 35 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 160.95 | 43.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 197.7667 | 17 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6803.4663 | 496 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 100-Fossil-Steam
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Winter | 32906.61 | 425.7 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 200-Nuclear
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 35.2 | 4.4 | 1 | 2 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 74.4 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 92.845 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 13.2 | 4.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 33 | 4.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 92.7 | 10.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 102.3 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 130.2 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 800 | Miscellaneous | WECC | Off-Peak | 133 | 266 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 37.4 | 4.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 20.925 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 110.98 | 9.3 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | RFC | Summer | 31.9 | 4.4 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 800-Miscellaneous
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 86.85 | 27 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 830-Geothermal
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 2591.1 | 27 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 830-Geothermal
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 254.9166 | 57.5 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Winter | 622.2 | 244 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 3952.095 | 537.7 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | TRE | Winter | 4.0332 | 242 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 850-Combined Cycle Block
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 170.7999 | 168 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 1111.5999 | 168 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 1858.1333 | 64 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 1398.8 | 269 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 243.9998 | 240 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 383.5999 | 168 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 884.7999 | 168 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 252 | 168 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 213.75 | 225 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 851-CC GT units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Off-Peak | 211.4999 | 135 | 1 | 1 | 3199-Other miscellaneous condensing system problems | U1-Forced - Immediate | 852-CC steam units
3199 | Other miscellaneous condensing system problems | Balance of Plant | Condensing System | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 81.76 | 102.2 | 1 | 1 | 3199-Other miscellaneous condensing system problems | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 126.5 | 22 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1177 | 107 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 2800.6 | 209 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 1830.65 | 41 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 83.1999 | 96 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5503.5333 | 124 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 22863.7499 | 315 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 556.9666 | 77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1531.25 | 175 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 3633.7499 | 135 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 517.6998 | 501 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 80.7833 | 37 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 935.8499 | 153 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 1188 | 22 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 7082.95 | 21 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 89145.4 | 122 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 44.1 | 27 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 127.0333 | 37 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 234.5 | 42 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 9150.4166 | 25 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 632.1 | 98 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 1116 | 240 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 1592.2666 | 112 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 3944.4164 | 331 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7963.935 | 103.9 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 32745.2 | 142 | 1 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 232.8166 | 61 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 8 | 12 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 24.5 | 10 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 78.4 | 14 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 147.9 | 17 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 554.6166 | 107 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 14678 | 164 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 157.3 | 22 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.2 | 12 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 559.9998 | 300 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 52273.2 | 381 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 400.9333 | 124 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 597.5 | 150 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 626.1665 | 289 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2588.5999 | 258 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 4830 | 140 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 837.6 | 279.2 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 5839.18 | 103.9 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 239.6333 | 79 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 799.5166 | 77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 4533.3332 | 400 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 24748.6 | 20.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 50627.9666 | 122 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Winter | 22540 | 28 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 18682.9516 | 103.9 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 41.6 | 52 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 134.4 | 42 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 198.7499 | 225 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1927.5998 | 366 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 4351.6667 | 20 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 6963.25 | 69 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 32.5 | 26 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 39.2 | 42 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11572.8332 | 230 | 1 | 1 | 3210-Circulating water pumps | SF-Startup Failure | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 413.4 | 39 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 914.6665 | 392 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 102739.44 | 39.4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.6 | 32 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 123.2 | 32 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 128.9166 | 119 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 89.4 | 12 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 6476.6665 | 232 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 6319.68 | 131.66 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 90.6499 | 147 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 25476.5 | 21 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 52.2 | 12 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 81 | 20 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 273.7 | 42 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1389.8666 | 64 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1830.65 | 123 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 11021.6665 | 425 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 474.5 | 73 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 14016.6666 | 116 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 136019.8333 | 122 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 181.1333 | 44 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 385 | 77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 425.4167 | 25 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 604.75 | 41 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 21265.2 | 118.14 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 12.6 | 27 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 43.2667 | 22 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 712.8 | 99 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1485.9 | 39 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 940 | 188 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 29462.6333 | 142 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 919.45 | 21 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 16 | 32 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 25.3 | 22 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 41787.0833 | 25 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Summer | 6862.5 | 375 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 391.7333 | 104 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 26.1 | 27 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7550.55 | 119 | 1 | 1 | 3210-Circulating water pumps | D3-Forced - Postponed | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 11059.2998 | 543.9 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 347.6665 | 298 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Off-Peak | 620.55 | 27 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 9585.8 | 164 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3.6 | 12 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 6386.3332 | 322 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 137735.9666 | 122 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 512.05 | 133 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | WECC | Winter | 2669.5 | 57 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 10646.3331 | 820 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 100-Fossil-Steam
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 447.75 | 15 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 36 | 4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 197.0328 | 3.53 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1152.5 | 15 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0.65 | 0.65 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 0.96 | 0.96 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 774.37 | 21.1 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | NPCC | Summer | 16699.1 | 355.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 871 | 20 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 74.8 | 4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 100.38 | 4.78 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 2304.7337 | 13.54 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 40.74 | 2.91 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 14703.85 | 9.77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 10991.8667 | 8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 55.5 | 3.7 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 3054.06 | 10.83 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 38.78 | 2.77 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 169.57 | 5.47 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 269.28 | 6.12 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 382.2 | 6.3 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 76 | 4 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Off-Peak | 1158.5 | 15 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 7.65 | 1.53 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 2041.5 | 10 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 19.8333 | 10 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 70.74 | 3.93 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1091.5667 | 22 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 200-Nuclear
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 810 | Multi-boiler/Multi-turbine | SERC | Summer | 96612 | 194 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 810-Multi-boiler/Multi-turbine
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 10135.9193 | 25.64 | 1 | 1 | 3210-Circulating water pumps | U2-Forced - Delayed | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 6.15 | 9 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 120.508 | 25.64 | 1 | 1 | 3210-Circulating water pumps | U2-Forced - Delayed | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Winter | 5.95 | 17 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 830-Geothermal
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 377 | 29 | 1 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 120 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 87 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 232 | 29 | 1 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 174 | 29 | 1 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 6136.9998 | 510 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 29.34 | 97.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 930.9998 | 570 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1009.4999 | 90 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 3081.6 | 48 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 16.2866 | 69.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 58 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 69211.4999 | 90 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 111572.6466 | 85.9 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 87 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 10307.9999 | 180 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 29406.8331 | 365 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8723.9995 | 720 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 238.4665 | 292 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 605 | 242 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 35578.9166 | 215 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 58 | 29 | 1 | 3 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 248.9 | 262 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 133.4666 | 91 | 2 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 406 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 29 | 29 | 1 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 290 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 37.38 | 106.8 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 1031.9333 | 92 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 7403.4997 | 510 | 1 | 1 | 3210-Circulating water pumps | U2-Forced - Delayed | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Summer | 203 | 29 | 1 | 3 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | MRO | Off-Peak | 1682 | 29 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 102224.925 | 360.9 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Summer | 114.597 | 429.74 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 55171.3165 | 259 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 8918.833 | 907 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 850-Combined Cycle Block
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | MRO | Summer | 733.3333 | 80 | 2 | 2 | 3210-Circulating water pumps | D2-Forced - Delayed | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 44143.75 | 175 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 590.9999 | 180 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Off-Peak | 1381.6333 | 181 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 323.75 | 15 | 2 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 2858.1446 | 213.56 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Winter | 160.4666 | 166 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 20.8332 | 125 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 22.9166 | 125 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 152.9833 | 67 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3724.4165 | 187 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 966.9333 | 56 | 2 | 2 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Summer | 3644.7499 | 183 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 1539 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 448 | 56 | 2 | 6 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 209.9999 | 180 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Off-Peak | 2166 | 30 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 70.35 | 67 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 1576.7846 | 213.56 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 354 | 177 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 851-CC GT units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 1093.89 | 208.36 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 542.5 | 217 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 947.2203 | 124.09 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 146.2 | 86 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 53.3331 | 320 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 3347.1411 | 407.36 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | NPCC | Summer | 3565.0832 | 179 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 852 | CC steam units | MRO | Summer | 824.9999 | 90 | 1 | 1 | 3210-Circulating water pumps | D2-Forced - Delayed | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 832 | 260 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 291.8333 | 34 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 17353.4166 | 121 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 26692.8332 | 170 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Summer | 126.9 | 141 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 119.1667 | 26 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 1756.8833 | 101.75 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Off-Peak | 0 | 0 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Summer | 61.2 | 72 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 5767 | 73 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 539.5833 | 25 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 193.5 | 135 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 5754.8333 | 73 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 3264 | 170 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 17.2 | 24 | 1 | 1 | 3210-Circulating water pumps | U1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 28.8749 | 157.5 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | MRO | Off-Peak | 2742 | 40 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 814 | 101.75 | 1 | 3 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3210 | Circulating water pumps | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 9221.044 | 20.36 | 1 | 1 | 3210-Circulating water pumps | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 10886.1666 | 215 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 108680 | 130 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2023 | Coal | LI | 100 | Fossil-Steam | MRO | Off-Peak | 75105 | 450 | 1 | 1 | 3211-Circulating water pump motors | U3-Forced - Postponed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 87.8332 | 170 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 144.9999 | 150 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 534.75 | 115 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 130.1333 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 417.0667 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 5773.3333 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 36890.5186 | 162.92 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 2782.3332 | 340 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7074.6666 | 70 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 3002.8265 | 433.1 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 16940.5 | 17 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 0 | 71 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Oil | OO | 100 | Fossil-Steam | NPCC | Winter | 11174.41 | 111.8 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 51.5666 | 91 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 780.2666 | 77 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 8550 | 90 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Summer | 5752.5 | 130 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 6759.9998 | 240 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 459.25 | 55 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 822.6667 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 3591.975 | 101.9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 770.5 | 15 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 402.5 | 350 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 378.6667 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 393.6175 | 59.79 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 1110.6667 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 6457.3333 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 49324.9333 | 17 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 955.7997 | 486 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 154 | 220 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Off-Peak | 2805.0667 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 9.75 | 45 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 185.3333 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5601.8333 | 190 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 5700 | 240 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 34.1666 | 25 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 233.3333 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 233.5666 | 91 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 57.95 | 61 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 156.75 | 57 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 873.8332 | 245 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1236 | 240 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 7475 | 250 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 260 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 1258.9666 | 179 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 34713.0666 | 97 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 10263.5 | 39 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 837.5833 | 23 | 1 | 1 | 3211-Circulating water pump motors | D3-Forced - Postponed | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 3142.4999 | 225 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Off-Peak | 20239.5 | 393 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1404 | 90 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 103.3333 | 50 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 284 | 16 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 100 | Fossil-Steam | TRE | Summer | 31688.08 | 96.61 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 2542.4 | 21 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 19.25 | 35 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Winter | 1954.6 | 116 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 100-Fossil-Steam
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 91.35 | 6.09 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 1445.1666 | 65 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Summer | 12 | 6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Summer | 1056.0867 | 7.85 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Off-Peak | 260.6247 | 12.52 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 2.415 | 6.3 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | WECC | Winter | 3395.792 | 11.38 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | RFC | Summer | 42.84 | 30.6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 200-Nuclear
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 650 | Fluidized Bed | SERC | Summer | 240.8 | 48 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 650-Fluidized Bed
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 8.8833 | 13 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 830-Geothermal
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 4999.75 | 35 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 6.82 | 6.2 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 13.95 | 15.5 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | RFC | Summer | 43421.6666 | 50 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 64 | 64 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 718.0166 | 67 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 83.1333 | 86 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 6.955 | 10.7 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 363.895 | 196.7 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Summer | 4490.7495 | 759 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Summer | 27.6933 | 24.8 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | NPCC | Summer | 506.9166 | 55 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 850-Combined Cycle Block
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Winter | 1859.22 | 187.8 | 2 | 2 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 1383.0666 | 164 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | WECC | Summer | 36382.5 | 225 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2023 | Gas | GG | 851 | CC GT units | WECC | Off-Peak | 8321.9333 | 172 | 1 | 1 | 3211-Circulating water pump motors | U2-Forced - Delayed | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 805.4167 | 25 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 193.5 | 135 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 141.1332 | 146 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 196.2233 | 136.9 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 48.6666 | 146 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Off-Peak | 10556.7733 | 58.4 | 2 | 2 | 3211-Circulating water pump motors | D1-Forced - Immediate | 851-CC GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 86.7566 | 61.24 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 6289.8333 | 130 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 1997.4333 | 62 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Winter | 744.3332 | 140 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | WECC | Off-Peak | 486 | 120 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Off-Peak | 2776 | 80 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3600 | 50 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Winter | 100.4416 | 70.9 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 3109.9999 | 150 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 11785.9866 | 65.2 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Winter | 82.9883 | 58.58 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Off-Peak | 14864.3333 | 190 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Off-Peak | 118.6083 | 33.1 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Summer | 19080.6 | 118 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | WECC | Off-Peak | 5911 | 60 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 5.7 | 19 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | TRE | Winter | 1689.93 | 170.7 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 21054.6 | 252 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | RFC | Summer | 57.2 | 44 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 187.45 | 163 | 1 | 1 | 3211-Circulating water pump motors | U1-Forced - Immediate | 852-CC steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 9328.3333 | 58 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 861-CoG GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 861 | CoG GT units | TRE | Winter | 7920.5 | 31 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 861-CoG GT units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 1533 | 6 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 862-CoG steam units
3211 | Circulating water pump motors | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 862 | CoG steam units | TRE | Winter | 3860 | 24 | 1 | 1 | 3211-Circulating water pump motors | D1-Forced - Immediate | 862-CoG steam units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 16495.8332 | 535 | 1 | 1 | 3220-Circulating water piping | SF-Startup Failure | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 181.755 | 173.1 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 55944 | 560 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 11031.9999 | 336 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 9193.3499 | 330.3 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Winter | 26915.2095 | 720.3 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 50175.9998 | 480 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 27776.6665 | 650 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 188.2383 | 213.1 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 1072.0813 | 159.22 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 11757.6 | 552 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 64473.6 | 335.8 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2625.91 | 163.1 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 897.6 | 96 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 2169.0666 | 332 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 103026 | 330 | 1 | 1 | 3220-Circulating water piping | U3-Forced - Postponed | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Summer | 54.915 | 52.3 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 100-Fossil-Steam
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 115 | 115 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 28562.5 | 457 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Off-Peak | 6717.9 | 457 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 60311.55 | 591 | 1 | 1 | 3220-Circulating water piping | SF-Startup Failure | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 95 | 95 | 2 | 2 | 3220-Circulating water piping | D1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Summer | 133.4666 | 104 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | RFC | Winter | 77696.6665 | 650 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 850-Combined Cycle Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 24709.2199 | 157.2 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 851-CC GT units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | TRE | Off-Peak | 25023.5866 | 159.2 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 851-CC GT units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2867.4999 | 186 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 851-CC GT units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | NPCC | Off-Peak | 2449.1499 | 183 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 851-CC GT units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | TRE | Off-Peak | 48726.8332 | 310 | 1 | 1 | 3220-Circulating water piping | U1-Forced - Immediate | 852-CC steam units
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 18.535 | 16.85 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 860-Co-generator Block
3220 | Circulating water piping | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | WECC | Off-Peak | 63.108 | 70.12 | 1 | 1 | 3220-Circulating water piping | D1-Forced - Immediate | 860-Co-generator Block
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Off-Peak | 37966.1166 | 113 | 1 | 1 | 3221-Circulating water piping fouling | D1-Forced - Immediate | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 9894 | 102 | 1 | 1 | 3221-Circulating water piping fouling | D1-Forced - Immediate | 100-Fossil-Steam
3221 | Circulating water piping fouling | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Summer | 579.5833 | 13 | 1 | 1 | 3221-Circulating water piping fouling | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 5157.6331 | 359 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 234.5997 | 414 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 42.3 | 94 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 57.6 | 144 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Winter | 479.5998 | 264 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Off-Peak | 4858.5333 | 104 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | OG | 100 | Fossil-Steam | WECC | Winter | 1892.7333 | 44 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 2126.5999 | 294 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Off-Peak | 2671.1662 | 682 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 3166.25 | 425 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 937.4665 | 316 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 88 | 44 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 182.4999 | 219 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 100.6833 | 172.6 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Off-Peak | 3006.3331 | 311 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 100-Fossil-Steam
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 1 | 1 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 2.4667 | 2 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 29.5 | 3 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 0.78333 | 1 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | LI | 650 | Fluidized Bed | SERC | Off-Peak | 23.3333 | 7 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 650-Fluidized Bed
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | OS | 800 | Miscellaneous | NPCC | Summer | 135.3333 | 58 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 800-Miscellaneous
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Summer | 7.2 | 36 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 830-Geothermal
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 545.6 | 33 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 830-Geothermal
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Geothermal | GE | 830 | Geothermal | WECC | Off-Peak | 524.2667 | 32 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 830-Geothermal
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Off-Peak | 10832.6832 | 173 | 2 | 2 | 3230-Circulating water valves | U1-Forced - Immediate | 850-Combined Cycle Block
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 850 | Combined Cycle Block | SERC | Off-Peak | 12338.7666 | 197 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 850-Combined Cycle Block
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 653.1166 | 149 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 397968.9999 | 165 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | RFC | Summer | 286.9583 | 242.5 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | MRO | Winter | 400410.9999 | 165 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Gas | GG | 851 | CC GT units | SERC | Winter | 311.85 | 189 | 1 | 1 | 3230-Circulating water valves | SF-Startup Failure | 851-CC GT units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | SERC | Summer | 717.8332 | 146 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | RFC | Summer | 705.1998 | 492 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 1208.2499 | 405 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Waste Heat | WH | 852 | CC steam units | MRO | Winter | 338856 | 140 | 1 | 1 | 3230-Circulating water valves | U1-Forced - Immediate | 852-CC steam units
3230 | Circulating water valves | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 860 | Co-generator Block | RFC | Off-Peak | 101.2 | 23 | 1 | 1 | 3230-Circulating water valves | D1-Forced - Immediate | 860-Co-generator Block
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 1752.9832 | 391 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Summer | 188.6913 | 14.78 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Off-Peak | 4406.25 | 375 | 1 | 1 | 3231-Waterbox | SF-Startup Failure | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2621.9165 | 365 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 34696.7499 | 165 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 73341.6658 | 1300 | 1 | 1 | 3231-Waterbox | U1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | TRE | Summer | 2415.6 | 366 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | NPCC | Winter | 465.4999 | 210 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 17606.4 | 168 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Winter | 564.8 | 48 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2847.6247 | 817.5 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 194.9333 | 172 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | TRE | Summer | 544.1331 | 308 | 1 | 1 | 3231-Waterbox | D2-Forced - Delayed | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 1683.7164 | 409 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | SF | Startup Failure | 2023 | Gas | GG | 100 | Fossil-Steam | MRO | Winter | 3675 | 375 | 1 | 1 | 3231-Waterbox | SF-Startup Failure | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 2655.9997 | 384 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 100-Fossil-Steam
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 32.22 | 1.79 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0.16 | 0.16 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0.12 | 0.06 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 0.24 | 0.12 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 8 | 2 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Nuclear | NU | 200 | Nuclear | SERC | Off-Peak | 21.76 | 1.36 | 1 | 1 | 3231-Waterbox | D1-Forced - Immediate | 200-Nuclear
3231 | Waterbox | Balance of Plant | Circulating Water Systems | D2 | Forced - Delayed | 2023 | Gas | GG | 850 | Combined Cycle Block | SERC | Winter | 980.1165 | 271 | 1 | 1 | 3231-Waterbox | D2-Forced - Delayed | 850-Combined Cycle Block
3231 | Waterbox | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Off-Peak | 97.8 | 163 | 1 | 1 | 3231-Waterbox | U1-Forced - Immediate | 852-CC steam units
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 138.3331 | 332 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 502.9331 | 368 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7387.4997 | 450 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | SERC | Summer | 741.9999 | 168 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 141.9867 | 9.2 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 134.5664 | 367 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | U2 | Forced - Delayed | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 26327.35 | 259 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | U2-Forced - Delayed | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Summer | 2944 | 160 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 374.2665 | 401 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 7883.75 | 425 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 0.56 | 4.2 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 51.9767 | 6.2 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Off-Peak | 871.2 | 363 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | U1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 2171.4164 | 367 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | SERC | Summer | 9149.9999 | 450 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | RFC | Winter | 195.81 | 12.2 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 100-Fossil-Steam
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2023 | Gas | GG | 850 | Combined Cycle Block | WECC | Winter | 18368.4997 | 510 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | U3-Forced - Postponed | 850-Combined Cycle Block
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 851 | CC GT units | SERC | Summer | 6651.875 | 181.25 | 2 | 2 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 851-CC GT units
3232 | Condenser tube cleaning system including debris filter | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Gas | GG | 852 | CC steam units | SERC | Summer | 6385.8 | 174 | 1 | 1 | 3232-Condenser tube cleaning system including debris filter | D1-Forced - Immediate | 852-CC steam units
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | D1 | Forced - Immediate | 2023 | Coal | CC | 100 | Fossil-Steam | WECC | Off-Peak | 205.5 | 411 | 1 | 1 | 3235-Cooling tower booster pump | D1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Other | BM | 100 | Fossil-Steam | WECC | Winter | 24.4451 | 63.77 | 1 | 1 | 3235-Cooling tower booster pump | U1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 9729.4999 | 174 | 1 | 1 | 3235-Cooling tower booster pump | U1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U3 | Forced - Postponed | 2023 | Coal | CC | 100 | Fossil-Steam | MRO | Summer | 159423.4832 | 511 | 1 | 1 | 3235-Cooling tower booster pump | U3-Forced - Postponed | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 1233.75 | 175 | 1 | 1 | 3235-Cooling tower booster pump | U1-Forced - Immediate | 100-Fossil-Steam
3235 | Cooling tower booster pump | Balance of Plant | Circulating Water Systems | U1 | Forced - Immediate | 2023 | Gas | GG | 100 | Fossil-Steam | RFC | Winter | 1194.7999 | 174 | 1 | 1 | 3235-Cooling tower booster pump | U1-Forced - Immediate | 100-Fossil-Steam