## Sheet1
Generator Catagory/Classification | Start | End | # Units | Unit-Years | NMC | NDC | Attempts | Actual | SH | RSH | # RSH | Pump Hr | SCH | AH | FOH | # FOH | POH | # POH | SEPO | # SEPO | MOH | # MOH | SEMO | # SEMO | UAH | PH | EFDH | ESDH | EFDHRS | EDOH | POF | MOF | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
FOSSIL All Fuel Types All Sizes | 2022 | 2022 | 797 | 798 | 352 | 351 | 39 | 38.57 | 4436.53 | 2127.93 | 15.67 | 0 | 1.6 | 6566.06 | 537.5 | 6.38 | 768.88 | 1.4 | 36.55 | 0.14 | 307.22 | 2.5 | 4.76 | 0.04 | 1654.9 | 8220.96 | 221.48 | 49.76 | 54.21 | 271.24 | 9.8 | 3.79 | 115.03 | 98.9 | 38.77 | 67.7 | 53.97 | 79.87 | 76.24 | 10.8 | 15.09 | 11.68 | 13.59 | 6.54 | 10.33 | 13.22 | 20.33 | 57.27 | 79.61 | 75.83 | 9.98 | 14.5 | 14.04 | 6.35
FOSSIL All Fuel Types 001-099 | 2022 | 2022 | 150 | 150 | 52 | 51 | 38.59 | 38.43 | 3555.93 | 2147.69 | 18.26 | 0 | 0 | 5703.62 | 664.93 | 5.43 | 813.75 | 1.27 | 26.25 | 0.07 | 206.07 | 1.3 | 0.21 | 0.01 | 1711.21 | 7414.84 | 164.31 | 51.84 | 50.44 | 216.15 | 11.33 | 2.78 | 92.53 | 99.59 | 32.48 | 67.28 | 47.96 | 76.92 | 73.55 | 15.75 | 19.41 | 14.23 | 14.11 | 8.97 | 11.75 | 14.14 | 23.41 | 48.28 | 76.41 | 72.95 | 16.61 | 20.65 | 13.98 | 9.62
FOSSIL All Fuel Types 100-199 | 2022 | 2022 | 151 | 151 | 134 | 133 | 112.32 | 111.73 | 3787.05 | 2912.1 | 23.97 | 0 | 0 | 6699.15 | 456.93 | 5.64 | 705.45 | 1.3 | 22.87 | 0.07 | 228.54 | 1.95 | 2.42 | 0.05 | 1416.2 | 8115.35 | 176.18 | 49.41 | 46.72 | 225.58 | 8.97 | 2.85 | 33.89 | 99.47 | 28.24 | 60.08 | 46.67 | 82.55 | 79.32 | 10.77 | 14.76 | 9.54 | 11.82 | 5.63 | 8.48 | 10.75 | 19.3 | 47.01 | 82.22 | 78.98 | 10.64 | 14.72 | 12.18 | 5.6
FOSSIL All Fuel Types 200-299 | 2022 | 2022 | 92 | 92 | 230 | 229 | 17.61 | 17.35 | 4961.56 | 2036.29 | 13.85 | 0 | 0 | 6997.85 | 448.42 | 5.96 | 703.3 | 1.6 | 31.51 | 0.13 | 332.4 | 3.3 | 23.32 | 0.14 | 1538.95 | 8536.8 | 235.56 | 60.43 | 54.65 | 295.99 | 8.61 | 4.17 | 285.97 | 98.52 | 37.93 | 64.98 | 58.12 | 81.97 | 78.06 | 8.29 | 12.52 | 10.35 | 12.77 | 5.25 | 9.42 | 12.36 | 18.13 | 58.37 | 82.37 | 78.55 | 8.11 | 12.31 | 12.48 | 5.15
FOSSIL All Fuel Types 300-399 | 2022 | 2022 | 73 | 74 | 341 | 340 | 25.01 | 24.58 | 4204.89 | 2428.05 | 21.47 | 0 | 0 | 6632.93 | 495.74 | 7.07 | 966.68 | 2.05 | 45.57 | 0.23 | 434.1 | 3.49 | 6.81 | 0.04 | 1948.9 | 8581.83 | 252.63 | 54.21 | 61.05 | 306.85 | 11.8 | 5.14 | 171.07 | 98.28 | 27.66 | 57.03 | 49 | 77.29 | 73.49 | 10.55 | 15.72 | 12.17 | 16.93 | 5.78 | 10.91 | 14.25 | 23.4 | 48.51 | 77.43 | 73.67 | 10.66 | 15.81 | 16.79 | 5.78
FOSSIL All Fuel Types 400-599 | 2022 | 2022 | 157 | 157 | 484 | 483 | 18.15 | 17.73 | 4979.26 | 1840.22 | 13.54 | 0 | 8.15 | 6827.63 | 506.76 | 7.37 | 748.86 | 1.45 | 54.89 | 0.19 | 322.2 | 2.98 | 0.99 | 0.02 | 1633.71 | 8461.34 | 227.83 | 47.15 | 48.38 | 274.98 | 9.5 | 3.82 | 280.84 | 97.69 | 39.35 | 66.61 | 58.85 | 80.69 | 77.23 | 9.22 | 13.25 | 11.22 | 13.32 | 5.99 | 9.81 | 12.58 | 18.14 | 59.08 | 80.65 | 77.19 | 9.08 | 13.12 | 13.44 | 5.91
FOSSIL All Fuel Types 600-799 | 2022 | 2022 | 110 | 110 | 662 | 659 | 12.78 | 12.21 | 5431.6 | 1247.91 | 6.71 | 0 | 0 | 6679.51 | 653.48 | 7.55 | 720.47 | 1.14 | 40.21 | 0.16 | 384.59 | 2.65 | 2.87 | 0.04 | 1801.62 | 8481.13 | 298.06 | 51.23 | 73.33 | 349.28 | 8.97 | 4.57 | 444.85 | 95.54 | 47.42 | 73.59 | 64.04 | 78.76 | 74.31 | 10.74 | 15.45 | 13.86 | 13.54 | 7.71 | 12.27 | 16.16 | 20.93 | 64.44 | 78.74 | 74.36 | 10.69 | 15.31 | 13.55 | 7.71
FOSSIL All Fuel Types 800-999 | 2022 | 2022 | 52 | 52 | 828 | 828 | 10.5 | 9.79 | 4501.27 | 2472 | 7.29 | 0 | 0 | 6973.27 | 436.19 | 5.73 | 706.16 | 1.15 | 34.51 | 0.13 | 323.89 | 2.85 | 4.86 | 0.04 | 1505.62 | 8478.88 | 241.29 | 13.75 | 56.99 | 255.03 | 8.74 | 3.88 | 459.78 | 93.24 | 36.42 | 68.19 | 53.09 | 82.24 | 79.2 | 8.83 | 13.56 | 11.12 | 12.61 | 5.14 | 9.02 | 12.02 | 19.14 | 53.41 | 82.45 | 79.42 | 8.53 | 13.23 | 12.57 | 4.98
FOSSIL All Fuel Types 1000 Plus | 2022 | 2022 | 12 | 12 | 1254 | 1251 | 8.33 | 7.92 | 4516.99 | 1205.25 | 3.67 | 0 | 0 | 5722.23 | 676.76 | 5.75 | 1266.59 | 1.17 | 55.69 | 0.33 | 608.44 | 2.83 | 2.21 | 0.08 | 2609.68 | 8331.92 | 334.98 | 95.97 | 39.06 | 430.95 | 15.87 | 7.33 | 570.33 | 95.08 | 36.9 | 67.25 | 54.21 | 68.68 | 63.35 | 13.03 | 19.33 | 17.02 | 23.2 | 8.12 | 15.45 | 19.67 | 28.04 | 54.87 | 68 | 62.61 | 12.86 | 19.2 | 23.91 | 8.1
FOSSIL Coal Primary All Sizes | 2022 | 2022 | 444 | 439.08 | 443 | 441 | 35.16 | 34.77 | 5496.65 | 1031.02 | 5.25 | 0 | 2.91 | 6530.58 | 536.62 | 6.87 | 712 | 1.2 | 41.86 | 0.15 | 320.49 | 2.58 | 7.5 | 0.06 | 1618.47 | 8149.05 | 239.62 | 56.42 | 24.41 | 296.04 | 9.25 | 4.02 | 158.09 | 98.89 | 47.75 | 71.29 | 67.45 | 80.14 | 76.1 | 8.89 | 12.81 | 11.3 | 13.28 | 6.59 | 10.61 | 13.8 | 17.59 | 66.98 | 79.25 | 75.34 | 9.27 | 13.33 | 13.9 | 6.85
FOSSIL Coal Primary 001-099 | 2022 | 2022 | 38 | 37.17 | 54 | 54 | 9.09 | 9.07 | 4222.65 | 707.45 | 4.87 | 0 | 0 | 4930.1 | 243.55 | 5.62 | 739.25 | 1.05 | 52.02 | 0.13 | 76.57 | 0.97 | 0 | 0 | 1111.39 | 6041.49 | 99.02 | 41.74 | 5.72 | 140.76 | 13.1 | 1.27 | 465.56 | 99.78 | 56.65 | 77.03 | 69.89 | 81.6 | 79.16 | 5.45 | 7.66 | 7.07 | 14.36 | 4.03 | 5.3 | 7.46 | 9.91 | 73.54 | 82.88 | 79.79 | 4.61 | 7.47 | 13.57 | 3.56
FOSSIL Coal Primary 100-199 | 2022 | 2022 | 64 | 64 | 138 | 137 | 171.84 | 171.53 | 5262.47 | 1188.68 | 4.02 | 0 | 0 | 6451.15 | 435.04 | 6.08 | 527.79 | 0.91 | 20.4 | 0.13 | 181.3 | 1.44 | 0.26 | 0.02 | 1164.77 | 7615.92 | 239.16 | 97.03 | 10.13 | 336.2 | 7.2 | 2.38 | 30.68 | 99.82 | 46.81 | 68.3 | 69.1 | 84.71 | 79.3 | 7.64 | 11.81 | 9.89 | 9.58 | 5.71 | 8.1 | 11.34 | 14.66 | 68.54 | 84.38 | 79.1 | 7.51 | 11.8 | 10.06 | 5.57
FOSSIL Coal Primary 200-299 | 2022 | 2022 | 59 | 55.25 | 227 | 225 | 11.35 | 11.06 | 5565.48 | 1149.74 | 5.1 | 0 | 0 | 6715.22 | 564.71 | 6.82 | 753.83 | 1.57 | 41.19 | 0.13 | 390.8 | 3.64 | 38.83 | 0.24 | 1789.37 | 8504.59 | 257.98 | 90.18 | 25.15 | 348.16 | 9.35 | 5.05 | 503.21 | 97.44 | 48.41 | 73.57 | 65.44 | 78.96 | 74.27 | 9.21 | 13.37 | 12.03 | 14.4 | 6.64 | 11.69 | 15.01 | 19.39 | 65.8 | 79.68 | 75.05 | 9.14 | 13.32 | 13.7 | 6.62
FOSSIL Coal Primary 300-399 | 2022 | 2022 | 36 | 36.58 | 333 | 331 | 15.09 | 14.71 | 5162.19 | 1316.6 | 8.61 | 0 | 0 | 6478.8 | 731.65 | 7.74 | 856.01 | 1.64 | 43.2 | 0.25 | 514.39 | 3.55 | 13.77 | 0.08 | 2159.01 | 8637.8 | 316.24 | 56.49 | 26.5 | 372.73 | 10.41 | 6.11 | 350.93 | 97.48 | 40.4 | 67.32 | 59.76 | 75.01 | 70.32 | 12.41 | 17.7 | 15.49 | 16.52 | 8.47 | 14.58 | 18.55 | 24.81 | 60.02 | 75.13 | 70.41 | 12.61 | 17.92 | 16.21 | 8.66
FOSSIL Coal Primary 400-599 | 2022 | 2022 | 102 | 101.92 | 491 | 490 | 12.5 | 12.2 | 6038.55 | 919.42 | 5.52 | 0 | 12.55 | 6970.52 | 496.51 | 7.22 | 685.14 | 1.22 | 55.57 | 0.2 | 292.48 | 2.67 | 1.17 | 0.02 | 1530.86 | 8501.38 | 202.81 | 35.78 | 13.55 | 238.58 | 8.71 | 3.45 | 494.96 | 97.6 | 50.06 | 70.29 | 71.03 | 81.99 | 78.94 | 7.58 | 10.66 | 9.83 | 12.17 | 5.84 | 9.29 | 11.77 | 14.59 | 71.22 | 81.94 | 78.86 | 7.43 | 10.51 | 12.33 | 5.73
FOSSIL Coal Primary 600-799 | 2022 | 2022 | 96 | 95.33 | 662 | 659 | 12.03 | 11.49 | 5897.66 | 801.36 | 4.66 | 0 | 0 | 6699.03 | 650.65 | 7.69 | 688.25 | 1.09 | 33.97 | 0.09 | 378.35 | 2.66 | 2.43 | 0.03 | 1753.64 | 8452.67 | 276.89 | 48.87 | 47.08 | 325.75 | 8.54 | 4.5 | 513.29 | 95.51 | 52.49 | 75.14 | 69.77 | 79.25 | 75.04 | 9.94 | 14.06 | 13.07 | 13.05 | 7.7 | 12.2 | 15.9 | 19.26 | 69.86 | 79.34 | 75.23 | 9.87 | 13.91 | 13.01 | 7.65
FOSSIL Coal Primary 800-999 | 2022 | 2022 | 38 | 37.83 | 834 | 834 | 10.7 | 9.86 | 5072.97 | 1624.74 | 6.24 | 0 | 0 | 6697.71 | 529.24 | 5.92 | 733.98 | 1.08 | 45.31 | 0.13 | 360.6 | 3.09 | 6.68 | 0.05 | 1675.81 | 8373.52 | 254.37 | 13.35 | 38.61 | 267.72 | 9.31 | 4.39 | 514.5 | 92.15 | 40.58 | 67 | 60.58 | 79.99 | 76.76 | 9.45 | 13.89 | 12.07 | 13.69 | 6.32 | 10.71 | 13.89 | 19.36 | 60.57 | 80.34 | 77.13 | 9.14 | 13.58 | 13.57 | 6.09
FOSSIL Coal Primary 1000 Plus | 2022 | 2022 | 11 | 11 | 1279 | 1276 | 8.64 | 8.18 | 4891.32 | 643.25 | 2.45 | 0 | 0 | 5534.58 | 736.96 | 6.09 | 1381.73 | 1.27 | 60.75 | 0.36 | 576.57 | 2.91 | 2.41 | 0.09 | 2758.42 | 8293 | 337.69 | 104.7 | 15.2 | 442.39 | 17.39 | 6.98 | 597.96 | 94.68 | 39.48 | 67.4 | 58.98 | 66.74 | 61.23 | 13.09 | 19.04 | 17.62 | 24.38 | 8.89 | 15.87 | 20.15 | 26.86 | 58.59 | 66.46 | 60.93 | 12.91 | 18.97 | 24.86 | 8.68
FOSSIL Oil Primary All Sizes | 2022 | 2022 | 38 | 36.5 | 326 | 325 | 26.66 | 26.33 | 2177.34 | 4618.63 | 28.55 | 0 | 0 | 6795.98 | 427.6 | 4.58 | 592.92 | 1.34 | 23.23 | 0.11 | 399.81 | 1.92 | 0 | 0 | 1443.56 | 8239.53 | 310.1 | 17.43 | 116.15 | 327.53 | 7.48 | 4.85 | 82.69 | 98.76 | 6.05 | 50.69 | 26.43 | 82.48 | 78.44 | 16.41 | 27.11 | 14.27 | 12.33 | 5.19 | 10.04 | 13.97 | 36.88 | 11.93 | 83.21 | 80.43 | 26.27 | 37.74 | 12.54 | 4.25
FOSSIL Oil Primary 001-099 | 2022 | 2022 | 12 | 12 | 71 | 71 | 56.75 | 56.33 | 4127.86 | 1689.86 | 55.08 | 0 | 0 | 5817.71 | 685.31 | 3.83 | 378.03 | 0.33 | 0 | 0 | 418.95 | 2.25 | 0 | 0 | 1482.29 | 7300 | 622.99 | 24.91 | 150.86 | 647.9 | 5.18 | 5.74 | 73.28 | 99.26 | 31.62 | 51.01 | 56.55 | 79.69 | 70.82 | 14.24 | 26.36 | 20.5 | 10.92 | 9.39 | 15.13 | 23.84 | 32.34 | 61.99 | 78.06 | 69.03 | 14.89 | 26.21 | 11.1 | 10.85
FOSSIL Oil Primary 100-199 | 2022 | 2022 | 5 | 5 | 126 | 126 | 8.8 | 8.8 | 3275.86 | 4533.8 | 11.2 | 0 | 0 | 7809.66 | 94.07 | 3.6 | 353.12 | 2 | 0 | 0 | 503.15 | 1.6 | 0 | 0 | 950.34 | 8760 | 259.89 | 3.4 | 23.68 | 263.29 | 4.03 | 5.74 | 372.26 | 100 | 25.08 | 61.32 | 37.4 | 89.15 | 86.15 | 2.79 | 10.43 | 5.86 | 9.77 | 1.07 | 6.82 | 9.81 | 22.05 | 40.91 | 89.32 | 85.94 | 2.57 | 10.44 | 9.6 | 1.08
FOSSIL Oil Primary 200-299 | 2022 | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FOSSIL Oil Primary 300-399 | 2022 | 2022 | 7 | 6.08 | 359 | 357 | 13.32 | 12.66 | 1381.07 | 5468.54 | 14.47 | 0 | 0 | 6849.6 | 230.24 | 4.77 | 986.29 | 2.63 | 0 | 0 | 573.87 | 2.47 | 0 | 0 | 1790.4 | 8640 | 22.46 | 52.62 | 6.02 | 75.08 | 11.42 | 6.64 | 109.09 | 95.05 | 7.07 | 45.45 | 15.98 | 79.28 | 78.32 | 14.29 | 15.62 | 10.96 | 18.06 | 2.66 | 9.31 | 10.17 | 40.11 | 15.56 | 79.63 | 78.7 | 14.43 | 15.87 | 17.74 | 2.62
FOSSIL Oil Primary 400-599 | 2022 | 2022 | 6 | 5.92 | 464 | 463 | 14.87 | 14.87 | 371.24 | 6629.31 | 19.77 | 0 | 0 | 7000.56 | 475.7 | 6.59 | 940.04 | 1.86 | 100.65 | 0.34 | 244.74 | 1.69 | 0 | 0 | 1761.13 | 8761.69 | 10.36 | 0 | 3.41 | 10.36 | 11.88 | 2.79 | 24.97 | 100 | 2.11 | 49.19 | 4.24 | 79.9 | 79.7 | 56.17 | 57.16 | 26.97 | 14.67 | 5.43 | 8.22 | 8.34 | 66.73 | 4.3 | 79.63 | 79.41 | 56.89 | 57.9 | 14.7 | 5.67
FOSSIL Oil Primary 600-799 | 2022 | 2022 | 4 | 3.5 | 596 | 596 | 17.43 | 17.43 | 647.13 | 6775.45 | 20.86 | 0 | 0 | 7422.57 | 571.64 | 6.57 | 477.41 | 1.14 | 72.09 | 0.57 | 0 | 0 | 0 | 0 | 1121.14 | 8543.71 | 182.09 | 0 | 164 | 182.09 | 6.43 | 0 | 37.13 | 100 | 3.88 | 50.61 | 7.57 | 86.88 | 84.67 | 46.9 | 54.51 | 25.15 | 6.43 | 6.69 | 6.69 | 8.82 | 54.51 | 7.67 | 86.93 | 84.75 | 46.36 | 53.94 | 6.44 | 6.63
FOSSIL Oil Primary 800-999 | 2022 | 2022 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
FOSSIL Oil Primary 1000 Plus | 2022 | 2022 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
FOSSIL Gas Primary All Sizes | 2022 | 2022 | 263 | 257.33 | 242 | 242 | 46.57 | 45.99 | 2478.88 | 3976.31 | 31.74 | 0 | 0 | 6455.2 | 596.96 | 5.56 | 886.3 | 1.7 | 33.19 | 0.11 | 310.12 | 2.7 | 1.68 | 0.03 | 1828.25 | 8283.44 | 188.76 | 28.02 | 109.3 | 216.78 | 11.1 | 3.76 | 53.9 | 98.75 | 13.77 | 43.16 | 29.93 | 77.93 | 75.16 | 19.41 | 24.67 | 13.93 | 14.86 | 7.21 | 10.97 | 13.35 | 31.56 | 31.91 | 78.58 | 74.99 | 15.49 | 22.36 | 15.57 | 5.85
FOSSIL Gas Primary 001-099 | 2022 | 2022 | 64 | 60.33 | 54 | 53 | 41.02 | 40.77 | 1354.48 | 3942.81 | 19.72 | 0 | 0 | 5297.29 | 1059.66 | 3.75 | 926.78 | 1.43 | 16.93 | 0.03 | 272.84 | 1.24 | 0 | 0 | 2276.2 | 7573.49 | 116.75 | 0.19 | 91.34 | 116.94 | 12.46 | 3.6 | 33.22 | 99.39 | 10.77 | 51.55 | 17.88 | 69.95 | 67.97 | 43.89 | 46.95 | 21.62 | 16.06 | 13.99 | 17.59 | 19.14 | 52.16 | 20.89 | 70.34 | 68.13 | 40.7 | 43.87 | 15.32 | 14.34
FOSSIL Gas Primary 100-199 | 2022 | 2022 | 80 | 80 | 130 | 130 | 73.93 | 73.08 | 2544.83 | 4262.29 | 41.33 | 0 | 0 | 6807.12 | 508.12 | 5.54 | 861.55 | 1.6 | 26.84 | 0.04 | 250.5 | 2.41 | 4.36 | 0.08 | 1651.37 | 8458.49 | 122.92 | 10.72 | 78.6 | 133.63 | 10.5 | 3.01 | 34.82 | 98.85 | 13.93 | 46.38 | 30.09 | 80.48 | 78.79 | 16.64 | 20.15 | 10.66 | 13.52 | 6.01 | 9.02 | 10.55 | 26.34 | 30.03 | 80.19 | 78.45 | 16.78 | 20.33 | 13.76 | 6.06
FOSSIL Gas Primary 200-299 | 2022 | 2022 | 32 | 30.75 | 235 | 234 | 28.55 | 28.33 | 3374.32 | 3979.9 | 29.76 | 0 | 0 | 7354.21 | 286.08 | 4.29 | 626.68 | 1.46 | 18.46 | 0.13 | 265.68 | 2.99 | 0 | 0 | 1196.91 | 8551.12 | 201.81 | 15.5 | 114.59 | 217.31 | 7.54 | 3.11 | 119.11 | 99.23 | 16.08 | 40.04 | 39.46 | 86 | 83.44 | 7.82 | 12.92 | 8.38 | 10.65 | 3.35 | 6.45 | 8.85 | 18.72 | 40.15 | 85.75 | 83.29 | 7.35 | 12.22 | 11.06 | 3.19
FOSSIL Gas Primary 300-399 | 2022 | 2022 | 28 | 27.42 | 348 | 347 | 37.9 | 37.42 | 3642.72 | 3273.6 | 36.95 | 0 | 0 | 6916.33 | 306.43 | 7.33 | 1150.99 | 2.55 | 64.83 | 0.26 | 323.11 | 4.01 | 0 | 0 | 1845.35 | 8761.68 | 252.76 | 50.33 | 126.97 | 303.09 | 13.88 | 3.69 | 97.35 | 98.73 | 16.94 | 41.2 | 41.58 | 78.94 | 75.38 | 7.76 | 13.72 | 9.55 | 17.56 | 3.5 | 7.19 | 10.58 | 20.83 | 41.12 | 78.94 | 75.5 | 7.77 | 13.62 | 17.59 | 3.46
FOSSIL Gas Primary 400-599 | 2022 | 2022 | 43 | 43 | 477 | 476 | 32.7 | 31.93 | 2813.11 | 3577.49 | 33 | 0 | 0 | 6390.6 | 548.4 | 7.88 | 864.5 | 1.93 | 48.72 | 0.14 | 430.52 | 4.09 | 0 | 0 | 1892.14 | 8282.74 | 305.17 | 82.82 | 144.07 | 387.99 | 11.03 | 5.2 | 88.1 | 97.65 | 14.35 | 42.69 | 33.96 | 77.16 | 72.42 | 16.31 | 24.35 | 15.84 | 16.22 | 6.62 | 11.82 | 15.6 | 32.73 | 33.62 | 77.11 | 72.43 | 16.34 | 24.57 | 16.32 | 6.57
FOSSIL Gas Primary 600-799 | 2022 | 2022 | 10 | 10 | 682 | 680 | 18.3 | 17.2 | 2591.57 | 3632.64 | 21.4 | 0 | 0 | 6224.21 | 698.05 | 6.2 | 1127.1 | 1.5 | 93.19 | 0.7 | 609 | 3.5 | 8.44 | 0.1 | 2535.79 | 8760 | 517.73 | 92.48 | 300.45 | 610.21 | 13.93 | 7.05 | 150.67 | 93.99 | 14.85 | 46.46 | 29.58 | 71.05 | 63.92 | 21.22 | 33.87 | 22.46 | 20.98 | 7.97 | 15.02 | 20.93 | 43.57 | 31.96 | 70.6 | 63.36 | 20.92 | 32.83 | 20.95 | 8.46
FOSSIL Gas Primary 800-999 | 2022 | 2022 | 6 | 5.83 | 797 | 797 | 15.26 | 15.09 | 356.89 | 7213.79 | 19.03 | 0 | 0 | 7570.68 | 218.67 | 4.8 | 679.39 | 1.71 | 0 | 0 | 286.46 | 2.4 | 0 | 0 | 1184.52 | 8755.2 | 44.8 | 0 | 21.27 | 44.8 | 7.76 | 3.27 | 23.65 | 98.89 | 1.22 | 30.62 | 4.08 | 86.47 | 85.96 | 37.99 | 44.14 | 18.67 | 11.03 | 2.5 | 5.77 | 6.28 | 62.26 | 4 | 86.29 | 85.78 | 37.01 | 43.4 | 11.36 | 2.35
FOSSIL Gas Primary 1000 Plus | 2022 | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FOSSIL Oil/Gas Primary All Sizes | 2022 | 2022 | 301 | 293.83 | 253 | 252 | 44.1 | 43.55 | 2441.43 | 4056.1 | 31.34 | 0 | 0 | 6497.53 | 575.92 | 5.44 | 849.85 | 1.65 | 31.95 | 0.11 | 321.26 | 2.6 | 1.47 | 0.02 | 1780.46 | 8277.99 | 203.83 | 26.71 | 110.15 | 230.54 | 10.65 | 3.9 | 56.06 | 98.75 | 12.52 | 43.67 | 29.49 | 78.49 | 75.56 | 19.09 | 24.93 | 13.95 | 14.55 | 6.96 | 10.86 | 13.43 | 32.15 | 28.67 | 79.33 | 75.87 | 16.32 | 23.61 | 15.08 | 5.59
FOSSIL Oil/Gas Primary 001-099 | 2022 | 2022 | 76 | 72.33 | 56 | 56 | 43.63 | 43.35 | 1814.58 | 3569.05 | 25.59 | 0 | 0 | 5383.63 | 997.55 | 3.76 | 835.74 | 1.24 | 14.12 | 0.03 | 297.08 | 1.41 | 0 | 0 | 2144.49 | 7528.12 | 200.73 | 4.29 | 101.21 | 205.03 | 11.29 | 3.95 | 41.86 | 99.36 | 15.1 | 51.31 | 24.1 | 71.51 | 68.43 | 35.47 | 41.13 | 21.12 | 15.24 | 13.25 | 17.2 | 19.89 | 46.65 | 29.43 | 71.94 | 68.31 | 31.63 | 37.73 | 14.44 | 13.62
FOSSIL Oil/Gas Primary 100-199 | 2022 | 2022 | 85 | 85 | 130 | 130 | 70.09 | 69.29 | 2587.83 | 4278.26 | 39.55 | 0 | 0 | 6866.09 | 483.77 | 5.42 | 831.64 | 1.62 | 25.26 | 0.04 | 265.36 | 2.36 | 4.1 | 0.07 | 1610.13 | 8476.22 | 130.97 | 10.29 | 75.37 | 141.26 | 10.11 | 3.18 | 37.35 | 98.86 | 14.58 | 47.55 | 30.53 | 81 | 79.24 | 15.75 | 19.53 | 10.41 | 13.29 | 5.71 | 8.89 | 10.5 | 26.05 | 30.67 | 80.72 | 78.89 | 15.82 | 19.67 | 13.51 | 5.76
FOSSIL Oil/Gas Primary 200-299 | 2022 | 2022 | 32 | 30.75 | 235 | 234 | 28.55 | 28.33 | 3374.32 | 3979.9 | 29.76 | 0 | 0 | 7354.21 | 286.08 | 4.29 | 626.68 | 1.46 | 18.46 | 0.13 | 265.68 | 2.99 | 0 | 0 | 1196.91 | 8551.12 | 201.81 | 15.5 | 114.59 | 217.31 | 7.54 | 3.11 | 119.11 | 99.23 | 16.08 | 40.04 | 39.46 | 86 | 83.44 | 7.82 | 12.92 | 8.38 | 10.65 | 3.35 | 6.45 | 8.85 | 18.72 | 40.15 | 85.75 | 83.29 | 7.35 | 12.22 | 11.06 | 3.19
FOSSIL Oil/Gas Primary 300-399 | 2022 | 2022 | 35 | 33.5 | 350 | 349 | 33.43 | 32.93 | 3232.03 | 3672.18 | 32.87 | 0 | 0 | 6904.21 | 292.59 | 6.87 | 1121.08 | 2.57 | 53.05 | 0.21 | 368.65 | 3.73 | 0 | 0 | 1835.37 | 8739.58 | 210.94 | 50.75 | 105 | 261.68 | 13.43 | 4.22 | 98.15 | 98.5 | 15.12 | 41.53 | 36.98 | 79 | 75.91 | 8.3 | 13.87 | 9.31 | 17.65 | 3.35 | 7.57 | 10.51 | 22.73 | 36.42 | 79.07 | 76.09 | 8.33 | 13.8 | 17.62 | 3.31
FOSSIL Oil/Gas Primary 400-599 | 2022 | 2022 | 49 | 48.92 | 475 | 475 | 30.54 | 29.87 | 2517.76 | 3946.62 | 31.4 | 0 | 0 | 6464.38 | 539.61 | 7.73 | 873.64 | 1.92 | 55 | 0.16 | 408.05 | 3.8 | 0 | 0 | 1876.3 | 8340.67 | 269.51 | 72.8 | 127.05 | 342.32 | 11.13 | 4.89 | 84.29 | 97.81 | 12.84 | 42.81 | 30.19 | 77.5 | 73.35 | 17.65 | 25.41 | 15.89 | 16.03 | 6.47 | 11.36 | 14.68 | 33.98 | 30 | 77.42 | 73.29 | 17.71 | 25.65 | 16.12 | 6.46
FOSSIL Oil/Gas Primary 600-799 | 2022 | 2022 | 14 | 13.5 | 660 | 658 | 18.07 | 17.26 | 2087.46 | 4447.44 | 21.26 | 0 | 0 | 6534.9 | 665.28 | 6.3 | 958.66 | 1.41 | 87.72 | 0.67 | 451.11 | 2.59 | 6.25 | 0.07 | 2169.03 | 8703.93 | 430.71 | 68.5 | 265.07 | 499.21 | 12.02 | 5.25 | 120.94 | 95.52 | 12.32 | 46.73 | 23.98 | 75.08 | 69.2 | 24.17 | 36.32 | 22.01 | 17.28 | 7.64 | 12.9 | 17.85 | 44.7 | 26.37 | 74.35 | 68.28 | 23.36 | 34.93 | 17.61 | 8.04
FOSSIL Oil/Gas Primary 800-999 | 2022 | 2022 | 9 | 8.83 | 801 | 800 | 11.55 | 11.09 | 269.32 | 7259.07 | 15.96 | 0 | 0 | 7528.39 | 221.71 | 4.3 | 687.17 | 1.58 | 0 | 0 | 319.57 | 2.49 | 0 | 0 | 1228.44 | 8756.83 | 188.42 | 0 | 170.11 | 188.42 | 7.85 | 3.65 | 24.28 | 96.02 | 0.92 | 30.48 | 3.08 | 85.97 | 83.73 | 45.15 | 62.03 | 23.71 | 11.5 | 2.53 | 6.18 | 8.33 | 74.41 | 3.02 | 85.87 | 83.65 | 44.5 | 61.76 | 11.72 | 2.42
FOSSIL Oil/Gas Primary 1000 Plus | 2022 | 2022 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
FOSSIL Lignite Primary All Sizes | 2022 | 2022 | 16 | 14.25 | 559 | 556 | 11.44 | 11.09 | 7489.09 | 104.28 | 2.53 | 0 | 0 | 7593.37 | 353.95 | 7.58 | 607.57 | 1.33 | 24.21 | 0.28 | 121.62 | 1.89 | 4.81 | 0.14 | 1112.15 | 8705.52 | 293.84 | 40.01 | 0 | 333.85 | 7.26 | 1.45 | 675.3 | 96.94 | 66.93 | 77.35 | 86.03 | 87.22 | 82.6 | 4.51 | 8.26 | 8.16 | 8.71 | 4.07 | 5.52 | 9.11 | 9.95 | 86.52 | 87.66 | 83.46 | 3.93 | 7.69 | 8.8 | 3.54
NUCLEAR All Types All Sizes | 2022 | 2022 | 92 | 92 | 1040 | 1035 | 1.4 | 1.38 | 8036.32 | 2.53 | 0.01 | 0 | 0 | 8038.85 | 110.96 | 0.66 | 497.84 | 0.9 | 31.6 | 0.15 | 24.93 | 0.16 | 0 | 0 | 665.32 | 8704.17 | 36.81 | 80.7 | 0 | 117.51 | 6.08 | 0.29 | 5823.42 | 98.57 | 91.35 | 98.95 | 92.33 | 92.36 | 90.54 | 1.36 | 1.81 | 1.81 | 6.37 | 1.27 | 1.56 | 2.34 | 2.49 | 92.32 | 92.35 | 90.55 | 1.36 | 1.83 | 6.38 | 1.27
NUCLEAR All Types 400-799 | 2022 | 2022 | 8 | 8 | 622 | 616 | 1 | 1 | 8007.72 | 0 | 0 | 0 | 0 | 8007.72 | 162.79 | 0.63 | 578.84 | 0.88 | 0 | 0 | 10.65 | 0.25 | 0 | 0 | 752.28 | 8760 | 13.11 | 87.79 | 0 | 100.9 | 6.61 | 0.12 | 8007.72 | 100 | 89.64 | 98.77 | 91.41 | 91.41 | 89.21 | 1.99 | 2.15 | 2.15 | 6.73 | 1.86 | 1.98 | 2.29 | 2.46 | 90.75 | 90.75 | 88.68 | 2.31 | 2.47 | 7.1 | 2.15
NUCLEAR All Types 800-999 | 2022 | 2022 | 32 | 32 | 895 | 892 | 1.47 | 1.44 | 7952.58 | 0 | 0 | 0 | 0 | 7952.58 | 104.14 | 0.69 | 447.23 | 0.81 | 69.72 | 0.19 | 25.84 | 0.13 | 0 | 0 | 646.92 | 8599.5 | 28.58 | 87.52 | 0 | 116.1 | 6.01 | 0.3 | 5522.63 | 97.96 | 92.07 | 99.49 | 92.48 | 92.48 | 90.8 | 1.29 | 1.65 | 1.65 | 6.31 | 1.21 | 1.51 | 2.2 | 2.34 | 92.55 | 92.55 | 90.89 | 1.28 | 1.64 | 6.25 | 1.2
NUCLEAR All Types 1000 Plus | 2022 | 2022 | 52 | 52 | 1193 | 1187 | 1.42 | 1.4 | 8092.25 | 4.48 | 0.02 | 0 | 0 | 8096.73 | 107.18 | 0.65 | 516.53 | 0.96 | 13 | 0.15 | 26.57 | 0.17 | 0 | 0 | 663.27 | 8760 | 45.53 | 75.41 | 0 | 120.94 | 6.04 | 0.3 | 5780.18 | 98.59 | 91.16 | 98.72 | 92.38 | 92.43 | 90.59 | 1.31 | 1.86 | 1.86 | 6.35 | 1.22 | 1.53 | 2.43 | 2.59 | 92.34 | 92.39 | 90.55 | 1.31 | 1.87 | 6.38 | 1.23
NUCLEAR PWR All Sizes | 2022 | 2022 | 54 | 54 | 1048 | 1043 | 1.35 | 1.31 | 8091.23 | 4.31 | 0.02 | 0 | 0 | 8095.54 | 110.29 | 0.65 | 515.62 | 0.85 | 32.17 | 0.15 | 6.38 | 0.06 | 0 | 0 | 664.46 | 8760 | 25.73 | 51.3 | 0 | 77.03 | 6.25 | 0.07 | 6176.51 | 97.04 | 92.22 | 99.82 | 92.37 | 92.41 | 91.08 | 1.34 | 1.66 | 1.66 | 6.33 | 1.26 | 1.33 | 1.75 | 1.87 | 92.38 | 92.43 | 91.16 | 1.27 | 1.59 | 6.38 | 1.19
NUCLEAR PWR 400-799 | 2022 | 2022 | 4 | 4 | 608 | 601 | 1 | 1 | 8247.06 | 0 | 0 | 0 | 0 | 8247.06 | 175.05 | 0.75 | 335.93 | 0.5 | 0 | 0 | 1.96 | 0.25 | 0 | 0 | 512.94 | 8760 | 11.48 | 138.19 | 0 | 149.67 | 3.83 | 0.02 | 8247.06 | 100 | 93.36 | 100.05 | 94.14 | 94.14 | 91.29 | 2.08 | 2.21 | 2.21 | 3.86 | 2 | 2.02 | 2.17 | 2.26 | 93.32 | 93.32 | 90.74 | 2.6 | 2.74 | 4.19 | 2.5
NUCLEAR PWR 800-999 | 2022 | 2022 | 17 | 17 | 893 | 891 | 1.53 | 1.47 | 8015.79 | 0 | 0 | 0 | 0 | 8015.79 | 141.56 | 0.71 | 526.79 | 0.82 | 75.86 | 0.12 | 0 | 0 | 0 | 0 | 744.21 | 8760 | 13.36 | 58.05 | 0 | 71.41 | 6.88 | 0 | 5452.92 | 96.08 | 91.89 | 100.36 | 91.5 | 91.5 | 90.46 | 1.74 | 1.9 | 1.9 | 6.88 | 1.62 | 1.62 | 1.9 | 2.04 | 91.56 | 91.56 | 90.51 | 1.72 | 1.88 | 6.84 | 1.6
NUCLEAR PWR 1000 Plus | 2022 | 2022 | 33 | 33 | 1182 | 1176 | 1.3 | 1.27 | 8111.2 | 7.06 | 0.03 | 0 | 0 | 8118.26 | 86.33 | 0.61 | 531.65 | 0.91 | 13.57 | 0.18 | 10.19 | 0.06 | 0 | 0 | 641.74 | 8760 | 33.83 | 37.29 | 0 | 71.12 | 6.22 | 0.12 | 6386.77 | 97.69 | 92.27 | 99.61 | 92.59 | 92.67 | 91.37 | 1.05 | 1.47 | 1.46 | 6.34 | 0.99 | 1.1 | 1.63 | 1.74 | 92.64 | 92.72 | 91.44 | 1.02 | 1.4 | 6.33 | 0.95
NUCLEAR BWR All Sizes | 2022 | 2022 | 28 | 28 | 1069 | 1064 | 1.54 | 1.54 | 8233.69 | 0 | 0 | 0 | 0 | 8233.69 | 116.19 | 0.71 | 353.08 | 0.82 | 15.59 | 0.11 | 41.45 | 0.32 | 0 | 0 | 526.31 | 8760 | 55.71 | 141.36 | 0 | 197.07 | 4.21 | 0.47 | 5346.55 | 100 | 91.57 | 97.84 | 93.99 | 93.99 | 91.32 | 1.39 | 2.06 | 2.06 | 4.68 | 1.33 | 1.8 | 3.21 | 3.35 | 93.59 | 93.59 | 90.89 | 1.56 | 2.27 | 4.92 | 1.49
NUCLEAR BWR 400-799 | 2022 | 2022 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
NUCLEAR BWR 800-999 | 2022 | 2022 | 9 | 9 | 894 | 890 | 1.44 | 1.44 | 8265.64 | 0 | 0 | 0 | 0 | 8265.64 | 58.77 | 0.67 | 386.38 | 0.78 | 24.16 | 0.22 | 25.06 | 0.22 | 0 | 0 | 494.36 | 8760 | 50.22 | 141.17 | 0 | 191.39 | 4.69 | 0.29 | 5740.03 | 100 | 93.73 | 99.23 | 94.36 | 94.36 | 91.69 | 0.71 | 1.31 | 1.31 | 4.97 | 0.67 | 0.96 | 2.19 | 2.3 | 94.45 | 94.45 | 91.85 | 0.7 | 1.32 | 4.88 | 0.66
NUCLEAR BWR 1000 Plus | 2022 | 2022 | 17 | 17 | 1212 | 1208 | 1.71 | 1.71 | 8159.4 | 0 | 0 | 0 | 0 | 8159.4 | 160.26 | 0.82 | 376.99 | 0.94 | 12.88 | 0.06 | 50.46 | 0.35 | 0 | 0 | 600.6 | 8760 | 61.71 | 151.69 | 0 | 213.4 | 4.45 | 0.58 | 4771.58 | 100 | 90.34 | 97.26 | 93.14 | 93.14 | 90.4 | 1.93 | 2.67 | 2.67 | 5.03 | 1.83 | 2.41 | 3.97 | 4.15 | 92.88 | 92.88 | 90.11 | 2 | 2.77 | 5.22 | 1.9
NUCLEAR CANDU All Sizes | 2022 | 2022 | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | * | [10 empty] | * | * | * | * | * | * | * | * | * | * | * | * | * | * | bar: POF to FOR
JET ENGINE All Sizes | 2022 | 2022 | 176 | 168.67 | 41 | 40 | 93.53 | 92.45 | 530.24 | 7134.16 | 97.44 | 0 | 45.46 | 7709.87 | 286.43 | 6.47 | 456.03 | 2.55 | 21.49 | 0.03 | 280.56 | 4.19 | 6.28 | 0.05 | 1050.8 | 8760.66 | 95.43 | 13.77 | 87.9 | 109.2 | 5.45 | 3.27 | 5.74 | 98.85 | 6.44 | 84.09 | 6.05 | 88.01 | 84.25 | 33.22 | 40.19 | 9.54 | 8.72 | 3.27 | 6.54 | 7.74 | 54.12 | 7.66 | 87.1 | 81.99 | 29.79 | 37.76 | 9.42 | 3.49
JET ENGINE 001-019 | 2022 | 2022 | 17 | 17 | 14 | 14 | 16.65 | 16.29 | 52.68 | 7890.33 | 24.24 | 0 | 0 | 7943.01 | 172.3 | 3.18 | 25.49 | 0.06 | 0 | 0 | 619.2 | 4.65 | 0 | 0 | 816.99 | 8760 | 4.1 | 0.31 | 3.28 | 4.41 | 0.29 | 7.07 | 3.23 | 97.84 | 0.48 | 73.86 | 0.6 | 90.67 | 90.62 | 76.58 | 77.28 | 16.95 | 7.36 | 1.97 | 9.04 | 9.09 | 93.92 | 0.65 | 90.06 | 90.01 | 75.83 | 76.49 | 7.9 | 2.04
JET ENGINE 20 Plus | 2022 | 2022 | 159 | 151.67 | 44 | 43 | 102.15 | 100.99 | 583.77 | 7049.4 | 105.65 | 0 | 50.56 | 7683.73 | 299.22 | 6.84 | 504.29 | 2.83 | 23.9 | 0.03 | 242.61 | 4.13 | 6.98 | 0.05 | 1077 | 8760.74 | 105.66 | 15.28 | 97.38 | 120.94 | 6.03 | 2.85 | 5.78 | 98.86 | 6.64 | 84.12 | 6.66 | 87.71 | 83.53 | 32.05 | 39.27 | 9.6 | 8.88 | 3.42 | 6.26 | 7.59 | 51.21 | 7.9 | 86.99 | 81.71 | 29.44 | 37.48 | 9.47 | 3.54
GAS TURBINE All Sizes | 2022 | 2022 | 534 | 534.42 | 70 | 68 | 60.4 | 59.45 | 547.36 | 7088.73 | 64.63 | 0 | 0 | 7636.09 | 400.88 | 5.03 | 480.93 | 1.74 | 12.12 | 0.03 | 169.02 | 2.68 | 5.55 | 0.02 | 1068.48 | 8704.57 | 48.9 | 6.15 | 44.15 | 55.05 | 5.66 | 2.01 | 9.21 | 98.43 | 5.91 | 69.74 | 6.29 | 87.73 | 84.33 | 42.28 | 45.32 | 11.21 | 7.67 | 4.61 | 6.61 | 7.21 | 53.49 | 8.48 | 87.79 | 83.95 | 30.67 | 34.17 | 8.46 | 3.75
GAS TURBINE 001-019 | 2022 | 2022 | 59 | 59 | 15 | 15 | 35.71 | 33.98 | 186.72 | 7551.12 | 41.05 | 0 | 0 | 7737.84 | 404.54 | 3.95 | 189.57 | 0.58 | 0 | 0 | 196.76 | 3.39 | 44.96 | 0.14 | 835.84 | 8573.68 | 0.52 | 11.48 | 0.43 | 12 | 2.21 | 2.82 | 5.49 | 95.16 | 0.87 | 40.29 | 2.18 | 90.25 | 89.07 | 68.42 | 68.46 | 13.79 | 5.03 | 4.72 | 7.54 | 7.54 | 77.61 | 2.17 | 90.76 | 89.53 | 67.8 | 67.84 | 4.68 | 4.57
GAS TURBINE 020-049 | 2022 | 2022 | 102 | 102 | 30 | 29 | 52.3 | 51.78 | 331.69 | 7135.57 | 59.45 | 0 | 0 | 7467.26 | 629.03 | 5.75 | 409.81 | 1.73 | 1.37 | 0.01 | 183.8 | 3.6 | 0 | 0 | 1224.01 | 8691.27 | 20.45 | 0.11 | 19.4 | 20.56 | 4.73 | 2.11 | 6.41 | 99.01 | 4.05 | 83.68 | 3.82 | 85.92 | 83.05 | 65.47 | 66.27 | 15.56 | 6.85 | 7.24 | 9.35 | 9.59 | 71.6 | 4.84 | 86.63 | 83.79 | 55.91 | 56.73 | 7.23 | 6.13
GAS TURBINE 50 Plus | 2022 | 2022 | 373 | 373.42 | 90 | 86 | 66.51 | 65.56 | 663.24 | 7002.88 | 69.76 | 0 | 0 | 7666.13 | 337.98 | 5 | 546.39 | 1.93 | 16.97 | 0.04 | 160.59 | 2.32 | 0.83 | 0 | 1062.76 | 8728.88 | 64.32 | 6.96 | 57.81 | 71.28 | 6.45 | 1.85 | 10.12 | 98.57 | 6.22 | 69.24 | 7.6 | 87.82 | 83.93 | 33.76 | 37.99 | 9.9 | 8.3 | 3.87 | 5.72 | 6.51 | 46.23 | 8.98 | 87.82 | 83.82 | 28.09 | 31.93 | 8.67 | 3.51
COMBINED CYCLE All Sizes | 2022 | 2022 | 296 | 289.67 | 322 | 316 | 64.84 | 64.29 | 5042.74 | 2312.16 | 57.69 | 0 | 0 | 7354.89 | 335.85 | 5.79 | 789.12 | 2.39 | 38.83 | 0.21 | 145.27 | 2.07 | 0.57 | 0.02 | 1309.63 | 8664.52 | 59.8 | 53.04 | 17.83 | 112.84 | 9.56 | 1.68 | 78.44 | 99.15 | 57.04 | 82.34 | 58.2 | 84.89 | 81.4 | 6.24 | 7.33 | 5.71 | 11.24 | 3.88 | 5.56 | 6.52 | 10.16 | 69.27 | 86.4 | 82.65 | 3.81 | 5.08 | 10.86 | 2.74
HYDRO All Sizes | 2022 | 2022 | 814 | 814 | 63 | 63 | 76.92 | 76.84 | 5094.57 | 1595.34 | 42.2 | 7.1 | 196.8 | 6893.8 | 566.29 | 3.31 | 975.3 | 2.52 | 26.66 | 0.02 | 190.44 | 2.33 | 10.94 | 0.01 | 1769.62 | 8663.43 | 13.62 | 13.59 | 4.97 | 27.21 | 11.57 | 2.32 | 66.3 | 99.9 | 34.97 | 58.34 | 58.81 | 79.57 | 78.89 | 9.66 | 9.88 | 8.18 | 13.89 | 6.54 | 8.86 | 9.03 | 12.88 | 59.95 | 81.65 | 81.04 | 5.28 | 5.42 | 14.88 | 3.47
HYDRO 001-029 | 2022 | 2022 | 306 | 306 | 11 | 11 | 26.47 | 26.38 | 4879.22 | 1306.95 | 17.96 | 13.06 | 141.22 | 6340.45 | 993.19 | 5.23 | 879.08 | 1.86 | 20.26 | 0.03 | 269.65 | 2.32 | 0.47 | 0.01 | 2162.65 | 8503.1 | 18.27 | 6.22 | 0.24 | 24.49 | 10.58 | 3.18 | 184.96 | 99.66 | 28.53 | 49.93 | 57.38 | 74.57 | 74.15 | 16.48 | 16.78 | 14.63 | 13.75 | 11.68 | 14.86 | 15.07 | 20.35 | 57.14 | 76.84 | 76.39 | 13.29 | 13.77 | 13.97 | 9.19
HYDRO 30 Plus | 2022 | 2022 | 508 | 508 | 94 | 94 | 107.31 | 107.23 | 5224.28 | 1769.05 | 56.81 | 3.52 | 230.27 | 7227.12 | 309.14 | 2.15 | 1033.25 | 2.92 | 30.52 | 0.01 | 142.72 | 2.34 | 17.24 | 0 | 1532.88 | 8760 | 10.82 | 18.02 | 7.81 | 28.85 | 12.14 | 1.83 | 48.72 | 99.93 | 35.45 | 58.92 | 59.64 | 82.5 | 81.67 | 5.36 | 5.54 | 4.49 | 13.97 | 3.53 | 5.36 | 5.49 | 8.1 | 60.16 | 82 | 81.38 | 4.65 | 4.77 | 14.95 | 3.05
PUMPED STORAGE All Sizes | 2022 | 2022 | 106 | 106 | 135 | 134 | 234.97 | 234.73 | 2063.34 | 3605.54 | 205.01 | 981.1 | 285.81 | 6935.78 | 552.84 | 2.91 | 952.05 | 2.4 | 14.88 | 0.1 | 302.94 | 5.11 | 1.51 | 0.01 | 1824.22 | 8760 | 1.73 | 0.58 | 1.15 | 2.31 | 11.04 | 3.48 | 8.79 | 99.9 | 8.88 | 53.46 | 23.55 | 79.18 | 79 | 14.24 | 14.28 | 9.32 | 14.51 | 6.31 | 9.79 | 9.81 | 20.51 | 16.62 | 78.73 | 78.28 | 12.46 | 12.51 | 16.47 | 4.8
MULTIBOILER/MULTI-TURBINE All Sizes | 2022 | 2022 | 15 | 15 | 242 | 239 | 14.27 | 13.87 | 4356.32 | 2042.31 | 12.93 | 0 | 0 | 6398.62 | 764.7 | 2.93 | 928.69 | 2.53 | 48.45 | 0.2 | 288.27 | 2.07 | 0 | 0 | 2030.11 | 8428.73 | 499.28 | 150.56 | 51.62 | 649.84 | 11.59 | 3.42 | 314.08 | 97.2 | 21.87 | 50.41 | 51.68 | 75.91 | 66.27 | 14.93 | 24.44 | 18.81 | 15.01 | 9.07 | 12.49 | 18.72 | 28.7 | 43.39 | 72.96 | 63.39 | 9.64 | 20.78 | 22.41 | 4.63
GEOTHERMAL All Sizes | 2022 | 2022 | 45 | 44.67 | 34 | 33 | 5.57 | 5.37 | 7972.95 | 0 | 0 | 0 | 0 | 7972.95 | 182.84 | 3.92 | 60.72 | 0.36 | 22.66 | 0.07 | 129.51 | 1.63 | 0 | 0 | 395.73 | 8368.68 | 43.7 | 20.53 | 0 | 64.23 | 1 | 1.55 | 1484.72 | 96.41 | 74.36 | 78.64 | 95.27 | 95.27 | 90.79 | 2.24 | 2.78 | 2.78 | 2.54 | 2.18 | 3.73 | 4.33 | 4.38 | 94.55 | 94.55 | 90.8 | 2.53 | 3.03 | 3 | 2.45
DIESEL All Sizes | 2022 | 2022 | 179 | 179 | 12 | 12 | 233.69 | 232.53 | 1920.37 | 6065.33 | 198.12 | 0 | 0 | 7985.7 | 263.63 | 9.07 | 279.98 | 1.97 | 0 | 0 | 132.79 | 3.41 | 0.01 | 0.01 | 676.42 | 8662.12 | 22.85 | 26.35 | 13.17 | 49.2 | 3.23 | 1.53 | 8.26 | 99.5 | 19.64 | 63.31 | 22.17 | 92.19 | 91.55 | 12.07 | 13.04 | 5.18 | 4.77 | 3.04 | 4.58 | 4.96 | 18.36 | 31.02 | 94.52 | 92.3 | 6.96 | 9.15 | 3.16 | 2.32
* - indicates 3 or fewer units in results