## Brochure 1 2015
2015 Generating Unit Statistical Brochure -- Units Reporting Events
NOTE: This brochure contains data on units reporting events only. For a review of statistics containing all units that reported , see the brochure "2015 Generating Unit Statistical Brochure -- All Units Reporting".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1268 | 1267.5 | 155.09 | 98.87 | 43.95 | 71.49 | 52.91 | 83.13 | 80.52 | 8.45 | 11.37 | 8.82 | 11.99 | 4.89 | 7.95 | 9.91 | 16.15 | 8.92 | 3.07 | 61.47 | 82.78 | 80.19 | 7.02 | 9.7 | 12.58 | 4.64
| All Fuel Types | 1-99 | 300 | 297.75 | 124.23 | 99.06 | 28.47 | 64.98 | 40.43 | 84.23 | 82.03 | 11.61 | 14.31 | 9.71 | 10.46 | 5.31 | 8.38 | 9.81 | 19.92 | 7.39 | 3.07 | 43.81 | 84.41 | 82.23 | 10.23 | 12.89 | 10.6 | 4.99
|  | 100-199 | 302 | 301.75 | 66.1 | 99.48 | 29.08 | 61.72 | 45.54 | 84.49 | 81.67 | 8.46 | 11.82 | 7.84 | 11.3 | 4.21 | 6.85 | 8.73 | 16.44 | 8.66 | 2.64 | 47.12 | 84.09 | 81.26 | 8.03 | 11.31 | 11.8 | 4.11
|  | 200-299 | 151 | 151 | 206.38 | 98.55 | 35.58 | 65.54 | 53.79 | 79.2 | 76 | 11.09 | 14.46 | 11.71 | 14.09 | 6.71 | 10.7 | 13.08 | 20.06 | 10.1 | 3.99 | 54.29 | 79.46 | 76.28 | 10.59 | 13.93 | 14.12 | 6.43
|  | 300-399 | 107 | 108 | 199.88 | 97.45 | 34.46 | 66.6 | 52.38 | 82.59 | 80.36 | 7.88 | 10.51 | 8.49 | 12.93 | 4.48 | 7.43 | 9.25 | 15.29 | 9.98 | 2.95 | 51.74 | 82.46 | 80.25 | 8.03 | 10.67 | 13.02 | 4.52
|  | 400-599 | 202 | 202 | 297.59 | 97.99 | 44.8 | 71.9 | 62.11 | 82.12 | 79.1 | 7.52 | 10.96 | 9.44 | 12.82 | 5.05 | 8.14 | 10.65 | 15.1 | 9.74 | 3.09 | 62.31 | 82.11 | 79.07 | 7.59 | 11.03 | 12.77 | 5.12
|  | 600-799 | 133 | 133 | 549.52 | 97.34 | 53.04 | 75.54 | 70.11 | 84.29 | 81.74 | 5.27 | 7.59 | 6.92 | 11.8 | 3.9 | 6.82 | 9.03 | 11.69 | 8.88 | 2.92 | 70.22 | 84.29 | 81.76 | 5.27 | 7.57 | 11.81 | 3.9
|  | 800-999 | 60 | 60 | 297.76 | 98.3 | 49.21 | 72.71 | 67.38 | 84.46 | 82.73 | 5.3 | 7.16 | 6.31 | 11.76 | 3.77 | 6.63 | 8.29 | 11.19 | 8.91 | 2.86 | 67.67 | 84.59 | 82.87 | 5.26 | 7.1 | 11.65 | 3.76
|  | 1000 Plus | 13 | 13 | 866.23 | 96.92 | 56.26 | 77.83 | 71.49 | 75.42 | 72.86 | 8.81 | 10.02 | 9.66 | 17.67 | 6.91 | 11.02 | 12.49 | 15.14 | 13.56 | 4.11 | 72.28 | 75.81 | 73.3 | 8.1 | 9.36 | 17.82 | 6.37
| Coal | All Sizes | 800 | 784.5 | 468.38 | 97.47 | 54.13 | 74.57 | 64.62 | 83.09 | 80.35 | 7.39 | 9.82 | 8.72 | 11.75 | 5.15 | 8.46 | 10.45 | 14.25 | 8.44 | 3.31 | 72.58 | 83.27 | 80.61 | 6.12 | 8.34 | 12 | 4.73
| Primary | 1-99 | 132 | 126.75 | 226.92 | 98.8 | 32.97 | 70.56 | 41.86 | 83.48 | 81.65 | 12.98 | 14.92 | 11.25 | 10.28 | 6.24 | 10.08 | 11.17 | 21.36 | 6.45 | 3.84 | 46.72 | 85.18 | 83.46 | 9.28 | 11.15 | 10.04 | 4.78
|  | 100-199 | 191 | 183.83 | 430.12 | 97.13 | 39.33 | 66.14 | 58.71 | 84.95 | 81.61 | 6.96 | 9.93 | 8.41 | 10.66 | 4.39 | 7.21 | 9.3 | 14 | 7.84 | 2.82 | 59.47 | 84.94 | 81.6 | 6.74 | 9.73 | 10.76 | 4.3
|  | 200-299 | 111 | 109 | 433.32 | 97.88 | 41.87 | 69.39 | 59.89 | 78.11 | 74.57 | 10.86 | 13.99 | 12.33 | 14.6 | 7.29 | 11.67 | 14.14 | 19.62 | 10.23 | 4.37 | 60.34 | 78.46 | 74.91 | 10.3 | 13.47 | 14.6 | 6.93
|  | 300-399 | 64 | 63.58 | 462.55 | 95.45 | 49.09 | 72.39 | 67.54 | 82.62 | 80.03 | 6.14 | 8.73 | 7.91 | 12.96 | 4.42 | 7.96 | 10.1 | 13.32 | 9.41 | 3.54 | 67.82 | 82.59 | 79.99 | 6.26 | 8.84 | 12.88 | 4.53
|  | 400-599 | 139 | 137.33 | 569.45 | 97.29 | 57.9 | 75.22 | 76.97 | 82.87 | 79.99 | 6.26 | 8.77 | 8.37 | 11.99 | 5.14 | 7.97 | 10.22 | 12.03 | 9.16 | 2.83 | 76.98 | 82.8 | 79.84 | 6.32 | 8.91 | 12 | 5.19
|  | 600-799 | 108 | 108 | 702.74 | 97.06 | 59.22 | 76.31 | 77.35 | 85.31 | 82.75 | 4.85 | 6.83 | 6.46 | 10.74 | 3.94 | 6.8 | 8.96 | 10.63 | 7.88 | 2.86 | 77.61 | 85.43 | 82.88 | 4.83 | 6.79 | 10.63 | 3.94
|  | 800-999 | 43 | 43 | 733.87 | 96.65 | 57.51 | 75.65 | 76.02 | 84.15 | 82.48 | 5.94 | 7.38 | 6.99 | 11.06 | 4.8 | 7.75 | 9.36 | 11.17 | 8.1 | 2.96 | 76.02 | 84.33 | 82.69 | 5.87 | 7.3 | 10.92 | 4.74
|  | 1000 Plus | 12 | 12 | 867.93 | 96.77 | 58.8 | 78.91 | 74.31 | 77.5 | 74.86 | 5.27 | 6.53 | 6.35 | 18.36 | 4.13 | 8.59 | 10.05 | 12.12 | 13.91 | 4.45 | 74.52 | 77.45 | 74.88 | 5.31 | 6.62 | 18.37 | 4.18
| Oil | All Sizes | 76 | 66.58 | 76.21 | 98.95 | 7.58 | 44.16 | 23.31 | 82.71 | 81.14 | 14.96 | 19.79 | 11.02 | 13.19 | 4.1 | 7.94 | 9.46 | 29.73 | 9.35 | 3.84 | 17.16 | 78.75 | 77.87 | 23.5 | 26.27 | 15.98 | 5.27
| Primary | 1-99 | 24 | 19.33 | 67.89 | 99.31 | 27.54 | 53.61 | 41.27 | 85.77 | 82.71 | 5.19 | 11.7 | 6.89 | 11.97 | 2.26 | 7.83 | 10.84 | 21.74 | 6.4 | 5.57 | 51.37 | 84.94 | 81.54 | 3.73 | 9.67 | 13.08 | 1.99
|  | 100-199 | 17 | 17 | 157.22 | 98.72 | 8.54 | 39.08 | 18.9 | 84.8 | 83.05 | 24.17 | 29.83 | 18.99 | 9.18 | 6.02 | 8.35 | 10.07 | 35.87 | 6.85 | 2.33 | 21.86 | 83.61 | 81.8 | 22.15 | 27.52 | 10.17 | 6.22
|  | 200-299 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
|  | 300-399 | 11 | 11 | 108.32 | 99.13 | 11.85 | 41.89 | 27.95 | 83.49 | 82.95 | 5.65 | 7.07 | 5.07 | 14.83 | 1.67 | 4.46 | 4.94 | 15.05 | 12.04 | 2.79 | 28.28 | 83.32 | 82.8 | 5.55 | 6.86 | 15.02 | 1.66
|  | 400-599 | 12 | 10 | 21.22 | 98.98 | 1.9 | 41.47 | 4.7 | 80.19 | 79.41 | 55.39 | 58.75 | 25.73 | 13.97 | 5.84 | 11.16 | 11.87 | 72.52 | 8.65 | 5.32 | 4.58 | 79.89 | 79.12 | 57.63 | 60.75 | 13.89 | 6.23
|  | 600-799 | 5 | 5 | 31.31 | 99.26 | 4.73 | 50.37 | 9.58 | 73.88 | 73.53 | 10.03 | 11.5 | 6.99 | 25.06 | 1.07 | 5.44 | 5.74 | 37.53 | 20.68 | 4.38 | 9.39 | 71.56 | 71.24 | 10.53 | 11.99 | 27.33 | 1.11
|  | 800-999 | 4 | 2.17 | 116 | 88.92 | 0.42 | 8.91 | 4.88 | 84.01 | 84 | 1.62 | 1.76 | 1.56 | 15.91 | 0.08 | 0.76 | 0.77 | 13.59 | 15.23 | 0.68 | 4.73 | 83.91 | 83.91 | 1.68 | 1.82 | 16.01 | 0.08
| Gas | All Sizes | 334 | 319.42 | 45.31 | 99.09 | 11.93 | 42.61 | 24.61 | 82.13 | 80.12 | 16.98 | 21.5 | 10.46 | 12.83 | 5.03 | 7.76 | 9.41 | 28.16 | 10.11 | 2.73 | 28 | 80.46 | 78.13 | 14.53 | 19.71 | 14.78 | 4.76
| Primary | 1-99 | 103 | 98.67 | 51.33 | 98.9 | 10.42 | 45.34 | 18.01 | 83.76 | 82.69 | 24.52 | 26.78 | 11.06 | 10.39 | 5.85 | 8.35 | 9.07 | 33.59 | 7.88 | 2.5 | 22.98 | 82.3 | 80.94 | 23.72 | 26 | 10.56 | 7.14
|  | 100-199 | 93 | 89.75 | 30.85 | 99.56 | 11.6 | 43.35 | 25.54 | 83.94 | 81.79 | 13.37 | 17.93 | 8.25 | 12.12 | 3.94 | 6.14 | 7.78 | 23.73 | 9.92 | 2.2 | 26.77 | 83.3 | 81.07 | 12.47 | 17.03 | 12.89 | 3.81
|  | 200-299 | 37 | 33.33 | 67.21 | 99.18 | 15.51 | 45.47 | 33.61 | 79.7 | 77.06 | 15.69 | 20.91 | 12.16 | 14.05 | 6.26 | 9.95 | 12.45 | 27.62 | 10.35 | 3.7 | 34.1 | 79.77 | 77.26 | 15.31 | 20.26 | 14.07 | 6.16
|  | 300-399 | 31 | 30.42 | 48.14 | 98.25 | 9.69 | 40.34 | 23.93 | 81.05 | 78.85 | 19.94 | 23.66 | 12.5 | 12.99 | 5.96 | 7.99 | 9.75 | 29.01 | 10.95 | 2.03 | 24.02 | 80.86 | 78.65 | 19.69 | 23.45 | 13.25 | 5.89
|  | 400-599 | 52 | 49.42 | 64.1 | 98.45 | 12.21 | 43.22 | 27.91 | 79.42 | 76.26 | 14.84 | 22.57 | 12.57 | 15.72 | 4.86 | 8.38 | 11.21 | 30.13 | 12.2 | 3.52 | 28.26 | 79.63 | 76.53 | 14.72 | 22.2 | 15.5 | 4.88
|  | 600-799 | 11 | 11 | 184.93 | 96.25 | 12.9 | 47.59 | 26.37 | 75.39 | 72.99 | 14.44 | 20.7 | 14.29 | 20.16 | 4.45 | 8.4 | 10.8 | 29.55 | 16.21 | 3.95 | 27.12 | 75.99 | 73.62 | 14.11 | 20.26 | 19.56 | 4.46
|  | 800-999 | 7 | 6.83 | 30.14 | 99.27 | 11.07 | 32.01 | 34.3 | 82.83 | 82.58 | 2.17 | 2.68 | 1.66 | 16.41 | 0.76 | 4.45 | 4.7 | 12.1 | 12.72 | 3.69 | 34.58 | 82.74 | 82.49 | 2.12 | 2.62 | 16.51 | 0.75
| Lignite Primary | All Sizes | 33 | 30.42 | 28.2 | 99.92 | 63.32 | 79.31 | 79.78 | 88.4 | 84.11 | 3.01 | 7.6 | 6.9 | 9.12 | 2.48 | 3.51 | 7.38 | 8.87 | 8.09 | 1.03 | 79.84 | 89.02 | 84.01 | 3.27 | 8.93 | 8.28 | 2.7
| Oil/Gas | All Sizes | 403 | 386 | 48.55 | 99.09 | 11.02 | 42.83 | 24.38 | 82.23 | 80.3 | 16.66 | 21.22 | 10.5 | 12.89 | 4.87 | 7.79 | 9.42 | 28.42 | 9.98 | 2.92 | 25.73 | 80.1 | 78.07 | 15.91 | 20.7 | 15.03 | 4.87
| Primary | 1-99 | 126 | 118 | 55.52 | 98.98 | 13.82 | 48.29 | 21.81 | 84.09 | 82.69 | 19.44 | 22.84 | 10.17 | 10.64 | 5.26 | 8.27 | 9.36 | 30.45 | 7.64 | 3 | 28.62 | 82.82 | 81.06 | 17.62 | 21.06 | 11.06 | 6.12
|  | 100-199 | 110 | 106.75 | 34.02 | 99.54 | 11.16 | 42.83 | 24.54 | 84.07 | 81.97 | 14.78 | 19.47 | 9 | 11.68 | 4.26 | 6.48 | 8.13 | 25.33 | 9.46 | 2.22 | 26.06 | 83.34 | 81.17 | 13.78 | 18.44 | 12.49 | 4.17
|  | 200-299 | 39 | 34.42 | 67.88 | 98.97 | 15.39 | 45.74 | 33.21 | 80.06 | 77.46 | 15.49 | 20.73 | 12.05 | 13.85 | 6.09 | 9.7 | 12.16 | 27.41 | 10.24 | 3.61 | 33.65 | 80.16 | 77.68 | 15.1 | 20.07 | 13.86 | 5.98
|  | 300-399 | 42 | 41.42 | 57.17 | 98.38 | 10.26 | 40.8 | 24.95 | 81.67 | 79.89 | 16.34 | 19.54 | 10.92 | 13.45 | 4.87 | 7.1 | 8.53 | 25.53 | 11.23 | 2.22 | 25.16 | 81.51 | 79.76 | 15.92 | 19.1 | 13.72 | 4.76
|  | 400-599 | 60 | 59.42 | 59.78 | 98.51 | 10.33 | 43.16 | 23.72 | 79.56 | 76.82 | 17.53 | 25.01 | 13.4 | 15.4 | 5.04 | 8.88 | 11.33 | 33.87 | 11.56 | 3.84 | 23.94 | 79.67 | 77 | 17.63 | 24.87 | 15.2 | 5.12
|  | 600-799 | 16 | 16 | 106.11 | 97.72 | 10.41 | 47.96 | 20.83 | 74.89 | 73.17 | 13.8 | 19.42 | 12.21 | 21.77 | 3.33 | 7.42 | 9.14 | 30.91 | 17.68 | 4.09 | 21.71 | 74.64 | 72.89 | 13.66 | 19.24 | 21.93 | 3.43
|  | 800-999 | 9 | 9 | 31.13 | 99.15 | 8.4 | 31 | 27.21 | 83.11 | 82.92 | 2.15 | 2.64 | 1.59 | 16.29 | 0.6 | 3.56 | 3.75 | 12.16 | 13.33 | 2.96 | 27.09 | 83.03 | 82.84 | 2.1 | 2.58 | 16.39 | 0.58
| NUCLEAR | All Sizes | 99 | 99 | 4221.14 | 98.96 | 91.48 | 99.18 | 92.04 | 92.05 | 90.31 | 1.35 | 1.78 | 1.78 | 6.7 | 1.26 | 1.86 | 2.54 | 2.71 | 6.09 | 0.61 | 92.24 | 92.25 | 90.45 | 1.19 | 1.63 | 6.64 | 1.12
| All Types | 400-799 | 13 | 13 | 2803.09 | 100 | 87.27 | 98.39 | 88.64 | 88.64 | 86.96 | 3.77 | 4.38 | 4.38 | 7.9 | 3.47 | 4.78 | 5.51 | 5.9 | 6.58 | 1.31 | 88.69 | 88.69 | 87.01 | 3.85 | 4.49 | 7.76 | 3.55
|  | 800-999 | 34 | 34 | 4458.23 | 98.38 | 92.36 | 99.76 | 92.63 | 92.63 | 91.53 | 1.02 | 1.29 | 1.29 | 6.42 | 0.95 | 1.38 | 1.82 | 1.94 | 6 | 0.43 | 92.57 | 92.57 | 91.48 | 1.01 | 1.29 | 6.48 | 0.95
|  | 1000 Plus | 52 | 52 | 4630.33 | 98.87 | 91.6 | 98.98 | 92.5 | 92.52 | 90.35 | 0.96 | 1.46 | 1.46 | 6.58 | 0.9 | 1.45 | 2.27 | 2.42 | 6.04 | 0.55 | 92.54 | 92.55 | 90.39 | 0.94 | 1.43 | 6.57 | 0.88
| PWR | All Sizes | 62 | 62 | 4106.61 | 98.48 | 90.76 | 99.48 | 90.95 | 90.96 | 89.6 | 1.42 | 1.8 | 1.8 | 7.73 | 1.31 | 2.04 | 2.59 | 2.78 | 7 | 0.73 | 91.23 | 91.25 | 89.83 | 1.28 | 1.68 | 7.58 | 1.18
|  | 400-799 | 5 | 5 | 2837.04 | 100 | 83.83 | 99.32 | 84.2 | 84.2 | 82.85 | 4.31 | 4.52 | 4.52 | 12 | 3.79 | 7.08 | 7.37 | 8.07 | 8.71 | 3.29 | 84.4 | 84.4 | 83.1 | 4.3 | 4.49 | 11.81 | 3.79
|  | 800-999 | 22 | 22 | 4308.75 | 97.38 | 91.4 | 99.94 | 91.49 | 91.49 | 90.59 | 1.19 | 1.48 | 1.48 | 7.41 | 1.11 | 1.53 | 1.95 | 2.1 | 6.98 | 0.42 | 91.45 | 91.45 | 90.55 | 1.17 | 1.46 | 7.47 | 1.08
|  | 1000 Plus | 35 | 35 | 4244.1 | 98.95 | 90.95 | 99.28 | 91.57 | 91.59 | 89.95 | 1.17 | 1.64 | 1.64 | 7.32 | 1.08 | 1.64 | 2.3 | 2.47 | 6.77 | 0.56 | 91.61 | 91.64 | 89.97 | 1.12 | 1.59 | 7.33 | 1.04
| BWR | All Sizes | 31 | 31 | 4671.08 | 100 | 93.42 | 98.88 | 94.38 | 94.38 | 92 | 0.82 | 1.24 | 1.24 | 4.84 | 0.78 | 1.25 | 2.15 | 2.25 | 4.36 | 0.47 | 94.48 | 94.48 | 91.97 | 0.74 | 1.18 | 4.82 | 0.7
|  | 400-799 | 4 | 4 | 1977.4 | 100 | 88.77 | 98.5 | 90.29 | 90.29 | 89.04 | 3.02 | 3.27 | 3.27 | 6.9 | 2.81 | 2.96 | 3.6 | 3.87 | 6.75 | 0.15 | 90.12 | 90.12 | 88.87 | 3.07 | 3.33 | 7.02 | 2.86
|  | 800-999 | 10 | 10 | 6003.66 | 100 | 95.9 | 100.02 | 95.95 | 95.95 | 94.6 | 0.42 | 0.71 | 0.71 | 3.65 | 0.4 | 0.92 | 1.48 | 1.53 | 3.13 | 0.51 | 95.88 | 95.88 | 94.56 | 0.42 | 0.71 | 3.72 | 0.4
|  | 1000 Plus | 17 | 17 | 5626.77 | 100 | 92.91 | 98.41 | 94.42 | 94.42 | 91.17 | 0.55 | 1.08 | 1.08 | 5.05 | 0.53 | 1.05 | 2.2 | 2.31 | 4.53 | 0.52 | 94.42 | 94.42 | 91.23 | 0.59 | 1.12 | 5.02 | 0.56
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 303 | 303 | 4.23 | 98.76 | 4.09 | 81.34 | 3.49 | 91.11 | 89.85 | 40.07 | 42.8 | 11.22 | 5.67 | 3.22 | 6.59 | 7.05 | 59.4 | 2.31 | 3.37 | 5.03 | 90.88 | 88.83 | 34.98 | 40.12 | 5.58 | 3.54
| ENGINE** | 1-19 | 36 | 36 | 2.48 | 95 | 0.22 | 62.51 | 0.39 | 89.11 | 89.04 | 90.16 | 90.33 | 21.38 | 7.36 | 3.53 | 9.13 | 9.19 | 96.04 | 1.76 | 5.6 | 0.35 | 89.29 | 89.21 | 91.28 | 91.45 | 7.04 | 3.67
|  | 20 Plus | 267 | 267 | 4.27 | 98.85 | 4.29 | 81.4 | 3.91 | 91.37 | 89.96 | 37.02 | 39.95 | 10.88 | 5.45 | 3.18 | 6.25 | 6.76 | 55.56 | 2.38 | 3.07 | 5.27 | 90.96 | 88.81 | 33.88 | 39.13 | 5.51 | 3.53
| GAS | All Sizes | 746 | 746 | 8.94 | 98.16 | 5.52 | 77.21 | 4.15 | 89.72 | 87.82 | 47.11 | 48.95 | 11.3 | 6.56 | 3.72 | 6.01 | 6.28 | 60.16 | 4.27 | 2.29 | 7.15 | 90.72 | 88.87 | 27.14 | 29.34 | 6.61 | 2.67
| TURBINE** | 1-19 | 124 | 124 | 2.75 | 96.5 | 0.57 | 70.1 | 0.79 | 85.99 | 85.31 | 89.08 | 89.28 | 18.38 | 7.52 | 6.49 | 10.32 | 10.43 | 92.95 | 3.69 | 3.83 | 0.81 | 85.19 | 84.53 | 89.02 | 89.21 | 8.24 | 6.57
|  | 20-49 | 152 | 152 | 4.46 | 98.56 | 2.05 | 86.86 | 1.56 | 91.58 | 87.87 | 72.3 | 73.3 | 12.13 | 4.34 | 4.08 | 5.78 | 5.97 | 79.34 | 2.64 | 1.7 | 2.36 | 91.9 | 87.9 | 57.79 | 59.24 | 4.87 | 3.23
|  | 50 Plus | 469 | 469 | 10.66 | 98.31 | 6.07 | 76.96 | 5.82 | 90.07 | 88.41 | 33.26 | 35.78 | 9.6 | 7.01 | 2.92 | 5 | 5.34 | 47.8 | 4.92 | 2.08 | 7.89 | 90.84 | 89.15 | 23.65 | 25.96 | 6.71 | 2.45
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 280 | 277 | 84.26 | 98.57 | 56.09 | 80.73 | 59 | 88.18 | 84.83 | 3.59 | 4.97 | 3.95 | 9.62 | 2.2 | 3.82 | 4.85 | 7.67 | 8 | 1.62 | 69.48 | 88.61 | 85.17 | 2.18 | 3.39 | 9.85 | 1.55
| HYDRO | All Sizes | 1053 | 1053 | 22 | 99.95 | 38.02 | 65.67 | 54.6 | 81.18 | 80.7 | 9.32 | 9.52 | 7.89 | 12.6 | 6.21 | 8.23 | 8.38 | 12.19 | 10.59 | 2.01 | 57.89 | 82.97 | 82.51 | 4.16 | 4.32 | 14.37 | 2.66
|  | 1-29 | 397 | 397 | 83.44 | 99.79 | 30.73 | 59.98 | 50.2 | 76.97 | 76.57 | 17.3 | 17.61 | 15.85 | 10.76 | 12.27 | 13.85 | 14.09 | 19.44 | 9.18 | 1.58 | 51.24 | 83.67 | 83.17 | 8.33 | 8.8 | 10.67 | 5.66
|  | 30 Plus | 656 | 656 | 15.82 | 99.97 | 38.52 | 66.01 | 57.26 | 83.73 | 83.2 | 3.98 | 4.12 | 3.29 | 13.72 | 2.55 | 4.83 | 4.92 | 7.41 | 11.45 | 2.27 | 58.35 | 82.92 | 82.46 | 3.86 | 4 | 14.62 | 2.46
| PUMPED STORAGE | All Sizes | 109 | 109 | 8.27 | 99.9 | 7.63 | 52.95 | 25.31 | 81.48 | 81.11 | 11.86 | 12.04 | 7.58 | 13.3 | 5.22 | 7.08 | 7.16 | 15.6 | 11.44 | 1.86 | 14.41 | 77.91 | 76.73 | 16.3 | 17.04 | 15.73 | 6.37
| MULTIBOILER/MULTI-TURBINE | All Sizes | 21 | 21 | 299.68 | 99.37 | 45.19 | 66.85 | 76.08 | 87.88 | 80.36 | 2.18 | 7.78 | 6.9 | 10.42 | 1.69 | 5.37 | 10.81 | 13.21 | 6.75 | 3.67 | 67.6 | 86.41 | 80.94 | 2.48 | 6.54 | 11.87 | 1.72
| DIESEL** | All Sizes | 134 | 131.75 | 14.77 | 99.59 | 9.68 | 56.69 | 7.97 | 94.31 | 93.4 | 10.52 | 13.3 | 3.7 | 4.75 | 0.94 | 3.37 | 3.67 | 31.9 | 2.32 | 2.43 | 17.07 | 95.39 | 93.99 | 3.33 | 5.94 | 4.03 | 0.59
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.