## Sheet1
2014 Generating Unit Statistical Brochure -- All Units Reporting
NOTE: This brochure contains data on all units, whether they reported event records or not. For a review of statistics containing only those units that reported events, see the brochure "2014 Generating Unit Statistical Brochure -- Units Reporting Events".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 988 | 990 | 270.65 | 97.7 | 49.17 | 76.23 | 56.39 | 83.92 | 81.81 | 7.65 | 9.93 | 8.22 | 11.41 | 4.67 | 7.61 | 9.25 | 14.44 | 8.46 | 2.94 | 64.5 | 82.96 | 80.8 | 6.8 | 8.84 | 12.34 | 4.7
| All Fuel Types | 1-99 | 197 | 197 | 178.98 | 98.76 | 27.33 | 63.7 | 40.72 | 85.77 | 83.66 | 11.6 | 14.62 | 10.13 | 8.89 | 5.34 | 8.75 | 10.24 | 20.7 | 5.48 | 3.41 | 42.9 | 85.52 | 83.36 | 11.1 | 13.94 | 9.12 | 5.36
|  | 100-199 | 233 | 233 | 223.84 | 97.62 | 34.1 | 67.47 | 48.36 | 85.76 | 84.1 | 6.88 | 8.83 | 6.96 | 10.67 | 3.57 | 6.38 | 7.62 | 13.91 | 7.86 | 2.81 | 50.53 | 85.41 | 83.61 | 6.67 | 8.7 | 10.98 | 3.61
|  | 200-299 | 110 | 110 | 271.09 | 97.37 | 40.04 | 67.88 | 58.62 | 81.17 | 78.58 | 9.35 | 12.17 | 10.28 | 12.79 | 6.05 | 9.41 | 11.58 | 16.97 | 9.43 | 3.36 | 58.99 | 81.46 | 78.88 | 9.03 | 11.79 | 12.69 | 5.85
|  | 300-399 | 96 | 97 | 223.32 | 97.68 | 37.67 | 67.91 | 55.89 | 82.7 | 80.69 | 6.8 | 9.11 | 7.5 | 13.22 | 4.08 | 6.81 | 8.45 | 13.47 | 10.5 | 2.73 | 55.47 | 82.68 | 80.75 | 6.61 | 8.84 | 13.39 | 3.93
|  | 400-599 | 180 | 180 | 322.43 | 97.2 | 51.1 | 76.08 | 66.66 | 83.3 | 80.69 | 6.44 | 8.91 | 7.9 | 12.12 | 4.59 | 7.34 | 9.34 | 12.62 | 9.36 | 2.75 | 67.16 | 83.12 | 80.47 | 6.49 | 8.97 | 12.22 | 4.66
|  | 600-799 | 116 | 116 | 623.44 | 96.7 | 59.3 | 80.64 | 73.59 | 82.75 | 80.58 | 6.73 | 8.48 | 7.95 | 11.94 | 5.31 | 8.14 | 9.83 | 12.01 | 9.11 | 2.83 | 73.55 | 82.62 | 80.47 | 6.76 | 8.49 | 12.05 | 5.33
|  | 800-999 | 50 | 50 | 279.23 | 98.21 | 55.34 | 82.49 | 66.62 | 83.66 | 82.21 | 4.82 | 6.21 | 5.48 | 12.96 | 3.38 | 5.57 | 6.95 | 9.62 | 10.77 | 2.19 | 67.08 | 83.72 | 82.27 | 4.77 | 6.14 | 12.92 | 3.36
|  | 1000 Plus | 7 | 7 | 759.7 | 84.84 | 58.86 | 83.92 | 69.38 | 74.51 | 72.83 | 11.65 | 12.74 | 12.23 | 16.34 | 9.15 | 12.71 | 14.34 | 17.47 | 12.78 | 3.56 | 70.14 | 74.55 | 72.86 | 10.98 | 12.1 | 16.8 | 8.65
| Coal | All Sizes | 629 | 626.58 | 510.81 | 96.86 | 61.12 | 79.88 | 70.04 | 84.92 | 82.53 | 5.97 | 8.1 | 7.36 | 10.63 | 4.45 | 7.51 | 9.41 | 12.13 | 7.57 | 3.06 | 76.52 | 84.05 | 81.66 | 5.58 | 7.46 | 11.43 | 4.52
| Primary | 1-99 | 86 | 82.92 | 265.52 | 98.71 | 37.33 | 71.95 | 51.31 | 87.08 | 85.07 | 7.45 | 10.34 | 8.07 | 8.79 | 4.13 | 8.54 | 10.28 | 17.18 | 4.38 | 4.41 | 51.88 | 87.23 | 85.14 | 6.9 | 9.89 | 8.92 | 3.85
|  | 100-199 | 147 | 146.17 | 461.14 | 96.41 | 46.43 | 73.55 | 61.43 | 87.12 | 85 | 6.01 | 8.12 | 7.03 | 8.95 | 3.93 | 7.2 | 8.88 | 12.91 | 5.68 | 3.27 | 63.13 | 86.92 | 84.66 | 5.84 | 8.06 | 9.16 | 3.92
|  | 200-299 | 79 | 78.67 | 458.24 | 96.18 | 48.84 | 72.9 | 66.77 | 82.53 | 79.5 | 8.03 | 10.81 | 9.73 | 11.64 | 5.83 | 9.14 | 11.64 | 15.28 | 8.33 | 3.31 | 66.99 | 82.97 | 79.94 | 7.67 | 10.41 | 11.47 | 5.56
|  | 300-399 | 58 | 58.92 | 527.23 | 96.02 | 56.28 | 75.63 | 74.15 | 83.96 | 81.09 | 5.3 | 7.82 | 7.28 | 11.89 | 4.15 | 7.04 | 9.43 | 11.62 | 8.99 | 2.89 | 74.42 | 84.04 | 81.26 | 5.16 | 7.6 | 11.91 | 4.05
|  | 400-599 | 124 | 124 | 612.35 | 96.96 | 64.49 | 80.41 | 80.23 | 84.14 | 81.43 | 5.09 | 7.05 | 6.83 | 11.55 | 4.31 | 6.81 | 8.72 | 10.02 | 9.05 | 2.5 | 80.2 | 83.91 | 81.14 | 5.17 | 7.19 | 11.72 | 4.37
|  | 600-799 | 97 | 96.92 | 697.03 | 96.74 | 65.4 | 81.45 | 80.29 | 84.21 | 81.97 | 5.62 | 7.32 | 7.09 | 11.01 | 4.78 | 7.29 | 9.05 | 10.33 | 8.5 | 2.51 | 80.3 | 84.19 | 81.97 | 5.64 | 7.33 | 11 | 4.8
|  | 800-999 | 33 | 33 | 918.88 | 98.48 | 68.74 | 84.19 | 81.71 | 84.5 | 82.9 | 4.64 | 5.7 | 5.57 | 11.52 | 3.97 | 6.34 | 7.86 | 8.92 | 9.15 | 2.37 | 81.64 | 84.49 | 82.91 | 4.55 | 5.6 | 11.62 | 3.89
|  | 1000 Plus | 6 | 6 | 829.63 | 82.42 | 64.19 | 86.77 | 74.16 | 75.86 | 74.29 | 7.89 | 8.99 | 8.85 | 17.79 | 6.35 | 9.23 | 10.75 | 12.89 | 14.91 | 2.88 | 73.97 | 75.61 | 74 | 7.96 | 9.09 | 17.99 | 6.4
| Oil | All Sizes | 61 | 57.5 | 87.86 | 99.39 | 9.25 | 49.33 | 26.97 | 84.84 | 83.97 | 8.65 | 11.04 | 6.58 | 12.6 | 2.55 | 5.62 | 6.4 | 19.62 | 9.54 | 3.06 | 18.76 | 76.96 | 76.24 | 14.46 | 16.83 | 19.87 | 3.17
| Primary | 1-99 | 24 | 23.67 | 75.24 | 99.62 | 25.21 | 52.73 | 41.03 | 90.79 | 89.58 | 6.41 | 8.7 | 5.18 | 6.4 | 2.81 | 6.24 | 7.29 | 15.42 | 2.98 | 3.43 | 47.81 | 89.68 | 88.19 | 5.29 | 7.97 | 7.65 | 2.67
|  | 100-199 | 12 | 12 | 161.95 | 99.12 | 13.04 | 58.84 | 19.97 | 89.5 | 88.69 | 10.68 | 13.8 | 9.24 | 8.11 | 2.39 | 4.84 | 5.65 | 22.74 | 5.66 | 2.46 | 22.17 | 88.98 | 88.08 | 9.55 | 12.71 | 8.68 | 2.34
|  | 200-299 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
|  | 300-399 | 11 | 11 | 162.83 | 99.24 | 11.19 | 45.76 | 23.98 | 75.9 | 75.28 | 4.02 | 5.91 | 4.08 | 23.1 | 1 | 3.08 | 3.58 | 13.16 | 21.02 | 2.08 | 24.46 | 76.3 | 75.66 | 3.95 | 5.9 | 22.69 | 1.01
|  | 400-599 | 5 | 5 | 25.51 | 97.96 | 3 | 52.57 | 5.59 | 89.36 | 88.87 | 26.78 | 32.79 | 16.64 | 8.59 | 2.04 | 4.08 | 4.56 | 47.17 | 6.56 | 2.03 | 5.7 | 89.27 | 88.73 | 25.35 | 32.09 | 8.79 | 1.94
|  | 600-799 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
|  | 800-999 | 6 | 2.83 | 27.17 | 90.98 | 0.39 | 34.67 | 1.1 | 69.92 | 69.92 | 0.25 | 0.25 | 0.24 | 30.08 | 0 | 1.79 | 1.79 | 62.02 | 28.29 | 1.79 | 1.11 | 70.56 | 70.56 | 0.24 | 0.24 | 29.44 | 0
| Gas | All Sizes | 269 | 260.58 | 69.89 | 98.15 | 10.2 | 36.85 | 25.1 | 80.81 | 79.76 | 18.58 | 20.69 | 11.51 | 13.46 | 5.73 | 8.44 | 9.18 | 27.31 | 10.75 | 2.71 | 27.68 | 79.12 | 77.84 | 17.05 | 19.79 | 15.19 | 5.69
| Primary | 1-99 | 74 | 70.17 | 130 | 97.15 | 8.13 | 42.32 | 15.86 | 82.19 | 81.55 | 34.48 | 35.11 | 18.61 | 9.47 | 8.35 | 10.49 | 10.65 | 40.4 | 7.33 | 2.14 | 19.21 | 80.96 | 80.2 | 31.58 | 32.27 | 10.17 | 8.87
|  | 100-199 | 75 | 74.83 | 66.48 | 98.43 | 10.9 | 39.22 | 26.29 | 82.5 | 81.62 | 10.34 | 11.44 | 7 | 14.47 | 3.03 | 4.97 | 5.4 | 17.27 | 12.53 | 1.94 | 27.79 | 81.7 | 80.76 | 10.14 | 11.18 | 15.16 | 3.14
|  | 200-299 | 30 | 28.25 | 83.33 | 98.88 | 12.44 | 35.57 | 35.37 | 76.8 | 75.47 | 16.45 | 19.31 | 11.93 | 16.23 | 6.97 | 10.57 | 11.78 | 25.65 | 12.63 | 3.6 | 34.97 | 76.38 | 75.09 | 16.69 | 19.44 | 16.62 | 7
|  | 300-399 | 28 | 27.08 | 49.99 | 98.54 | 8 | 29.73 | 26.87 | 82.45 | 81.86 | 15.95 | 17.15 | 9.71 | 12.46 | 5.1 | 7.7 | 8.1 | 23.42 | 9.85 | 2.6 | 26.91 | 82.32 | 81.72 | 15.28 | 16.51 | 12.83 | 4.85
|  | 400-599 | 45 | 45 | 68.48 | 97.47 | 11.83 | 38.05 | 30.7 | 80.03 | 77.8 | 14.91 | 20.08 | 12.13 | 14.59 | 5.38 | 8.95 | 11.03 | 27.76 | 11.02 | 3.57 | 31.09 | 79.82 | 77.61 | 15.19 | 20.17 | 14.61 | 5.57
|  | 600-799 | 10 | 9.08 | 188.33 | 94.01 | 10.02 | 40.65 | 23.56 | 71.65 | 70.57 | 34.87 | 36.36 | 24.95 | 15.73 | 12.62 | 18.48 | 19.56 | 45.15 | 9.87 | 5.86 | 24.64 | 71.99 | 70.87 | 33.62 | 35.1 | 15.53 | 12.48
|  | 800-999 | 7 | 6.17 | 16.34 | 98.88 | 5.51 | 34.04 | 16.02 | 76.66 | 76.55 | 1.43 | 1.94 | 1.08 | 23.11 | 0.23 | 3.68 | 3.8 | 18.83 | 19.66 | 3.45 | 16.18 | 76.4 | 76.29 | 1.44 | 1.94 | 23.36 | 0.24
| Lignite Primary | All Sizes | 23 | 23 | 760.3 | 92.81 | 67.39 | 85.46 | 79.46 | 86.02 | 82.17 | 4.76 | 8.28 | 7.87 | 10.02 | 3.97 | 6.21 | 9.29 | 10.84 | 7.77 | 2.24 | 78.85 | 87.01 | 83.5 | 4.63 | 8.05 | 9.16 | 3.83
| Oil/Gas | All Sizes | 324 | 318.08 | 72.75 | 98.35 | 10.02 | 38.51 | 25.44 | 81.54 | 80.52 | 16.84 | 19 | 10.67 | 13.3 | 5.15 | 7.93 | 8.68 | 25.95 | 10.53 | 2.77 | 26.03 | 78.72 | 77.54 | 16.71 | 19.41 | 16.05 | 5.22
| Primary | 1-99 | 96 | 93.83 | 96.2 | 98.63 | 12.92 | 47.44 | 22.53 | 84.47 | 83.68 | 23.38 | 24.67 | 12.52 | 8.66 | 6.88 | 9.36 | 9.76 | 30.59 | 6.17 | 2.48 | 27.23 | 83.41 | 82.44 | 20.75 | 22.26 | 9.46 | 7.13
|  | 100-199 | 87 | 86.83 | 70.63 | 98.46 | 11.16 | 41.17 | 25.49 | 83.38 | 82.51 | 10.37 | 11.68 | 7.16 | 13.67 | 2.95 | 4.96 | 5.44 | 17.84 | 11.66 | 2.01 | 27.11 | 82.58 | 81.65 | 10.09 | 11.33 | 14.37 | 3.04
|  | 200-299 | 31 | 29.25 | 82.81 | 98.89 | 12.13 | 35.78 | 34.38 | 77.32 | 76.02 | 16.52 | 19.37 | 11.87 | 15.88 | 6.8 | 10.33 | 11.51 | 25.75 | 12.35 | 3.53 | 33.9 | 76.96 | 75.72 | 16.76 | 19.51 | 16.21 | 6.83
|  | 300-399 | 39 | 38.08 | 60.73 | 98.62 | 8.93 | 34.07 | 26.07 | 80.63 | 80.04 | 13.2 | 14.56 | 8.63 | 15.4 | 3.96 | 6.42 | 6.84 | 21.04 | 12.95 | 2.46 | 26.2 | 80.57 | 79.96 | 12.49 | 13.89 | 15.69 | 3.74
|  | 400-599 | 50 | 50 | 66.07 | 97.49 | 10.85 | 38.38 | 27.97 | 81.04 | 79 | 15.21 | 20.4 | 12.02 | 13.94 | 5.02 | 8.42 | 10.33 | 28.32 | 10.53 | 3.41 | 28.28 | 80.87 | 78.84 | 15.44 | 20.47 | 13.97 | 5.16
|  | 600-799 | 11 | 10.08 | 181.41 | 94.39 | 9.18 | 41.07 | 21.63 | 67.31 | 66.3 | 34.43 | 36 | 24.51 | 21.34 | 11.35 | 18.34 | 19.35 | 47.05 | 14.35 | 6.99 | 22.35 | 67.09 | 66.06 | 33.14 | 34.72 | 21.83 | 11.08
|  | 800-999 | 9 | 9 | 16.54 | 98.72 | 3.84 | 34.06 | 11.33 | 74.54 | 74.46 | 1.4 | 1.89 | 1.03 | 25.3 | 0.16 | 3.09 | 3.17 | 21.49 | 22.37 | 2.93 | 11.29 | 74.5 | 74.43 | 1.4 | 1.89 | 25.34 | 0.16
| NUCLEAR | All Sizes | 91 | 91 | 3443.32 | 98.32 | 91.25 | 99.44 | 91.98 | 91.98 | 90.48 | 1.3 | 1.86 | 1.86 | 6.81 | 1.22 | 1.68 | 2.44 | 2.6 | 6.34 | 0.46 | 91.76 | 91.76 | 90.33 | 1.31 | 1.83 | 7.02 | 1.22
| All Types | 400-799 | 13 | 13 | 1997.17 | 100 | 90.15 | 97.2 | 93.02 | 93.02 | 90.22 | 1.43 | 2.75 | 2.75 | 5.63 | 1.35 | 2.26 | 3.71 | 3.89 | 4.72 | 0.91 | 92.74 | 92.74 | 89.97 | 1.34 | 2.68 | 6 | 1.26
|  | 800-999 | 34 | 34 | 4369.74 | 95.36 | 92.14 | 99.91 | 92.28 | 92.28 | 91.16 | 1.23 | 1.65 | 1.65 | 6.57 | 1.15 | 1.47 | 2.07 | 2.21 | 6.25 | 0.32 | 92.22 | 92.22 | 91.12 | 1.28 | 1.69 | 6.59 | 1.2
|  | 1000 Plus | 44 | 44 | 3640.84 | 98.65 | 90.9 | 99.52 | 91.44 | 91.44 | 90.04 | 1.33 | 1.77 | 1.77 | 7.33 | 1.23 | 1.67 | 2.34 | 2.52 | 6.9 | 0.44 | 91.34 | 91.34 | 89.92 | 1.32 | 1.77 | 7.44 | 1.22
| PWR | All Sizes | 59 | 59 | 3206.44 | 98.03 | 90.79 | 99.84 | 91.14 | 91.14 | 89.99 | 1.57 | 1.99 | 1.99 | 7.41 | 1.45 | 1.75 | 2.24 | 2.42 | 7.11 | 0.3 | 90.94 | 90.94 | 89.8 | 1.56 | 1.95 | 7.62 | 1.44
|  | 400-799 | 7 | 7 | 1400.7 | 100 | 89.33 | 98.26 | 91.3 | 91.3 | 89.23 | 1.61 | 2.63 | 2.63 | 7.2 | 1.49 | 2.93 | 3.92 | 4.16 | 5.77 | 1.43 | 90.92 | 90.92 | 88.76 | 1.48 | 2.61 | 7.72 | 1.36
|  | 800-999 | 22 | 22 | 4024.64 | 95.69 | 92.1 | 100.46 | 91.89 | 91.89 | 91.12 | 1.6 | 1.97 | 1.97 | 6.62 | 1.49 | 1.7 | 2.15 | 2.3 | 6.41 | 0.21 | 91.69 | 91.69 | 90.93 | 1.66 | 2.03 | 6.76 | 1.55
|  | 1000 Plus | 30 | 30 | 3777.59 | 98.59 | 90.24 | 99.69 | 90.56 | 90.56 | 89.34 | 1.54 | 1.85 | 1.85 | 8.03 | 1.41 | 1.51 | 1.92 | 2.09 | 7.93 | 0.1 | 90.52 | 90.52 | 89.3 | 1.51 | 1.82 | 8.09 | 1.39
| BWR | All Sizes | 30 | 30 | 3987.85 | 98.57 | 92.61 | 98.65 | 94.23 | 94.23 | 91.98 | 0.84 | 1.69 | 1.69 | 4.97 | 0.8 | 1.57 | 2.88 | 3.01 | 4.2 | 0.76 | 93.88 | 93.88 | 91.79 | 0.85 | 1.63 | 5.32 | 0.81
|  | 400-799 | 5 | 5 | 3883.16 | 100 | 93.03 | 95.33 | 97.52 | 97.52 | 93.22 | 1.26 | 3.11 | 3.11 | 1.24 | 1.24 | 1.6 | 3.89 | 3.92 | 0.88 | 0.36 | 97.58 | 97.58 | 93.4 | 1.19 | 2.98 | 1.24 | 1.17
|  | 800-999 | 11 | 11 | 5307.08 | 94.51 | 92.98 | 98.87 | 93.9 | 93.9 | 91.99 | 0.6 | 1.13 | 1.13 | 5.53 | 0.56 | 1 | 1.95 | 2.05 | 5.1 | 0.44 | 94.04 | 94.04 | 92.2 | 0.61 | 1.13 | 5.38 | 0.58
|  | 1000 Plus | 14 | 14 | 3364.05 | 100 | 92.31 | 99.17 | 93.32 | 93.32 | 91.53 | 0.88 | 1.59 | 1.59 | 5.85 | 0.83 | 2 | 3.25 | 3.41 | 4.69 | 1.17 | 93.09 | 93.09 | 91.25 | 0.93 | 1.66 | 6.04 | 0.87
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 308 | 308.08 | 4.65 | 98.25 | 4.1 | 81.58 | 3.6 | 89.61 | 89.14 | 51.43 | 51.6 | 12.61 | 5.21 | 5.17 | 7.88 | 7.9 | 60.94 | 2.51 | 2.7 | 5.02 | 89.17 | 88.53 | 45.56 | 45.73 | 5.4 | 5.44
| ENGINE** | 1-19 | 38 | 37.08 | 3.16 | 94.11 | 0.42 | 92.98 | 0.5 | 92.84 | 92.83 | 88.11 | 88.17 | 20.79 | 3.46 | 3.7 | 5.62 | 5.63 | 91.97 | 1.54 | 1.92 | 0.45 | 92.14 | 92.13 | 90.65 | 90.69 | 3.48 | 4.38
|  | 20 Plus | 270 | 271 | 4.69 | 98.37 | 4.29 | 81.54 | 4.02 | 89.19 | 88.65 | 49.54 | 49.71 | 12.52 | 5.45 | 5.37 | 8.18 | 8.2 | 59.12 | 2.64 | 2.81 | 5.26 | 89.01 | 88.34 | 44.65 | 44.83 | 5.49 | 5.49
| GAS | All Sizes | 745 | 745 | 7.85 | 97.79 | 3.72 | 67.39 | 3.49 | 89.88 | 87.81 | 51.9 | 52.02 | 12.25 | 6.23 | 3.89 | 6.42 | 6.43 | 64.1 | 3.7 | 2.53 | 5.53 | 89.77 | 88.08 | 39.26 | 39.37 | 6.6 | 3.64
| TURBINE** | 1-19 | 127 | 127 | 3.12 | 95.62 | 0.64 | 78.54 | 0.8 | 89.02 | 88.42 | 83.86 | 83.88 | 18.84 | 6.81 | 4.17 | 7.97 | 7.97 | 90.86 | 3.01 | 3.8 | 0.81 | 88.33 | 87.74 | 84.86 | 84.88 | 7.13 | 4.54
|  | 20-49 | 156 | 156 | 5.87 | 97.84 | 2.17 | 66.58 | 2.31 | 90.75 | 85.21 | 66.56 | 66.6 | 14.12 | 4.65 | 4.6 | 6.33 | 6.34 | 73.29 | 2.92 | 1.73 | 3.25 | 90.65 | 85.01 | 56.81 | 56.85 | 5.07 | 4.28
|  | 50 Plus | 458 | 458 | 7.92 | 98.02 | 2.53 | 57.67 | 4.01 | 89.89 | 88.59 | 46.2 | 46.37 | 11.02 | 6.51 | 3.61 | 6.04 | 6.06 | 59.09 | 4.07 | 2.44 | 4.39 | 89.94 | 88.6 | 44.43 | 44.58 | 6.45 | 3.61
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 150 | 146.33 | 76.25 | 98.51 | 53.27 | 80.89 | 53.01 | 85.91 | 83.34 | 6.29 | 7.04 | 5.42 | 10.53 | 3.56 | 5.19 | 5.73 | 9.83 | 8.91 | 1.63 | 65.86 | 88.03 | 85.15 | 3.35 | 4.24 | 9.68 | 2.28
| HYDRO | All Sizes | 975 | 975 | 30.69 | 99.92 | 37.6 | 64.65 | 54.06 | 80.73 | 80.16 | 9.54 | 9.78 | 8.26 | 12.87 | 6.4 | 8.3 | 8.47 | 12.28 | 10.97 | 1.9 | 58.15 | 82.35 | 81.86 | 4.1 | 4.23 | 15 | 2.65
|  | 1-29 | 402 | 402 | 77.2 | 99.84 | 31.75 | 63.28 | 49.23 | 76.39 | 75.96 | 16.41 | 16.8 | 15.29 | 12.13 | 11.48 | 13.24 | 13.52 | 18.85 | 10.38 | 1.75 | 50.16 | 82.87 | 82.3 | 6.62 | 7.22 | 12.75 | 4.38
|  | 30 Plus | 573 | 573 | 22.53 | 99.93 | 38.03 | 64.74 | 57.44 | 83.78 | 83.11 | 4.35 | 4.48 | 3.63 | 13.4 | 2.83 | 4.83 | 4.92 | 7.35 | 11.39 | 2.01 | 58.75 | 82.31 | 81.83 | 3.91 | 4 | 15.17 | 2.52
| PUMPED STORAGE | All Sizes | 111 | 111 | 7.41 | 99.94 | 8.08 | 50 | 25.17 | 82.49 | 82.26 | 7.8 | 7.84 | 5 | 14.2 | 3.31 | 5.41 | 5.43 | 12.18 | 12.1 | 2.1 | 16.17 | 79.9 | 79.28 | 5.78 | 5.94 | 18.06 | 2.03
| MULTIBOILER/MULTI-TURBINE | All Sizes | 14 | 14 | 1149.92 | 100 | 54.23 | 67.06 | 83.49 | 89.21 | 81.83 | 1.53 | 6.8 | 6.43 | 9.49 | 1.3 | 2.06 | 7.96 | 9.3 | 8.73 | 0.76 | 80.86 | 88.61 | 82 | 1.4 | 6.21 | 10.24 | 1.15
| DIESEL** | All Sizes | 86 | 86 | 25.23 | 98.23 | 12.9 | 65.42 | 12.96 | 93.79 | 92.63 | 22.6 | 23.57 | 8.18 | 2.42 | 3.79 | 5.35 | 5.71 | 31.13 | 0.86 | 1.56 | 19.72 | 95.43 | 94.6 | 10.94 | 12.4 | 2.15 | 2.42
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.