## Sheet1
2016 Generating Unit Statistical Brochure -- All Units Reporting
NOTE: This brochure contains data on all units, whether they reported event records or not. For a review of statistics containing only those units that reported events, see the brochure "2016 Generating Unit Statistical Brochure -- Units Reporting Events".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1145 | 1147 | 146.41 | 98.98 | 42.22 | 70.43 | 52.69 | 83.52 | 81.02 | 7.64 | 10.32 | 7.96 | 12.12 | 4.36 | 7.4 | 9.14 | 15.12 | 9.08 | 3.04 | 59.94 | 82.32 | 79.81 | 7.14 | 9.8 | 13.07 | 4.61
| All Fuel Types | 1-99 | 249 | 249 | 119.92 | 99.38 | 29.49 | 63.57 | 43.9 | 86.89 | 84.45 | 8.19 | 10.78 | 7.49 | 9.2 | 3.92 | 6.16 | 7.66 | 15.13 | 6.95 | 2.25 | 46.39 | 86.03 | 83.63 | 7.77 | 10.34 | 10.06 | 3.91
|  | 100-199 | 260 | 260 | 52.8 | 99.58 | 26.28 | 59.31 | 42.28 | 84.77 | 82.06 | 6.47 | 9.27 | 5.85 | 12.3 | 2.92 | 5.86 | 7.26 | 14.94 | 9.37 | 2.94 | 44.31 | 84.43 | 81.66 | 6.55 | 9.39 | 12.46 | 3.11
|  | 200-299 | 133 | 133 | 230.27 | 98.09 | 34.56 | 64.54 | 54 | 82.28 | 80.16 | 8.01 | 10.26 | 8.39 | 13.02 | 4.7 | 8.22 | 9.72 | 15.51 | 9.51 | 3.51 | 53.55 | 82.33 | 80.25 | 8.21 | 10.39 | 12.88 | 4.79
|  | 300-399 | 107 | 108 | 205.76 | 98.6 | 31.43 | 62.83 | 50.57 | 80.6 | 78.41 | 10.42 | 13.12 | 10.38 | 13.51 | 5.89 | 8.7 | 10.36 | 17.37 | 10.7 | 2.81 | 50.02 | 80.63 | 78.49 | 10.41 | 13.06 | 13.56 | 5.81
|  | 400-599 | 192 | 192 | 312.49 | 97.77 | 43.9 | 70.79 | 61.66 | 81.25 | 78.44 | 8.79 | 11.95 | 10.34 | 12.81 | 5.95 | 9.45 | 11.83 | 16.55 | 9.3 | 3.5 | 62.02 | 81.38 | 78.55 | 8.76 | 11.94 | 12.66 | 5.96
|  | 600-799 | 132 | 132 | 481.85 | 96.58 | 49.39 | 75.55 | 65.36 | 83.35 | 80.76 | 5.81 | 8.43 | 7.5 | 12.62 | 4.03 | 7.07 | 9.15 | 12.58 | 9.58 | 3.04 | 65.38 | 83.28 | 80.71 | 5.8 | 8.43 | 12.7 | 4.02
|  | 800-999 | 59 | 59 | 287.82 | 98.34 | 47.96 | 71.79 | 66.33 | 82.88 | 80.78 | 5.54 | 7.98 | 7 | 13.23 | 3.89 | 7.29 | 9.26 | 12.56 | 9.83 | 3.4 | 66.8 | 83.08 | 80.99 | 5.43 | 7.84 | 13.09 | 3.83
|  | 1000 Plus | 13 | 13 | 690.55 | 96.67 | 53.38 | 74.8 | 70.75 | 76.69 | 73.76 | 4.15 | 5.59 | 5.32 | 20.25 | 3.06 | 11.33 | 12.83 | 15.62 | 11.98 | 8.27 | 71.36 | 77.1 | 74.37 | 4.06 | 5.41 | 19.88 | 3.02
| Coal | All Sizes | 682 | 674.5 | 459.16 | 97.38 | 52.1 | 73.57 | 64.46 | 83.26 | 80.61 | 6.58 | 8.96 | 7.94 | 12.2 | 4.54 | 7.8 | 9.66 | 13.33 | 8.94 | 3.26 | 70.82 | 82.54 | 79.92 | 6.21 | 8.56 | 12.78 | 4.69
| Primary | 1-99 | 92 | 90.67 | 212.42 | 98.25 | 34.82 | 73.2 | 42.93 | 87.98 | 86 | 6.18 | 8.05 | 6.21 | 9.19 | 2.83 | 4.56 | 5.81 | 12.05 | 7.46 | 1.73 | 47.57 | 87.73 | 85.84 | 5.21 | 7.08 | 9.66 | 2.61
|  | 100-199 | 144 | 140.5 | 435.61 | 97.48 | 35.93 | 63.19 | 56.49 | 84.75 | 81.45 | 5.62 | 8.2 | 6.85 | 11.89 | 3.36 | 6.98 | 8.65 | 13.55 | 8.27 | 3.62 | 56.86 | 84.81 | 81.48 | 5.88 | 8.69 | 11.64 | 3.55
|  | 200-299 | 89 | 85.75 | 436.49 | 97.07 | 43.51 | 70.75 | 62.22 | 81.48 | 79.1 | 8.26 | 10.17 | 9.02 | 12.91 | 5.61 | 9.21 | 10.66 | 14.9 | 9.31 | 3.6 | 61.5 | 81.84 | 79.48 | 8.6 | 10.49 | 12.38 | 5.79
|  | 300-399 | 63 | 63.42 | 472.75 | 97.59 | 45.54 | 70.17 | 64.62 | 79.53 | 76.79 | 9.72 | 12.44 | 11.18 | 13.51 | 6.96 | 9.92 | 12.02 | 16.08 | 10.55 | 2.96 | 64.89 | 79.66 | 76.93 | 9.59 | 12.28 | 13.46 | 6.88
|  | 400-599 | 134 | 133.25 | 532.15 | 97.22 | 54.81 | 73.48 | 74.44 | 82.46 | 79.52 | 6.56 | 9.4 | 8.84 | 12.32 | 5.22 | 8.56 | 11.02 | 13.25 | 8.98 | 3.34 | 74.59 | 82.59 | 79.62 | 6.49 | 9.37 | 12.23 | 5.18
|  | 600-799 | 106 | 105.92 | 618.52 | 96.91 | 56.26 | 76.53 | 73.3 | 83.42 | 80.8 | 5.41 | 7.72 | 7.21 | 12.39 | 4.19 | 7.43 | 9.46 | 11.69 | 9.15 | 3.23 | 73.51 | 83.37 | 80.74 | 5.39 | 7.72 | 12.45 | 4.19
|  | 800-999 | 42 | 42 | 657.9 | 96.55 | 55.29 | 73.19 | 75.42 | 82.68 | 80.74 | 5.6 | 7.44 | 7.05 | 12.85 | 4.47 | 7.82 | 9.63 | 11.56 | 9.5 | 3.35 | 75.54 | 82.94 | 81.02 | 5.48 | 7.3 | 12.69 | 4.38
|  | 1000 Plus | 12 | 12 | 665.06 | 96.57 | 55.45 | 76.18 | 72.53 | 78.34 | 75.88 | 4.37 | 5.53 | 5.27 | 18.34 | 3.32 | 12.27 | 13.53 | 15.95 | 9.38 | 8.96 | 72.79 | 78.41 | 76.06 | 4.24 | 5.36 | 18.37 | 3.22
| Oil | All Sizes | 60 | 54 | 97.47 | 98.6 | 7.35 | 42.46 | 27.6 | 84.16 | 82.58 | 8.42 | 12.31 | 7.3 | 13.3 | 2.54 | 7.1 | 8.52 | 24.38 | 8.74 | 4.56 | 17.31 | 80.38 | 79.01 | 13.3 | 17.28 | 16.96 | 2.66
| Primary | 1-99 | 16 | 15.83 | 88.3 | 99.88 | 26.21 | 40.26 | 59.73 | 85.07 | 81.62 | 2.47 | 6.98 | 5.23 | 13.41 | 1.52 | 9.18 | 12.62 | 18.31 | 5.74 | 7.67 | 65.09 | 83.2 | 79.23 | 2.46 | 7.07 | 15.15 | 1.64
|  | 100-199 | 14 | 13.25 | 149.88 | 94.77 | 11.53 | 61.64 | 16.38 | 90.52 | 90.06 | 5.83 | 8.31 | 5.48 | 8.47 | 1.01 | 4.47 | 4.93 | 23.51 | 5.01 | 3.46 | 18.7 | 89.79 | 89.29 | 5.11 | 7.52 | 9.2 | 1.01
|  | 200-299 | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
|  | 300-399 | 9 | 9 | 239.13 | 95.6 | 12.57 | 41.83 | 29.28 | 78.41 | 77.71 | 17.54 | 18.11 | 13.92 | 15.36 | 6.23 | 10.04 | 10.26 | 26.03 | 11.55 | 3.81 | 30.04 | 78.82 | 78.09 | 16.13 | 16.71 | 15.41 | 5.78
|  | 400-599 | 8 | 7.17 | 16.46 | 98.71 | 0.62 | 31.05 | 2.01 | 87.71 | 86.53 | 71.11 | 76.06 | 28 | 7.33 | 4.96 | 6.75 | 7.93 | 80.41 | 5.54 | 1.79 | 2 | 88.03 | 86.92 | 70.1 | 75.11 | 7.28 | 4.69
|  | 600-799 | 5 | 5 | 33.54 | 96.49 | 2.55 | 31.92 | 8.4 | 80.87 | 80.42 | 11.54 | 15.37 | 8.47 | 18.03 | 1.1 | 6.07 | 6.52 | 43.9 | 13.06 | 4.98 | 8 | 79.25 | 78.72 | 11.53 | 16.35 | 19.7 | 1.04
|  | 800-999 | 6 | 2.5 | 10.65 | 90.91 | 0.17 | 35.43 | 0.48 | 75.15 | 75.15 | 33.12 | 33.12 | 19.98 | 24.61 | 0.24 | 4.1 | 4.1 | 89.43 | 20.75 | 3.86 | 0.49 | 75.3 | 75.3 | 33.2 | 33.2 | 24.45 | 0.24
| Gas | All Sizes | 333 | 324.42 | 53.56 | 99.35 | 11.78 | 43.08 | 26.31 | 82.33 | 80.47 | 14.9 | 18.37 | 9.61 | 13.06 | 4.61 | 7.56 | 8.86 | 25.62 | 10.11 | 2.95 | 27.34 | 80.06 | 78.06 | 16.06 | 20 | 14.71 | 5.23
| Primary | 1-99 | 92 | 91.25 | 65.34 | 99.6 | 13.3 | 45.91 | 23.49 | 85.42 | 84.26 | 18.83 | 20.45 | 9.72 | 9.13 | 5.45 | 7.94 | 8.52 | 26.67 | 6.64 | 2.49 | 28.97 | 83.68 | 82.56 | 17.1 | 18.07 | 10.34 | 5.97
|  | 100-199 | 100 | 96.25 | 36.31 | 99.53 | 12.13 | 44.13 | 25.74 | 83.42 | 81.12 | 9.86 | 13.68 | 6.85 | 13.77 | 2.82 | 5.15 | 6.42 | 20.4 | 11.43 | 2.34 | 27.48 | 82.52 | 80.05 | 9.81 | 13.4 | 14.49 | 2.99
|  | 200-299 | 43 | 40 | 86.23 | 99.13 | 14.03 | 42.48 | 33.24 | 81.59 | 79.76 | 9.69 | 13.92 | 8.55 | 14.84 | 3.57 | 7.45 | 9.26 | 22.19 | 10.96 | 3.88 | 33.03 | 81.03 | 79.29 | 9.51 | 13.55 | 15.49 | 3.47
|  | 300-399 | 33 | 32.58 | 58.96 | 99.27 | 8.46 | 33.06 | 25.73 | 81.95 | 80.28 | 14.18 | 17.87 | 9.56 | 13.8 | 4.25 | 6.77 | 8.09 | 24.31 | 11.27 | 2.52 | 25.59 | 81.73 | 80.14 | 14.53 | 18.06 | 13.92 | 4.35
|  | 400-599 | 46 | 45.83 | 75.5 | 98.88 | 14.06 | 46.14 | 30.19 | 76.33 | 73.79 | 21.68 | 26.22 | 15.9 | 15.31 | 8.36 | 12.87 | 15.06 | 34.22 | 10.8 | 4.51 | 30.47 | 76.5 | 73.92 | 22 | 26.55 | 14.9 | 8.59
|  | 600-799 | 12 | 12 | 145.68 | 94.41 | 11 | 51.46 | 21.01 | 79.41 | 77.4 | 16.7 | 22.39 | 14.5 | 16.38 | 4.21 | 6.35 | 8.37 | 29.31 | 14.24 | 2.14 | 21.38 | 80.36 | 78.41 | 16.16 | 21.79 | 15.52 | 4.12
|  | 800-999 | 7 | 6.5 | 15.16 | 99.55 | 5.57 | 31.4 | 17.59 | 79.82 | 79.17 | 15.09 | 17.45 | 6.12 | 17.05 | 3.13 | 8.64 | 9.25 | 34.58 | 11.54 | 5.51 | 17.74 | 79.78 | 79.13 | 14.79 | 17.14 | 17.14 | 3.08
| Lignite Primary | All Sizes | 32 | 30.83 | 25.47 | 99.72 | 64.16 | 78.62 | 80.48 | 88.32 | 85.15 | 3.76 | 6.56 | 6.01 | 8.53 | 3.15 | 4.69 | 7.29 | 8.56 | 6.98 | 1.54 | 81.61 | 88.64 | 84.69 | 3.93 | 7.79 | 8.02 | 3.34
| Oil/Gas | All Sizes | 386 | 378.42 | 57.34 | 99.26 | 11.01 | 43.01 | 26.49 | 82.59 | 80.77 | 14.01 | 17.55 | 9.32 | 13.1 | 4.32 | 7.49 | 8.81 | 25.45 | 9.92 | 3.18 | 25.59 | 80.12 | 78.23 | 15.74 | 19.69 | 15.1 | 4.78
| Primary | 1-99 | 108 | 107.08 | 70.99 | 99.68 | 15.64 | 44.03 | 28.84 | 85.37 | 83.87 | 14.44 | 16.88 | 8.73 | 9.76 | 4.87 | 8.12 | 9.12 | 24.4 | 6.51 | 3.26 | 35.51 | 83.6 | 81.96 | 12.75 | 14.82 | 11.21 | 5.19
|  | 100-199 | 113 | 109.5 | 38.43 | 99.43 | 12.06 | 45.4 | 24.71 | 84.2 | 82.1 | 9.58 | 13.31 | 6.66 | 13.18 | 2.62 | 5.08 | 6.26 | 20.64 | 10.72 | 2.46 | 26.57 | 83.27 | 81.01 | 9.48 | 13 | 13.95 | 2.78
|  | 200-299 | 43 | 40.25 | 86 | 99.09 | 13.93 | 42.48 | 33.02 | 81.68 | 79.87 | 9.73 | 13.95 | 8.57 | 14.76 | 3.56 | 7.43 | 9.23 | 22.25 | 10.89 | 3.87 | 32.81 | 81.14 | 79.41 | 9.55 | 13.58 | 15.4 | 3.47
|  | 300-399 | 42 | 41.58 | 70.58 | 99.01 | 9.31 | 35.11 | 26.43 | 81.26 | 79.78 | 14.94 | 17.93 | 10.16 | 14.1 | 4.64 | 7.42 | 8.52 | 24.7 | 11.33 | 2.78 | 26.51 | 81.13 | 79.71 | 14.91 | 17.74 | 14.23 | 4.64
|  | 400-599 | 53 | 53 | 72.6 | 98.86 | 12.2 | 45.98 | 26.13 | 77.98 | 75.63 | 23.14 | 27.89 | 15.99 | 14.16 | 7.87 | 11.99 | 14.03 | 35.91 | 10.04 | 4.12 | 26.53 | 78.1 | 75.72 | 23.29 | 28.02 | 13.85 | 8.05
|  | 600-799 | 17 | 17 | 98.63 | 95.24 | 8.72 | 49.09 | 17.3 | 79.84 | 78.29 | 16 | 21.42 | 13.03 | 16.86 | 3.3 | 6.27 | 7.82 | 31.91 | 13.89 | 2.97 | 17.77 | 80.06 | 78.5 | 15.62 | 21.15 | 16.65 | 3.29
|  | 800-999 | 9 | 9 | 15.1 | 99.41 | 4.02 | 31.45 | 12.83 | 78.52 | 78.05 | 15.33 | 17.66 | 5.64 | 19.16 | 2.32 | 7.37 | 7.82 | 37.97 | 14.1 | 5.05 | 12.78 | 78.49 | 78.03 | 15.05 | 17.36 | 19.24 | 2.26
| NUCLEAR | All Sizes | 99 | 99 | 5176.51 | 97.52 | 91.55 | 99.05 | 92.6 | 92.6 | 90.79 | 2.2 | 2.74 | 2.74 | 5.31 | 2.09 | 2.48 | 3.23 | 3.4 | 4.92 | 0.39 | 92.42 | 92.42 | 90.63 | 2.35 | 2.87 | 5.35 | 2.23
| All Types | 400-799 | 13 | 13 | 5547.93 | 94.81 | 90.53 | 97.41 | 92.82 | 92.82 | 90.74 | 2.14 | 2.64 | 2.64 | 5.15 | 2.03 | 2.73 | 3.37 | 3.53 | 4.45 | 0.7 | 92.94 | 92.94 | 90.88 | 2.07 | 2.59 | 5.1 | 1.97
|  | 800-999 | 33 | 33 | 5563.7 | 97.37 | 93.18 | 99.42 | 93.74 | 93.74 | 92.07 | 1.34 | 2.06 | 2.06 | 4.99 | 1.27 | 1.62 | 2.65 | 2.78 | 4.63 | 0.35 | 93.72 | 93.72 | 92.07 | 1.36 | 2.06 | 4.98 | 1.29
|  | 1000 Plus | 53 | 53 | 4918.93 | 97.62 | 90.91 | 99.09 | 91.84 | 91.84 | 90.01 | 2.76 | 3.19 | 3.19 | 5.55 | 2.61 | 2.95 | 3.56 | 3.76 | 5.21 | 0.34 | 91.74 | 91.74 | 89.93 | 2.86 | 3.28 | 5.56 | 2.7
| PWR | All Sizes | 62 | 62 | 5317.27 | 97.44 | 91.79 | 99.57 | 92.14 | 92.14 | 90.86 | 2.39 | 2.71 | 2.71 | 5.6 | 2.26 | 2.54 | 2.97 | 3.13 | 5.33 | 0.28 | 92.19 | 92.19 | 90.87 | 2.35 | 2.68 | 5.6 | 2.22
|  | 400-799 | 5 | 5 | 7924.31 | 100 | 91.98 | 99.78 | 91.77 | 91.77 | 90.42 | 3.79 | 3.86 | 3.86 | 4.62 | 3.61 | 4.11 | 4.23 | 4.42 | 4.13 | 0.49 | 92.19 | 92.19 | 90.92 | 3.62 | 3.71 | 4.35 | 3.46
|  | 800-999 | 22 | 22 | 4707.58 | 97.74 | 92.83 | 100.18 | 92.72 | 92.72 | 91.8 | 1.66 | 1.89 | 1.89 | 5.72 | 1.56 | 1.99 | 2.39 | 2.53 | 5.29 | 0.43 | 92.67 | 92.67 | 91.74 | 1.7 | 1.93 | 5.73 | 1.6
|  | 1000 Plus | 35 | 35 | 5524.61 | 96.69 | 91.28 | 99.27 | 91.83 | 91.83 | 90.33 | 2.66 | 3.06 | 3.06 | 5.67 | 2.51 | 2.66 | 3.15 | 3.33 | 5.52 | 0.15 | 91.96 | 91.96 | 90.45 | 2.57 | 2.97 | 5.62 | 2.42
| BWR | All Sizes | 32 | 32 | 4610.84 | 98.34 | 91.18 | 98.26 | 93.43 | 93.43 | 90.61 | 2.15 | 3.13 | 3.13 | 4.51 | 2.05 | 2.72 | 4.15 | 4.32 | 3.84 | 0.67 | 92.8 | 92.8 | 90.1 | 2.58 | 3.45 | 4.75 | 2.45
|  | 400-799 | 4 | 4 | 3361.07 | 90.91 | 91.58 | 95.7 | 95.66 | 95.66 | 92.93 | 1.92 | 2.96 | 2.96 | 2.47 | 1.87 | 3.52 | 4.93 | 4.97 | 0.82 | 1.65 | 95.7 | 95.7 | 93.01 | 2 | 3.03 | 2.35 | 1.95
|  | 800-999 | 10 | 10 | 7616.05 | 100 | 93.4 | 97.84 | 95.37 | 95.37 | 91.87 | 0.79 | 2.64 | 2.64 | 3.86 | 0.76 | 0.97 | 3.47 | 3.6 | 3.65 | 0.21 | 95.47 | 95.47 | 92.09 | 0.77 | 2.54 | 3.79 | 0.74
|  | 1000 Plus | 18 | 18 | 4034.62 | 100 | 90.2 | 98.76 | 91.86 | 91.86 | 89.39 | 2.96 | 3.44 | 3.44 | 5.33 | 2.81 | 3.51 | 4.36 | 4.58 | 4.62 | 0.71 | 91.34 | 91.34 | 88.92 | 3.41 | 3.88 | 5.43 | 3.23
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 263 | 263 | 6.1 | 98.75 | 5.09 | 73.09 | 5.37 | 90.5 | 89.24 | 26.89 | 29.43 | 9.23 | 6.97 | 2.53 | 5.85 | 6.37 | 47.69 | 3.65 | 3.32 | 6.97 | 90.25 | 88.37 | 24.16 | 27.84 | 6.96 | 2.78
| ENGINE** | 1-19 | 27 | 27 | 1.6 | 96.58 | 0.18 | 78.51 | 0.24 | 88.83 | 88.83 | 82.97 | 83.05 | 18.49 | 10.02 | 1.15 | 5.25 | 5.25 | 95.79 | 5.92 | 4.1 | 0.23 | 87.74 | 87.74 | 84.63 | 84.71 | 11.01 | 1.25
|  | 20 Plus | 236 | 236 | 6.17 | 98.77 | 5.31 | 73.08 | 5.97 | 90.69 | 89.29 | 26.02 | 28.63 | 9.18 | 6.62 | 2.69 | 5.92 | 6.5 | 45.55 | 3.39 | 3.23 | 7.27 | 90.36 | 88.4 | 23.83 | 27.54 | 6.79 | 2.85
| GAS | All Sizes | 704 | 703.25 | 9.38 | 98.38 | 6.29 | 75.4 | 5.27 | 90.22 | 88.59 | 36.79 | 39.52 | 9.05 | 6.72 | 3.07 | 5.61 | 6 | 53.33 | 4.17 | 2.55 | 8.34 | 90.78 | 89.25 | 22.78 | 25.37 | 6.76 | 2.46
| TURBINE** | 1-19 | 108 | 108 | 3.28 | 96.5 | 0.88 | 73.89 | 1.15 | 89.37 | 88.86 | 76.9 | 77.18 | 14.46 | 6.78 | 3.84 | 8.05 | 8.11 | 87.56 | 2.57 | 4.21 | 1.19 | 89.33 | 88.89 | 76.68 | 76.95 | 6.75 | 3.92
|  | 20-49 | 134 | 133.25 | 5.94 | 98.97 | 4.64 | 89.66 | 3.42 | 90.88 | 88.49 | 49.66 | 51.02 | 8.64 | 5.74 | 3.38 | 5.68 | 5.86 | 63.19 | 3.44 | 2.3 | 5.17 | 90.64 | 88.14 | 35.66 | 37.12 | 6.49 | 2.87
|  | 50 Plus | 462 | 462 | 11.06 | 98.48 | 6.64 | 74.67 | 6.68 | 90.21 | 88.57 | 29.66 | 33.1 | 8.4 | 6.97 | 2.81 | 5.07 | 5.58 | 45.63 | 4.72 | 2.25 | 8.89 | 90.85 | 89.36 | 21.02 | 23.75 | 6.78 | 2.37
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 277 | 276.75 | 86.38 | 98.63 | 56.2 | 80.59 | 58.03 | 87.82 | 85.24 | 3.72 | 4.69 | 3.72 | 9.94 | 2.24 | 3.87 | 4.61 | 7.43 | 8.31 | 1.63 | 69.73 | 88.37 | 85.34 | 2.06 | 3.13 | 10.16 | 1.47
| HYDRO | All Sizes | 1056 | 1047 | 25.75 | 99.95 | 40.39 | 64.32 | 62.93 | 80.89 | 80.53 | 8.61 | 8.73 | 7.28 | 13.03 | 6.08 | 7.97 | 8.07 | 11.12 | 11.15 | 1.88 | 62.79 | 82.58 | 82.26 | 4.32 | 4.4 | 14.5 | 2.92
|  | 1-29 | 398 | 389 | 104.19 | 99.86 | 35.57 | 54.06 | 61.31 | 75.37 | 75.09 | 15.42 | 15.58 | 13.59 | 13.26 | 11.36 | 13.34 | 13.5 | 17.85 | 11.28 | 1.98 | 65.8 | 82.46 | 82.16 | 6.08 | 6.31 | 13.18 | 4.36
|  | 30 Plus | 658 | 658 | 18.04 | 99.97 | 40.71 | 65.03 | 63.88 | 84.15 | 83.75 | 4.3 | 4.39 | 3.59 | 12.89 | 2.96 | 4.79 | 4.86 | 6.86 | 11.06 | 1.83 | 62.59 | 82.59 | 82.27 | 4.2 | 4.27 | 14.59 | 2.82
| PUMPED STORAGE | All Sizes | 111 | 111 | 9.21 | 99.92 | 7.91 | 44.7 | 27.5 | 80.74 | 80.6 | 8.37 | 8.38 | 5.99 | 15.36 | 3.9 | 6.04 | 6.04 | 12.38 | 13.23 | 2.13 | 17.7 | 79.37 | 79.01 | 9.6 | 9.6 | 16.94 | 3.69
| MULTIBOILER/MULTI-TURBINE | All Sizes | 22 | 22 | 314.96 | 98.51 | 33.81 | 65.37 | 66.03 | 86.12 | 78.92 | 2.53 | 8.88 | 7.25 | 12.17 | 1.72 | 3.93 | 9.16 | 12.97 | 9.96 | 2.21 | 51.73 | 80.86 | 77.27 | 3.26 | 6.94 | 17.4 | 1.74
| DIESEL** | All Sizes | 133 | 133 | 7.73 | 99.41 | 7.82 | 60.62 | 5 | 94.11 | 93.61 | 17.08 | 19.48 | 6.07 | 4.86 | 1.03 | 3.24 | 3.46 | 40.84 | 2.65 | 2.21 | 12.9 | 91.14 | 90.17 | 10.93 | 12.67 | 7.28 | 1.58
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.