## Brochure 3 2011-2015
2015 Generating Unit Statistical Brochure -- Five Years, 2011 - 2015, Units Reporting Events
NOTE: This brochure contains data on units reporting events only. For a review of statistics containing all units that reported, see the brochure "2011-2015 Generating Unit Statistical Brochure -- All Units Reporting".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1571 | 6392.58 | 202.06 | 98.43 | 47.49 | 74.11 | 55.32 | 84.7 | 82.32 | 8.08 | 10.47 | 8.4 | 10.44 | 4.86 | 7.74 | 9.46 | 14.93 | 7.55 | 2.88 | 64.08 | 83.75 | 81.37 | 6.9 | 9.14 | 11.5 | 4.75
| All Fuel Types | 1-99 | 419 | 1519.58 | 145.13 | 98.81 | 27.47 | 64.73 | 40.25 | 86.14 | 83.97 | 12.28 | 14.86 | 10.09 | 8.19 | 5.63 | 8.39 | 9.76 | 19.91 | 5.44 | 2.75 | 42.43 | 86.39 | 84.27 | 10.85 | 13.4 | 8.44 | 5.16
|  | 100-199 | 385 | 1581.58 | 114.99 | 99.07 | 32.39 | 63.92 | 49.36 | 86.36 | 83.94 | 7.18 | 9.58 | 6.95 | 9.82 | 3.82 | 6.52 | 8.08 | 14.36 | 7.11 | 2.71 | 50.67 | 86.12 | 83.66 | 6.92 | 9.36 | 10.11 | 3.77
|  | 200-299 | 191 | 762.5 | 228.48 | 98.21 | 39.14 | 65.6 | 59.26 | 82.35 | 79.58 | 9.15 | 11.85 | 9.86 | 11.69 | 5.97 | 9.32 | 11.47 | 16.64 | 8.33 | 3.36 | 59.66 | 82.58 | 79.82 | 8.81 | 11.49 | 11.66 | 5.77
|  | 300-399 | 125 | 548.92 | 234.83 | 97.5 | 36.84 | 66.28 | 56.08 | 83.67 | 81.73 | 6.94 | 9.06 | 7.52 | 12.15 | 4.18 | 6.92 | 8.45 | 13.36 | 9.41 | 2.74 | 55.59 | 83.61 | 81.7 | 6.95 | 9.04 | 12.24 | 4.15
|  | 400-599 | 231 | 995.5 | 340.82 | 97.5 | 49.85 | 74.16 | 66.95 | 83.76 | 81.14 | 7.02 | 9.58 | 8.51 | 11.19 | 5.05 | 8 | 10.08 | 13.41 | 8.25 | 2.94 | 67.22 | 83.64 | 80.99 | 7.11 | 9.69 | 11.21 | 5.15
|  | 600-799 | 142 | 632.33 | 560.57 | 96.63 | 56.86 | 78.92 | 72.02 | 83.91 | 81.47 | 6.31 | 8.37 | 7.78 | 11.24 | 4.85 | 7.84 | 9.83 | 12.28 | 8.25 | 2.99 | 72.05 | 83.93 | 81.49 | 6.25 | 8.31 | 11.27 | 4.8
|  | 800-999 | 62 | 282.17 | 341.73 | 97.47 | 54.84 | 80.03 | 68.21 | 83.39 | 81.57 | 5.45 | 7.26 | 6.52 | 12.68 | 3.94 | 6.49 | 8.15 | 10.89 | 10.12 | 2.56 | 68.53 | 83.54 | 81.75 | 5.4 | 7.17 | 12.55 | 3.91
|  | 1000 Plus | 16 | 65 | 776.53 | 92.26 | 61.49 | 83.29 | 72.91 | 78.45 | 75.77 | 7.6 | 9.04 | 8.66 | 15.55 | 6 | 10.42 | 12.17 | 14.6 | 11.13 | 4.42 | 73.82 | 78.58 | 75.97 | 7.39 | 8.83 | 15.52 | 5.89
| Coal | All Sizes | 989 | 4084.08 | 343.02 | 97.88 | 58.48 | 78.39 | 66.5 | 85.28 | 82.75 | 6.49 | 8.6 | 7.57 | 10.11 | 4.61 | 7.73 | 9.55 | 12.83 | 7 | 3.11 | 74.6 | 84.4 | 81.9 | 5.88 | 7.81 | 10.94 | 4.66
| Primary | 1-99 | 198 | 691.67 | 181.72 | 98.64 | 34.82 | 71.81 | 45.39 | 87.24 | 85.43 | 9.45 | 11.72 | 8.68 | 8.02 | 4.74 | 8.15 | 9.46 | 17.55 | 4.61 | 3.41 | 48.48 | 87.82 | 85.99 | 8 | 10.3 | 7.96 | 4.22
|  | 100-199 | 260 | 1046.58 | 187.97 | 98.78 | 42.56 | 69.55 | 60.27 | 87.46 | 84.64 | 5.57 | 7.76 | 6.31 | 8.99 | 3.56 | 6.58 | 8.29 | 12.33 | 5.96 | 3.03 | 61.19 | 87.29 | 84.47 | 5.47 | 7.7 | 9.16 | 3.54
|  | 200-299 | 133 | 562.75 | 473.19 | 96.93 | 46.61 | 71.13 | 65.11 | 82.12 | 78.9 | 8.99 | 11.76 | 10.49 | 11.46 | 6.43 | 10.09 | 12.53 | 16.6 | 7.8 | 3.66 | 65.53 | 82.44 | 79.22 | 8.61 | 11.37 | 11.39 | 6.17
|  | 300-399 | 71 | 320.83 | 512.36 | 95.86 | 53.81 | 74.42 | 72.07 | 84.4 | 81.92 | 5.65 | 7.82 | 7.21 | 11.28 | 4.31 | 7.39 | 9.37 | 11.78 | 8.2 | 3.08 | 72.31 | 84.49 | 82.03 | 5.64 | 7.78 | 11.19 | 4.32
|  | 400-599 | 152 | 682.5 | 604.15 | 96.87 | 63.68 | 79.78 | 79.82 | 84.86 | 82.3 | 5.35 | 7.37 | 7.09 | 10.62 | 4.52 | 7.21 | 9.14 | 10.49 | 7.92 | 2.7 | 79.82 | 84.79 | 82.19 | 5.38 | 7.43 | 10.67 | 4.54
|  | 600-799 | 115 | 513.42 | 703.75 | 96.48 | 63.87 | 80.26 | 79.44 | 84.63 | 82.23 | 5.6 | 7.32 | 7.04 | 10.66 | 4.71 | 7.59 | 9.49 | 10.89 | 7.78 | 2.88 | 79.58 | 84.7 | 82.3 | 5.58 | 7.29 | 10.6 | 4.7
|  | 800-999 | 45 | 201.33 | 762.59 | 95.59 | 64.27 | 82.16 | 78.18 | 83.57 | 81.76 | 5.68 | 7.1 | 6.83 | 11.73 | 4.71 | 7.45 | 9.09 | 10.62 | 8.98 | 2.74 | 78.22 | 83.76 | 81.98 | 5.6 | 6.99 | 11.6 | 4.64
|  | 1000 Plus | 15 | 60 | 822.85 | 91.78 | 64.66 | 84.32 | 76.51 | 79.03 | 76.27 | 6.5 | 7.92 | 7.75 | 15.64 | 5.32 | 9.48 | 11.24 | 13.07 | 11.49 | 4.16 | 76.68 | 79.05 | 76.38 | 6.53 | 7.95 | 15.59 | 5.36
| Oil | All Sizes | 124 | 376.17 | 88.07 | 98.54 | 8.37 | 42.29 | 25.41 | 84.5 | 83.33 | 12.9 | 15.8 | 9.91 | 11.61 | 3.76 | 6.88 | 7.9 | 24.14 | 8.49 | 3.12 | 19.78 | 80.03 | 78.91 | 18.13 | 21.27 | 15.58 | 4.38
| Primary | 1-99 | 35 | 122.5 | 79.74 | 99.07 | 22.87 | 47.89 | 40.77 | 89.76 | 88.52 | 4.33 | 6.49 | 4.1 | 8 | 1.85 | 4.96 | 5.97 | 13.03 | 4.88 | 3.12 | 47.76 | 89.36 | 87.94 | 3.8 | 6.22 | 8.64 | 1.89
|  | 100-199 | 25 | 81.5 | 94.27 | 98.77 | 8.27 | 47.46 | 15.77 | 85.5 | 84.05 | 29.12 | 33.66 | 16.51 | 8.02 | 6.48 | 8.74 | 10.12 | 39.92 | 5.76 | 2.26 | 17.43 | 85.15 | 83.53 | 25.41 | 30.3 | 8.91 | 5.94
|  | 200-299 | 8 | 11 | 63.49 | 86.84 | 3.09 | 47.85 | 6.31 | 93.18 | 91.85 | 22.04 | 33.26 | 16.93 | 5.04 | 1.78 | 3.77 | 5.1 | 45.38 | 3.05 | 1.98 | 6.47 | 92.87 | 91.37 | 23.36 | 35.4 | 5.16 | 1.97
|  | 300-399 | 15 | 65.33 | 169.11 | 97.32 | 12.44 | 42.33 | 28.92 | 79.83 | 79.15 | 6.93 | 8.53 | 6.16 | 18.02 | 2.15 | 4.61 | 5.2 | 15.41 | 15.56 | 2.45 | 29.39 | 79.71 | 79.02 | 6.95 | 8.53 | 18.1 | 2.2
|  | 400-599 | 20 | 46.08 | 96.13 | 98.71 | 6.38 | 33.25 | 18.47 | 84.04 | 82.81 | 23.21 | 25.67 | 15.06 | 10.37 | 5.58 | 10.05 | 11 | 37.94 | 5.91 | 4.47 | 19.18 | 83.44 | 82.19 | 24.79 | 27.14 | 10.24 | 6.32
|  | 600-799 | 13 | 30.08 | 32.69 | 98.32 | 5.32 | 48.87 | 10.93 | 78.21 | 76.91 | 32.33 | 37.75 | 26.17 | 16.57 | 5.22 | 10.02 | 11.24 | 51.46 | 11.77 | 4.8 | 10.89 | 77.39 | 76.03 | 30.74 | 36.61 | 17.78 | 4.84
|  | 800-999 | 7 | 14.67 | 44.42 | 91.96 | 0.5 | 25.25 | 1.97 | 69.49 | 69.08 | 31.44 | 40.52 | 16.61 | 29.6 | 0.91 | 2.85 | 3.26 | 62.88 | 27.65 | 1.95 | 1.96 | 69.97 | 69.56 | 31.37 | 40.41 | 29.13 | 0.9
| Gas | All Sizes | 469 | 1561.92 | 66.08 | 98.81 | 12.04 | 36.88 | 28.02 | 83.05 | 81.38 | 16.58 | 19.78 | 10.67 | 11.38 | 5.57 | 7.99 | 9.31 | 25.44 | 8.96 | 2.42 | 32.65 | 81.59 | 79.53 | 13.86 | 17.77 | 13.16 | 5.25
| Primary | 1-99 | 155 | 492.58 | 69.35 | 98.65 | 8.86 | 43.97 | 16.61 | 84.63 | 83.39 | 30.27 | 32.55 | 13.6 | 8.16 | 7.21 | 9.17 | 9.93 | 37.66 | 6.2 | 1.95 | 20.15 | 84.04 | 82.58 | 26.08 | 28.45 | 8.85 | 7.11
|  | 100-199 | 118 | 434.58 | 54.27 | 99.2 | 11.7 | 38.36 | 29.59 | 84 | 82.41 | 11.99 | 14.93 | 8.01 | 11.96 | 4.03 | 6.07 | 7.32 | 20.24 | 9.93 | 2.04 | 30.49 | 83.6 | 81.86 | 11.65 | 14.7 | 12.38 | 4.02
|  | 200-299 | 58 | 165.25 | 72.29 | 99.22 | 15.14 | 35.8 | 41.98 | 81.53 | 80.13 | 11.23 | 13.52 | 8.8 | 13.16 | 5.31 | 8.06 | 9.34 | 18.5 | 10.41 | 2.75 | 42.31 | 81.48 | 80.1 | 11.07 | 13.3 | 13.25 | 5.27
|  | 300-399 | 44 | 154.75 | 62.19 | 98.52 | 10.49 | 34.72 | 30.18 | 83.17 | 81.82 | 14.11 | 16.42 | 9.76 | 11.87 | 4.96 | 7.13 | 8.12 | 21.45 | 9.71 | 2.17 | 30.22 | 83.09 | 81.75 | 13.89 | 16.17 | 12.04 | 4.87
|  | 400-599 | 69 | 237.58 | 87.21 | 98.07 | 12.8 | 36.05 | 35.44 | 79.99 | 77.14 | 15.77 | 20.91 | 13.28 | 13.38 | 6.64 | 10.13 | 12.67 | 27.33 | 9.89 | 3.49 | 35.52 | 79.74 | 76.86 | 16.24 | 21.39 | 13.37 | 6.89
|  | 600-799 | 16 | 46.83 | 214.02 | 94.62 | 12.9 | 40.42 | 30.96 | 79 | 76 | 13.35 | 20.33 | 13.89 | 16.23 | 4.77 | 8.94 | 11.91 | 28.99 | 12.06 | 4.17 | 31.9 | 79.34 | 76.3 | 12.81 | 19.75 | 15.98 | 4.69
|  | 800-999 | 9 | 30.33 | 32.61 | 99.06 | 9.85 | 34.89 | 28.12 | 83.26 | 82.35 | 2.02 | 4.35 | 2.28 | 16.16 | 0.58 | 3.81 | 4.54 | 13.92 | 12.93 | 3.23 | 28.22 | 83.13 | 82.21 | 1.98 | 4.28 | 16.3 | 0.57
| Lignite Primary | All Sizes | 33 | 121.17 | 106.22 | 99.35 | 69.97 | 84.28 | 83.1 | 87.47 | 83.84 | 4.2 | 7.59 | 7.25 | 8.89 | 3.64 | 5.25 | 8.34 | 9.44 | 7.28 | 1.61 | 83.02 | 87.63 | 83.92 | 4.54 | 8.24 | 8.42 | 3.95
| Oil/Gas | All Sizes | 561 | 1938.08 | 69.3 | 98.77 | 11.17 | 37.74 | 27.49 | 83.34 | 81.77 | 15.92 | 19.07 | 10.53 | 11.43 | 5.21 | 7.77 | 9.03 | 25.2 | 8.87 | 2.56 | 29.58 | 81.22 | 79.38 | 14.57 | 18.35 | 13.74 | 5.04
| Primary | 1-99 | 186 | 615.08 | 73.14 | 98.81 | 12.06 | 45.58 | 21.78 | 85.73 | 84.49 | 21.78 | 24.1 | 11.1 | 8.12 | 6.06 | 8.27 | 9.08 | 29.75 | 5.92 | 2.2 | 26.45 | 85.26 | 83.8 | 18.29 | 20.75 | 8.8 | 5.92
|  | 100-199 | 140 | 516.08 | 56.43 | 99.18 | 11.15 | 39.25 | 27.41 | 84.24 | 82.66 | 13.88 | 17.03 | 8.85 | 11.34 | 4.42 | 6.49 | 7.76 | 22.52 | 9.27 | 2.07 | 28.41 | 83.85 | 82.13 | 13.22 | 16.52 | 11.82 | 4.33
|  | 200-299 | 64 | 176.25 | 72.19 | 99.05 | 14.35 | 35.93 | 39.7 | 82.28 | 80.88 | 11.36 | 13.77 | 8.74 | 12.64 | 5.09 | 7.78 | 9.07 | 18.91 | 9.94 | 2.7 | 39.93 | 82.24 | 80.85 | 11.22 | 13.61 | 12.72 | 5.05
|  | 300-399 | 55 | 220.08 | 76.3 | 98.36 | 11.11 | 37.11 | 29.8 | 82.16 | 81.01 | 12.13 | 14.25 | 8.81 | 13.72 | 4.11 | 6.37 | 7.24 | 19.77 | 11.47 | 2.25 | 29.95 | 82 | 80.88 | 11.82 | 13.91 | 13.98 | 4.02
|  | 400-599 | 78 | 283.67 | 88.02 | 98.13 | 11.69 | 35.76 | 32.5 | 80.69 | 78.12 | 16.57 | 21.42 | 13.23 | 12.86 | 6.45 | 10.11 | 12.38 | 28.55 | 9.2 | 3.66 | 32.69 | 80.38 | 77.78 | 17.2 | 22.03 | 12.83 | 6.79
|  | 600-799 | 26 | 76.92 | 104.55 | 96.83 | 10.08 | 41.84 | 23 | 78.68 | 76.36 | 17.7 | 24.42 | 17.05 | 16.37 | 4.95 | 9.37 | 11.64 | 34.83 | 11.95 | 4.42 | 24.09 | 78.61 | 76.2 | 16.44 | 23.26 | 16.65 | 4.74
|  | 800-999 | 11 | 45 | 32.9 | 98.86 | 6.72 | 34.57 | 19.61 | 78.78 | 78.03 | 3.38 | 6.18 | 2.9 | 20.54 | 0.69 | 3.5 | 4.12 | 17.41 | 17.72 | 2.81 | 19.45 | 78.74 | 77.99 | 3.37 | 6.16 | 20.58 | 0.68
| NUCLEAR | All Sizes | 105 | 498.75 | 3763.78 | 98.57 | 88.4 | 98.43 | 89.36 | 89.38 | 87.55 | 3.17 | 3.8 | 3.8 | 7.7 | 2.93 | 3.36 | 4.2 | 4.53 | 7.26 | 0.43 | 89.81 | 89.82 | 87.99 | 2.96 | 3.58 | 7.44 | 2.74
| All Types | 400-799 | 15 | 70 | 2927.28 | 99.6 | 82.31 | 96.97 | 84.28 | 84.35 | 81.92 | 5.27 | 6.27 | 6.27 | 10.96 | 4.69 | 5.26 | 6.47 | 7.23 | 10.39 | 0.57 | 84.88 | 84.94 | 82.5 | 4.65 | 5.69 | 10.92 | 4.14
|  | 800-999 | 36 | 169.75 | 4361.45 | 96.77 | 89.71 | 99.55 | 90.03 | 90.03 | 88.75 | 3.04 | 3.46 | 3.46 | 7.15 | 2.82 | 3.19 | 3.8 | 4.07 | 6.78 | 0.37 | 90.12 | 90.12 | 88.88 | 3.04 | 3.45 | 7.06 | 2.82
|  | 1000 Plus | 54 | 259 | 3716.87 | 98.6 | 88.6 | 98.07 | 90.3 | 90.3 | 88.28 | 2.72 | 3.38 | 3.38 | 7.17 | 2.52 | 2.96 | 3.86 | 4.13 | 6.73 | 0.44 | 90.34 | 90.35 | 88.32 | 2.7 | 3.36 | 7.15 | 2.5
| PWR | All Sizes | 65 | 309.75 | 3857.07 | 98.03 | 87.5 | 98.57 | 88.14 | 88.14 | 86.71 | 4.15 | 4.62 | 4.62 | 8.04 | 3.82 | 4.12 | 4.69 | 5.08 | 7.74 | 0.3 | 88.76 | 88.77 | 87.31 | 3.77 | 4.26 | 7.76 | 3.48
|  | 400-799 | 5 | 25 | 2529.22 | 100 | 79.26 | 98.87 | 78.49 | 78.49 | 76.89 | 10.79 | 10.99 | 10.99 | 12.02 | 9.49 | 10.57 | 11.05 | 12.41 | 10.94 | 1.07 | 80.17 | 80.17 | 78.62 | 9.2 | 9.39 | 11.71 | 8.12
|  | 800-999 | 23 | 109.75 | 4318.77 | 97.27 | 88.29 | 99.73 | 88.4 | 88.4 | 87.34 | 4.03 | 4.4 | 4.4 | 7.89 | 3.71 | 3.93 | 4.39 | 4.76 | 7.67 | 0.22 | 88.52 | 88.52 | 87.49 | 4.04 | 4.4 | 7.75 | 3.72
|  | 1000 Plus | 37 | 175 | 3852.41 | 98.06 | 87.71 | 98.01 | 89.37 | 89.37 | 87.73 | 3.32 | 3.89 | 3.89 | 7.56 | 3.07 | 3.31 | 3.96 | 4.27 | 7.32 | 0.24 | 89.49 | 89.5 | 87.85 | 3.27 | 3.85 | 7.48 | 3.03
| BWR | All Sizes | 33 | 162 | 3652.78 | 98.67 | 90.99 | 98.42 | 92.52 | 92.52 | 90.07 | 1.46 | 2.28 | 2.28 | 6.11 | 1.37 | 2.02 | 3.31 | 3.5 | 5.46 | 0.64 | 92.44 | 92.44 | 89.97 | 1.46 | 2.26 | 6.18 | 1.37
|  | 400-799 | 5 | 24 | 2655.21 | 98.68 | 88 | 96.79 | 90.88 | 90.88 | 87.97 | 2.61 | 3.9 | 3.9 | 6.68 | 2.44 | 2.75 | 4.5 | 4.81 | 6.37 | 0.31 | 90.92 | 90.92 | 88.06 | 2.64 | 3.91 | 6.61 | 2.47
|  | 800-999 | 11 | 54 | 4859.49 | 96.02 | 93.09 | 99.37 | 93.7 | 93.7 | 91.98 | 0.92 | 1.47 | 1.47 | 5.43 | 0.87 | 1.35 | 2.26 | 2.37 | 4.95 | 0.49 | 93.67 | 93.67 | 92.01 | 0.94 | 1.49 | 5.43 | 0.89
|  | 1000 Plus | 17 | 84 | 3469.42 | 100 | 90.42 | 98.2 | 92.23 | 92.23 | 89.44 | 1.49 | 2.34 | 2.34 | 6.37 | 1.4 | 2.24 | 3.64 | 3.85 | 5.53 | 0.84 | 92.08 | 92.08 | 89.27 | 1.54 | 2.39 | 6.48 | 1.44
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 331 | 1518.08 | 4.5 | 98.53 | 3.82 | 80.25 | 3.44 | 90.04 | 88.61 | 46.37 | 48.46 | 11.73 | 5.72 | 4.24 | 7.45 | 7.96 | 60.95 | 2.51 | 3.21 | 4.76 | 89.49 | 87.63 | 41.65 | 44.78 | 5.93 | 4.59
| ENGINE** | 1-19 | 39 | 184.08 | 7.01 | 95.66 | 0.23 | 26.5 | 0.87 | 92.41 | 91.2 | 77.24 | 78.69 | 22.14 | 4.63 | 2.97 | 6.27 | 6.53 | 88.25 | 1.32 | 3.31 | 0.87 | 92.08 | 90.8 | 79.09 | 80.24 | 4.62 | 3.3
|  | 20 Plus | 292 | 1334 | 4.45 | 98.59 | 4.01 | 80.74 | 3.78 | 89.73 | 88.27 | 44.76 | 46.83 | 11.62 | 5.86 | 4.41 | 7.6 | 8.15 | 58.99 | 2.67 | 3.19 | 4.97 | 89.35 | 87.46 | 40.93 | 44.1 | 5.99 | 4.65
| GAS | All Sizes | 876 | 3787.5 | 7.88 | 97.76 | 4.1 | 72.6 | 3.41 | 89.58 | 87.03 | 56.35 | 57.07 | 11.95 | 5.98 | 4.44 | 6.62 | 6.74 | 66.24 | 3.8 | 2.18 | 5.65 | 90.5 | 88.42 | 36.52 | 37.36 | 6.24 | 3.27
| TURBINE** | 1-19 | 169 | 676 | 3.66 | 95.5 | 0.67 | 64.17 | 1 | 85.02 | 83.15 | 89.09 | 89.29 | 20.49 | 6.83 | 8.15 | 11.11 | 11.24 | 91.88 | 3.87 | 2.96 | 1.04 | 85.18 | 83.08 | 88.7 | 88.89 | 6.65 | 8.18
|  | 20-49 | 217 | 836 | 4.91 | 97.33 | 1.7 | 72.9 | 1.59 | 90.68 | 85.12 | 77.27 | 77.66 | 14.8 | 3.9 | 5.42 | 6.8 | 6.91 | 81.24 | 2.52 | 1.38 | 2.33 | 90.85 | 84.86 | 67.33 | 67.93 | 4.35 | 4.8
|  | 50 Plus | 489 | 2271.5 | 9.17 | 98.21 | 4.53 | 72.65 | 4.75 | 90.48 | 88.82 | 38.77 | 39.77 | 9.19 | 6.48 | 3.04 | 5.28 | 5.4 | 53.01 | 4.24 | 2.24 | 6.24 | 90.72 | 89.07 | 31.37 | 32.24 | 6.42 | 2.86
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 309 | 1234.42 | 74.36 | 98.76 | 51.59 | 78.64 | 54.4 | 87.65 | 84.63 | 4.71 | 5.79 | 4.44 | 9.65 | 2.69 | 4.37 | 5.2 | 8.79 | 7.98 | 1.68 | 65.61 | 88.63 | 85.58 | 2.82 | 3.81 | 9.47 | 1.9
| HYDRO | All Sizes | 1141 | 4908.5 | 35.89 | 99.92 | 40.42 | 67.05 | 57.99 | 82.25 | 81.89 | 7.44 | 7.63 | 6.76 | 12.52 | 5.23 | 6.97 | 7.11 | 9.87 | 10.78 | 1.74 | 60.28 | 82.74 | 82.43 | 3.77 | 3.89 | 14.73 | 2.53
|  | 1-29 | 463 | 2068.83 | 116.7 | 99.78 | 35.83 | 64.8 | 55.06 | 79.51 | 79.15 | 11.87 | 12.18 | 11.61 | 11.82 | 8.67 | 10.36 | 10.6 | 14.18 | 10.13 | 1.69 | 55.3 | 84.21 | 83.75 | 5.84 | 6.33 | 11.61 | 4.18
|  | 30 Plus | 678 | 2839.67 | 24.59 | 99.94 | 40.77 | 67.21 | 60.12 | 84.24 | 83.88 | 4 | 4.1 | 3.49 | 13.02 | 2.73 | 4.51 | 4.58 | 6.54 | 11.25 | 1.78 | 60.66 | 82.63 | 82.33 | 3.6 | 3.69 | 14.97 | 2.4
| PUMPED STORAGE | All Sizes | 114 | 509.92 | 7.95 | 99.75 | 8.56 | 44.16 | 27.26 | 82.61 | 82.38 | 9.15 | 9.22 | 6.58 | 13.03 | 4.36 | 6.06 | 6.1 | 12.35 | 11.33 | 1.7 | 19.38 | 80.93 | 80.29 | 10.69 | 10.96 | 14.74 | 4.33
| MULTIBOILER/MULTI-TURBINE | All Sizes | 27 | 101.17 | 485.88 | 99.51 | 53.44 | 66.43 | 82.06 | 90.16 | 83.2 | 2.33 | 6.82 | 6.33 | 7.88 | 1.96 | 4 | 9.03 | 10.45 | 5.84 | 2.04 | 80.44 | 88.97 | 83.82 | 2.34 | 5.6 | 9.1 | 1.93
| DIESEL** | All Sizes | 199 | 659.75 | 21.73 | 99.31 | 11.4 | 64.41 | 10.48 | 94.59 | 93.4 | 17.24 | 19.27 | 8.97 | 3.23 | 2.18 | 4.03 | 4.38 | 29.85 | 1.38 | 1.84 | 17.7 | 95.62 | 94.16 | 8.58 | 10.69 | 2.72 | 1.66
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.