## Brochure 4 2011-2015
2015 Generating Unit Statistical Brochure -- Five Years, 2011 - 2015, All Units Reporting
NOTE: This brochure contains data on all units, whether they reported event records or not. For a review of statistics containing only those units that reported events, see the brochure "2011-2015 Generating Unit Statistical Brochure -- Units Reporting Events".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1573 | 6429.42 | 201.64 | 98.44 | 47.47 | 74.03 | 55.42 | 84.75 | 82.39 | 8.04 | 10.41 | 8.36 | 10.4 | 4.84 | 7.72 | 9.43 | 14.86 | 7.53 | 2.87 | 64.13 | 83.78 | 81.4 | 6.89 | 9.11 | 11.48 | 4.74
| All Fuel Types | 1-99 | 419 | 1539.58 | 143.36 | 98.87 | 27.59 | 64.25 | 40.63 | 86.28 | 84.13 | 12.07 | 14.61 | 9.92 | 8.11 | 5.58 | 8.31 | 9.67 | 19.6 | 5.37 | 2.73 | 42.94 | 86.56 | 84.48 | 10.61 | 13.1 | 8.33 | 5.1
|  | 100-199 | 386 | 1586.33 | 115.44 | 99.07 | 32.46 | 63.93 | 49.46 | 86.39 | 83.98 | 7.15 | 9.54 | 6.93 | 9.8 | 3.81 | 6.51 | 8.07 | 14.31 | 7.1 | 2.7 | 50.77 | 86.15 | 83.7 | 6.9 | 9.33 | 10.09 | 3.76
|  | 200-299 | 191 | 766.5 | 229.64 | 98.16 | 39.04 | 65.36 | 59.35 | 82.41 | 79.66 | 9.11 | 11.79 | 9.82 | 11.65 | 5.95 | 9.29 | 11.43 | 16.57 | 8.3 | 3.34 | 59.73 | 82.63 | 79.88 | 8.78 | 11.45 | 11.62 | 5.75
|  | 300-399 | 125 | 552.92 | 236.68 | 97.49 | 36.74 | 65.86 | 56.29 | 83.73 | 81.79 | 6.88 | 8.99 | 7.47 | 12.11 | 4.16 | 6.89 | 8.41 | 13.26 | 9.39 | 2.73 | 55.78 | 83.66 | 81.77 | 6.89 | 8.97 | 12.21 | 4.13
|  | 400-599 | 231 | 998.5 | 340.24 | 97.5 | 49.84 | 74.15 | 66.94 | 83.76 | 81.14 | 7.01 | 9.57 | 8.5 | 11.19 | 5.05 | 7.99 | 10.07 | 13.4 | 8.25 | 2.94 | 67.22 | 83.65 | 81 | 7.11 | 9.68 | 11.21 | 5.14
|  | 600-799 | 143 | 633.42 | 561.28 | 96.63 | 56.91 | 78.95 | 72.05 | 83.93 | 81.49 | 6.31 | 8.36 | 7.77 | 11.22 | 4.85 | 7.84 | 9.82 | 12.27 | 8.23 | 2.99 | 72.09 | 83.95 | 81.51 | 6.24 | 8.3 | 11.26 | 4.8
|  | 800-999 | 62 | 282.17 | 341.73 | 97.47 | 54.84 | 80.03 | 68.21 | 83.39 | 81.57 | 5.45 | 7.26 | 6.52 | 12.68 | 3.94 | 6.49 | 8.15 | 10.89 | 10.12 | 2.56 | 68.53 | 83.54 | 81.75 | 5.4 | 7.17 | 12.55 | 3.91
|  | 1000 Plus | 16 | 65 | 776.53 | 92.26 | 61.49 | 83.29 | 72.91 | 78.45 | 75.77 | 7.6 | 9.04 | 8.66 | 15.55 | 6 | 10.42 | 12.17 | 14.6 | 11.13 | 4.42 | 73.82 | 78.58 | 75.97 | 7.39 | 8.83 | 15.52 | 5.89
| Coal | All Sizes | 989 | 4092.08 | 343.41 | 97.82 | 58.49 | 78.4 | 66.53 | 85.29 | 82.77 | 6.48 | 8.58 | 7.55 | 10.1 | 4.61 | 7.72 | 9.54 | 12.81 | 6.99 | 3.11 | 74.61 | 84.41 | 81.92 | 5.88 | 7.8 | 10.93 | 4.66
| Primary | 1-99 | 198 | 693.67 | 182.73 | 98.59 | 34.91 | 71.84 | 45.54 | 87.28 | 85.47 | 9.4 | 11.66 | 8.64 | 8 | 4.73 | 8.13 | 9.44 | 17.47 | 4.6 | 3.4 | 48.59 | 87.84 | 86.01 | 7.98 | 10.27 | 7.94 | 4.21
|  | 100-199 | 260 | 1048.58 | 188.26 | 98.74 | 42.59 | 69.56 | 60.31 | 87.47 | 84.66 | 5.56 | 7.74 | 6.3 | 8.98 | 3.55 | 6.58 | 8.27 | 12.31 | 5.95 | 3.02 | 61.22 | 87.31 | 84.49 | 5.47 | 7.68 | 9.15 | 3.54
|  | 200-299 | 133 | 563.75 | 472.91 | 96.93 | 46.57 | 71.13 | 65.07 | 82.13 | 78.92 | 8.99 | 11.76 | 10.49 | 11.45 | 6.42 | 10.07 | 12.52 | 16.59 | 7.79 | 3.65 | 65.48 | 82.45 | 79.24 | 8.61 | 11.37 | 11.39 | 6.17
|  | 300-399 | 71 | 321.83 | 512.04 | 95.86 | 53.8 | 74.4 | 72.08 | 84.39 | 81.91 | 5.63 | 7.8 | 7.19 | 11.31 | 4.3 | 7.38 | 9.35 | 11.76 | 8.23 | 3.08 | 72.32 | 84.48 | 82.02 | 5.63 | 7.76 | 11.21 | 4.31
|  | 400-599 | 152 | 683.5 | 604.26 | 96.87 | 63.7 | 79.79 | 79.84 | 84.87 | 82.32 | 5.35 | 7.36 | 7.08 | 10.62 | 4.51 | 7.21 | 9.13 | 10.48 | 7.92 | 2.7 | 79.83 | 84.8 | 82.2 | 5.37 | 7.42 | 10.67 | 4.53
|  | 600-799 | 115 | 514.42 | 704.72 | 96.48 | 63.92 | 80.28 | 79.46 | 84.65 | 82.25 | 5.59 | 7.31 | 7.03 | 10.65 | 4.71 | 7.59 | 9.48 | 10.88 | 7.77 | 2.88 | 79.61 | 84.72 | 82.33 | 5.57 | 7.28 | 10.58 | 4.7
|  | 800-999 | 45 | 201.33 | 762.59 | 95.59 | 64.27 | 82.16 | 78.18 | 83.57 | 81.76 | 5.68 | 7.1 | 6.83 | 11.73 | 4.71 | 7.45 | 9.09 | 10.62 | 8.98 | 2.74 | 78.22 | 83.76 | 81.98 | 5.6 | 6.99 | 11.6 | 4.64
|  | 1000 Plus | 15 | 60 | 822.85 | 91.78 | 64.66 | 84.32 | 76.51 | 79.03 | 76.27 | 6.5 | 7.92 | 7.75 | 15.64 | 5.32 | 9.48 | 11.24 | 13.07 | 11.49 | 4.16 | 76.68 | 79.05 | 76.38 | 6.53 | 7.95 | 15.59 | 5.36
| Oil | All Sizes | 124 | 390.17 | 86.72 | 98.72 | 8.76 | 42.88 | 27.08 | 85.01 | 83.89 | 11.87 | 14.54 | 9.14 | 11.21 | 3.65 | 6.69 | 7.67 | 22.43 | 8.18 | 3.04 | 20.44 | 80.24 | 79.13 | 17.52 | 20.56 | 15.42 | 4.34
| Primary | 1-99 | 35 | 134.5 | 76.58 | 99.2 | 24.71 | 48.95 | 43.11 | 90.54 | 89.42 | 3.88 | 5.74 | 3.67 | 7.35 | 1.74 | 4.67 | 5.59 | 11.67 | 4.42 | 2.93 | 50.48 | 90.39 | 89.12 | 3.36 | 5.41 | 7.76 | 1.76
|  | 100-199 | 25 | 83.5 | 108.1 | 98.76 | 9.65 | 49.17 | 17.85 | 85.83 | 84.42 | 26.2 | 30.37 | 15.6 | 7.83 | 6.34 | 8.55 | 9.89 | 36.36 | 5.61 | 2.21 | 19.62 | 85.52 | 83.94 | 22.82 | 27.29 | 8.68 | 5.8
|  | 200-299 | 8 | 11 | 63.49 | 86.84 | 3.09 | 47.85 | 6.31 | 93.18 | 91.85 | 22.04 | 33.26 | 16.93 | 5.04 | 1.78 | 3.77 | 5.1 | 45.38 | 3.05 | 1.98 | 6.47 | 92.87 | 91.37 | 23.36 | 35.4 | 5.16 | 1.97
|  | 300-399 | 15 | 65.33 | 169.11 | 97.32 | 12.44 | 42.33 | 28.92 | 79.83 | 79.15 | 6.93 | 8.53 | 6.16 | 18.02 | 2.15 | 4.61 | 5.2 | 15.41 | 15.56 | 2.45 | 29.39 | 79.71 | 79.02 | 6.95 | 8.53 | 18.1 | 2.2
|  | 400-599 | 20 | 46.08 | 96.13 | 98.71 | 6.38 | 33.25 | 18.47 | 84.04 | 82.81 | 23.21 | 25.67 | 15.06 | 10.37 | 5.58 | 10.05 | 11 | 37.94 | 5.91 | 4.47 | 19.18 | 83.44 | 82.19 | 24.79 | 27.14 | 10.24 | 6.32
|  | 600-799 | 13 | 30.08 | 32.69 | 98.32 | 5.32 | 48.87 | 10.93 | 78.21 | 76.91 | 32.33 | 37.75 | 26.17 | 16.57 | 5.22 | 10.02 | 11.24 | 51.46 | 11.77 | 4.8 | 10.89 | 77.39 | 76.03 | 30.74 | 36.61 | 17.78 | 4.84
|  | 800-999 | 7 | 14.67 | 44.42 | 91.96 | 0.5 | 25.25 | 1.97 | 69.49 | 69.08 | 31.44 | 40.52 | 16.61 | 29.6 | 0.91 | 2.85 | 3.26 | 62.88 | 27.65 | 1.95 | 1.96 | 69.97 | 69.56 | 31.37 | 40.41 | 29.13 | 0.9
| Gas | All Sizes | 471 | 1576.75 | 67.07 | 98.8 | 11.99 | 36.45 | 28.33 | 83.12 | 81.45 | 16.37 | 19.53 | 10.58 | 11.34 | 5.55 | 7.96 | 9.27 | 25.15 | 8.93 | 2.41 | 32.9 | 81.66 | 79.6 | 13.72 | 17.58 | 13.11 | 5.23
| Primary | 1-99 | 155 | 498.58 | 71.29 | 98.64 | 8.79 | 42.4 | 17 | 84.7 | 83.47 | 29.69 | 31.93 | 13.5 | 8.12 | 7.18 | 9.12 | 9.88 | 37.01 | 6.17 | 1.95 | 20.74 | 84.16 | 82.71 | 25.38 | 27.7 | 8.78 | 7.06
|  | 100-199 | 119 | 435.33 | 54.27 | 99.2 | 11.7 | 38.36 | 29.59 | 84 | 82.41 | 11.99 | 14.93 | 8.01 | 11.96 | 4.03 | 6.07 | 7.32 | 20.24 | 9.93 | 2.04 | 30.49 | 83.6 | 81.86 | 11.65 | 14.7 | 12.38 | 4.02
|  | 200-299 | 58 | 168.25 | 74.49 | 99.2 | 14.98 | 34.91 | 42.71 | 81.76 | 80.38 | 10.93 | 13.17 | 8.65 | 12.99 | 5.24 | 7.95 | 9.22 | 18.05 | 10.28 | 2.71 | 42.92 | 81.68 | 80.31 | 10.83 | 13.01 | 13.11 | 5.21
|  | 300-399 | 44 | 157.75 | 65.08 | 98.52 | 10.35 | 33.26 | 31.15 | 83.4 | 82.07 | 13.57 | 15.8 | 9.53 | 11.71 | 4.89 | 7.03 | 8.01 | 20.68 | 9.57 | 2.14 | 31.13 | 83.31 | 81.99 | 13.38 | 15.59 | 11.88 | 4.81
|  | 400-599 | 69 | 239.58 | 87.06 | 98.09 | 12.79 | 36.01 | 35.44 | 80 | 77.13 | 15.74 | 20.86 | 13.23 | 13.38 | 6.62 | 10.11 | 12.65 | 27.28 | 9.89 | 3.49 | 35.52 | 79.75 | 76.85 | 16.21 | 21.34 | 13.38 | 6.87
|  | 600-799 | 17 | 46.92 | 213.99 | 94.62 | 12.9 | 40.42 | 30.96 | 79 | 76 | 13.35 | 20.33 | 13.89 | 16.23 | 4.77 | 8.94 | 11.91 | 29 | 12.06 | 4.17 | 31.9 | 79.34 | 76.3 | 12.81 | 19.75 | 15.98 | 4.69
|  | 800-999 | 9 | 30.33 | 32.61 | 99.06 | 9.85 | 34.89 | 28.12 | 83.26 | 82.35 | 2.02 | 4.35 | 2.28 | 16.16 | 0.58 | 3.81 | 4.54 | 13.92 | 12.93 | 3.23 | 28.22 | 83.13 | 82.21 | 1.98 | 4.28 | 16.3 | 0.57
| Lignite Primary | All Sizes | 33 | 121.17 | 106.22 | 99.35 | 69.97 | 84.28 | 83.1 | 87.47 | 83.84 | 4.2 | 7.59 | 7.25 | 8.89 | 3.64 | 5.25 | 8.34 | 9.44 | 7.28 | 1.61 | 83.02 | 87.63 | 83.92 | 4.54 | 8.24 | 8.42 | 3.95
| Oil/Gas | All Sizes | 563 | 1966.92 | 70.24 | 98.81 | 11.22 | 37.5 | 28.07 | 83.51 | 81.96 | 15.51 | 18.58 | 10.33 | 11.31 | 5.15 | 7.69 | 8.94 | 24.62 | 8.77 | 2.54 | 29.92 | 81.32 | 79.49 | 14.36 | 18.09 | 13.66 | 5.02
| Primary | 1-99 | 186 | 633.08 | 73.45 | 98.9 | 12.75 | 45.32 | 23 | 86.05 | 84.83 | 20.49 | 22.69 | 10.56 | 7.94 | 5.93 | 8.1 | 8.89 | 28.17 | 5.77 | 2.17 | 28.14 | 85.71 | 84.3 | 16.94 | 19.24 | 8.53 | 5.74
|  | 100-199 | 141 | 518.83 | 57.23 | 99.17 | 11.36 | 39.57 | 27.7 | 84.3 | 82.73 | 13.72 | 16.83 | 8.79 | 11.3 | 4.4 | 6.47 | 7.73 | 22.27 | 9.23 | 2.07 | 28.72 | 83.91 | 82.2 | 13.06 | 16.31 | 11.77 | 4.31
|  | 200-299 | 64 | 179.25 | 74.37 | 99.03 | 14.2 | 35.05 | 40.41 | 82.48 | 81.1 | 11.06 | 13.42 | 8.6 | 12.49 | 5.03 | 7.69 | 8.96 | 18.45 | 9.83 | 2.66 | 40.53 | 82.41 | 81.04 | 10.98 | 13.32 | 12.59 | 5
|  | 300-399 | 55 | 223.08 | 78.81 | 98.37 | 11.01 | 36.02 | 30.48 | 82.33 | 81.2 | 11.79 | 13.86 | 8.66 | 13.59 | 4.07 | 6.31 | 7.17 | 19.26 | 11.36 | 2.23 | 30.58 | 82.17 | 81.05 | 11.52 | 13.55 | 13.85 | 3.98
|  | 400-599 | 78 | 285.67 | 87.88 | 98.16 | 11.68 | 35.73 | 32.52 | 80.69 | 78.11 | 16.53 | 21.37 | 13.19 | 12.87 | 6.44 | 10.1 | 12.36 | 28.51 | 9.2 | 3.66 | 32.69 | 80.38 | 77.78 | 17.17 | 21.99 | 12.84 | 6.78
|  | 600-799 | 27 | 77 | 104.55 | 96.83 | 10.08 | 41.84 | 23 | 78.68 | 76.36 | 17.7 | 24.42 | 17.05 | 16.37 | 4.95 | 9.37 | 11.64 | 34.83 | 11.95 | 4.42 | 24.09 | 78.61 | 76.2 | 16.44 | 23.26 | 16.65 | 4.74
|  | 800-999 | 11 | 45 | 32.9 | 98.86 | 6.72 | 34.57 | 19.61 | 78.78 | 78.03 | 3.38 | 6.18 | 2.9 | 20.54 | 0.69 | 3.5 | 4.12 | 17.41 | 17.72 | 2.81 | 19.45 | 78.74 | 77.99 | 3.37 | 6.16 | 20.58 | 0.68
| NUCLEAR | All Sizes | 105 | 500.75 | 3783.93 | 98.56 | 88.45 | 98.45 | 89.41 | 89.42 | 87.6 | 3.16 | 3.78 | 3.78 | 7.66 | 2.92 | 3.35 | 4.18 | 4.51 | 7.23 | 0.43 | 89.84 | 89.85 | 88.03 | 2.95 | 3.57 | 7.42 | 2.73
| All Types | 400-799 | 15 | 70 | 2927.28 | 99.6 | 82.31 | 96.97 | 84.28 | 84.35 | 81.92 | 5.27 | 6.27 | 6.27 | 10.96 | 4.69 | 5.26 | 6.47 | 7.23 | 10.39 | 0.57 | 84.88 | 84.94 | 82.5 | 4.65 | 5.69 | 10.92 | 4.14
|  | 800-999 | 36 | 171.75 | 4416.4 | 96.74 | 89.86 | 99.59 | 90.14 | 90.14 | 88.89 | 3 | 3.41 | 3.41 | 7.07 | 2.79 | 3.15 | 3.75 | 4.02 | 6.71 | 0.36 | 90.23 | 90.23 | 89 | 3 | 3.41 | 6.98 | 2.79
|  | 1000 Plus | 54 | 259 | 3716.87 | 98.6 | 88.6 | 98.07 | 90.3 | 90.3 | 88.28 | 2.72 | 3.38 | 3.38 | 7.17 | 2.52 | 2.96 | 3.86 | 4.13 | 6.73 | 0.44 | 90.34 | 90.35 | 88.32 | 2.7 | 3.36 | 7.15 | 2.5
| PWR | All Sizes | 65 | 311.75 | 3880.06 | 98.02 | 87.58 | 98.6 | 88.22 | 88.22 | 86.8 | 4.12 | 4.59 | 4.59 | 7.98 | 3.79 | 4.09 | 4.66 | 5.05 | 7.69 | 0.3 | 88.82 | 88.83 | 87.38 | 3.75 | 4.24 | 7.72 | 3.46
|  | 400-799 | 5 | 25 | 2529.22 | 100 | 79.26 | 98.87 | 78.49 | 78.49 | 76.89 | 10.79 | 10.99 | 10.99 | 12.02 | 9.49 | 10.57 | 11.05 | 12.41 | 10.94 | 1.07 | 80.17 | 80.17 | 78.62 | 9.2 | 9.39 | 11.71 | 8.12
|  | 800-999 | 23 | 111.75 | 4429.09 | 96.67 | 88.54 | 99.8 | 88.61 | 88.61 | 87.57 | 3.95 | 4.31 | 4.31 | 7.74 | 3.65 | 3.86 | 4.31 | 4.66 | 7.53 | 0.21 | 88.72 | 88.72 | 87.71 | 3.96 | 4.31 | 7.62 | 3.66
|  | 1000 Plus | 37 | 175 | 3852.41 | 98.06 | 87.71 | 98.01 | 89.37 | 89.37 | 87.73 | 3.32 | 3.89 | 3.89 | 7.56 | 3.07 | 3.31 | 3.96 | 4.27 | 7.32 | 0.24 | 89.49 | 89.5 | 87.85 | 3.27 | 3.85 | 7.48 | 3.03
| BWR | All Sizes | 33 | 162 | 3652.78 | 98.67 | 90.99 | 98.42 | 92.52 | 92.52 | 90.07 | 1.46 | 2.28 | 2.28 | 6.11 | 1.37 | 2.02 | 3.31 | 3.5 | 5.46 | 0.64 | 92.44 | 92.44 | 89.97 | 1.46 | 2.26 | 6.18 | 1.37
|  | 400-799 | 5 | 24 | 2655.21 | 98.68 | 88 | 96.79 | 90.88 | 90.88 | 87.97 | 2.61 | 3.9 | 3.9 | 6.68 | 2.44 | 2.75 | 4.5 | 4.81 | 6.37 | 0.31 | 90.92 | 90.92 | 88.06 | 2.64 | 3.91 | 6.61 | 2.47
|  | 800-999 | 11 | 54 | 4859.49 | 96.02 | 93.09 | 99.37 | 93.7 | 93.7 | 91.98 | 0.92 | 1.47 | 1.47 | 5.43 | 0.87 | 1.35 | 2.26 | 2.37 | 4.95 | 0.49 | 93.67 | 93.67 | 92.01 | 0.94 | 1.49 | 5.43 | 0.89
|  | 1000 Plus | 17 | 84 | 3469.42 | 100 | 90.42 | 98.2 | 92.23 | 92.23 | 89.44 | 1.49 | 2.34 | 2.34 | 6.37 | 1.4 | 2.24 | 3.64 | 3.85 | 5.53 | 0.84 | 92.08 | 92.08 | 89.27 | 1.54 | 2.39 | 6.48 | 1.44
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 331 | 1518.08 | 4.5 | 98.53 | 3.82 | 80.25 | 3.44 | 90.04 | 88.61 | 46.37 | 48.46 | 11.73 | 5.72 | 4.24 | 7.45 | 7.96 | 60.95 | 2.51 | 3.21 | 4.76 | 89.49 | 87.63 | 41.65 | 44.78 | 5.93 | 4.59
| ENGINE** | 1-19 | 39 | 184.08 | 7.01 | 95.66 | 0.23 | 26.5 | 0.87 | 92.41 | 91.2 | 77.24 | 78.69 | 22.14 | 4.63 | 2.97 | 6.27 | 6.53 | 88.25 | 1.32 | 3.31 | 0.87 | 92.08 | 90.8 | 79.09 | 80.24 | 4.62 | 3.3
|  | 20 Plus | 292 | 1334 | 4.45 | 98.59 | 4.01 | 80.74 | 3.78 | 89.73 | 88.27 | 44.76 | 46.83 | 11.62 | 5.86 | 4.41 | 7.6 | 8.15 | 58.99 | 2.67 | 3.19 | 4.97 | 89.35 | 87.46 | 40.93 | 44.1 | 5.99 | 4.65
| GAS | All Sizes | 876 | 3821.5 | 7.85 | 97.76 | 4.09 | 72.4 | 3.4 | 89.65 | 87.12 | 56.3 | 57.01 | 11.86 | 5.94 | 4.41 | 6.58 | 6.7 | 66.19 | 3.77 | 2.17 | 5.64 | 90.53 | 88.47 | 36.5 | 37.34 | 6.21 | 3.26
| TURBINE** | 1-19 | 169 | 694 | 3.65 | 95.49 | 0.65 | 63.69 | 0.98 | 85.33 | 83.52 | 89.06 | 89.25 | 20.21 | 6.69 | 7.98 | 10.9 | 11.02 | 91.87 | 3.77 | 2.92 | 1.02 | 85.56 | 83.53 | 88.68 | 88.86 | 6.47 | 7.97
|  | 20-49 | 217 | 838 | 4.91 | 97.33 | 1.69 | 72.83 | 1.59 | 90.69 | 85.14 | 77.27 | 77.65 | 14.77 | 3.89 | 5.42 | 6.8 | 6.91 | 81.24 | 2.51 | 1.38 | 2.33 | 90.86 | 84.89 | 67.37 | 67.96 | 4.34 | 4.8
|  | 50 Plus | 489 | 2285.5 | 9.14 | 98.2 | 4.52 | 72.45 | 4.74 | 90.52 | 88.87 | 38.69 | 39.68 | 9.12 | 6.45 | 3.02 | 5.25 | 5.38 | 52.9 | 4.22 | 2.23 | 6.23 | 90.74 | 89.1 | 31.33 | 32.19 | 6.4 | 2.86
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 309 | 1235.42 | 74.33 | 98.76 | 51.57 | 78.64 | 54.36 | 87.66 | 84.63 | 4.71 | 5.79 | 4.44 | 9.65 | 2.69 | 4.36 | 5.2 | 8.79 | 7.98 | 1.67 | 65.58 | 88.63 | 85.59 | 2.82 | 3.81 | 9.47 | 1.9
| HYDRO | All Sizes | 1145 | 5034.5 | 36.39 | 99.92 | 40.62 | 67.38 | 57.92 | 82.39 | 82.03 | 7.38 | 7.56 | 6.71 | 12.42 | 5.19 | 6.91 | 7.04 | 9.78 | 10.7 | 1.72 | 60.29 | 82.84 | 82.53 | 3.76 | 3.87 | 14.64 | 2.53
|  | 1-29 | 465 | 2101.83 | 118.08 | 99.8 | 35.65 | 64.55 | 54.93 | 79.64 | 79.28 | 11.87 | 12.18 | 11.62 | 11.68 | 8.68 | 10.34 | 10.58 | 14.15 | 10.02 | 1.67 | 55.23 | 84.29 | 83.83 | 5.82 | 6.31 | 11.54 | 4.17
|  | 30 Plus | 680 | 2932.67 | 25.08 | 99.94 | 41 | 67.57 | 60.05 | 84.35 | 83.99 | 3.96 | 4.05 | 3.46 | 12.94 | 2.71 | 4.46 | 4.53 | 6.45 | 11.19 | 1.75 | 60.67 | 82.73 | 82.43 | 3.59 | 3.67 | 14.87 | 2.4
| PUMPED STORAGE | All Sizes | 114 | 516.92 | 8.17 | 99.75 | 8.59 | 44.17 | 27.6 | 82.71 | 82.48 | 9.22 | 9.29 | 6.63 | 12.88 | 4.41 | 6.1 | 6.14 | 12.38 | 11.19 | 1.69 | 19.44 | 80.93 | 80.3 | 10.76 | 11.02 | 14.7 | 4.36
| MULTIBOILER/MULTI-TURBINE | All Sizes | 27 | 101.17 | 485.88 | 99.51 | 53.44 | 66.43 | 82.06 | 90.16 | 83.2 | 2.33 | 6.82 | 6.33 | 7.88 | 1.96 | 4 | 9.03 | 10.45 | 5.84 | 2.04 | 80.44 | 88.97 | 83.82 | 2.34 | 5.6 | 9.1 | 1.93
| DIESEL** | All Sizes | 199 | 659.75 | 21.73 | 99.31 | 11.4 | 64.41 | 10.48 | 94.59 | 93.4 | 17.24 | 19.27 | 8.97 | 3.23 | 2.18 | 4.03 | 4.38 | 29.85 | 1.38 | 1.84 | 17.7 | 95.62 | 94.16 | 8.58 | 10.69 | 2.72 | 1.66
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.