## Sheet1
2016 Generating Unit Statistical Brochure -- Five Years, 2012 - 2016, All Units Reporting
NOTE: This brochure contains data on all units, whether they reported event records or not. For a review of statistics containing only those units that reported events, see the brochure "2012-2016 Generating Unit Statistical Brochure -- Units Reporting Events".
(The differences between statistics with or with events will appear in equations needing derating information such as EAF, EFOR, and other equations. The equations are more accurate if events are reported.)
|  | MW Trb/Gen | # of | Unit-
| Unit Type | Nameplate | Units | Years | ART | SR | NCF | NOF | SF | AF | EAF | FOR | EFOR | EFORd | SOF | FOF | UOF | EUOF | EUOR | POF | MOF | WSF | WAF | WEAF | WFOR | WEFOR | WSOF | WFOF
| FOSSIL | All Sizes | 1512 | 6324 | 178.57 | 98.62 | 45.82 | 73.04 | 54.29 | 84.29 | 81.97 | 8.17 | 10.55 | 8.34 | 10.88 | 4.83 | 7.8 | 9.45 | 15.16 | 7.91 | 2.97 | 62.73 | 83.24 | 80.88 | 7.07 | 9.35 | 11.99 | 4.77
| All Fuel Types | 1-99 | 382 | 1505.5 | 139.32 | 98.99 | 27.59 | 63.79 | 40.74 | 86.19 | 84.09 | 11.52 | 13.93 | 9.48 | 8.51 | 5.3 | 7.96 | 9.26 | 18.88 | 5.85 | 2.66 | 43.25 | 86.19 | 84.13 | 10.2 | 12.59 | 8.9 | 4.91
|  | 100-199 | 374 | 1529.08 | 87.92 | 99.34 | 30.99 | 63.18 | 47.62 | 85.89 | 83.55 | 7.41 | 9.81 | 6.83 | 10.3 | 3.81 | 6.59 | 8.03 | 14.71 | 7.52 | 2.78 | 49.05 | 85.61 | 83.24 | 7.18 | 9.6 | 10.6 | 3.79
|  | 200-299 | 181 | 747 | 213.82 | 98.28 | 37.16 | 64.32 | 57.57 | 81.94 | 79.35 | 9.44 | 12.04 | 9.91 | 12.06 | 6 | 9.58 | 11.53 | 17.08 | 8.49 | 3.57 | 57.78 | 82.13 | 79.56 | 9.15 | 11.72 | 12.05 | 5.82
|  | 300-399 | 123 | 549.92 | 224.8 | 97.73 | 35.31 | 65.12 | 54.77 | 83 | 81.05 | 7.52 | 9.71 | 7.97 | 12.55 | 4.45 | 7.31 | 8.82 | 14.15 | 9.69 | 2.85 | 54.22 | 82.97 | 81.07 | 7.52 | 9.67 | 12.62 | 4.41
|  | 400-599 | 226 | 993.08 | 326.72 | 97.54 | 48.25 | 73.46 | 65.44 | 82.98 | 80.32 | 7.45 | 10.13 | 8.93 | 11.75 | 5.26 | 8.37 | 10.5 | 14.19 | 8.65 | 3.11 | 65.68 | 82.91 | 80.22 | 7.54 | 10.24 | 11.73 | 5.35
|  | 600-799 | 148 | 641 | 541.29 | 96.65 | 54.58 | 77.91 | 69.99 | 83.67 | 81.25 | 6.22 | 8.34 | 7.66 | 11.68 | 4.65 | 7.7 | 9.66 | 12.4 | 8.63 | 3.06 | 70.05 | 83.65 | 81.23 | 6.2 | 8.32 | 11.72 | 4.63
|  | 800-999 | 62 | 288.42 | 302.56 | 97.71 | 52.23 | 77.71 | 66.84 | 82.89 | 81.09 | 5.75 | 7.66 | 6.8 | 13.03 | 4.08 | 6.93 | 8.61 | 11.66 | 10.18 | 2.85 | 67.22 | 83.06 | 81.27 | 5.68 | 7.56 | 12.89 | 4.05
|  | 1000 Plus | 16 | 65 | 811.67 | 92.55 | 59.24 | 80.81 | 72.47 | 77.97 | 75.23 | 6.77 | 8.13 | 7.78 | 16.76 | 5.27 | 10.85 | 12.48 | 14.97 | 11.17 | 5.59 | 73.3 | 78.19 | 75.54 | 6.53 | 7.87 | 16.69 | 5.12
| Coal | All Sizes | 970 | 3948.17 | 344.37 | 97.92 | 56.46 | 77.07 | 65.36 | 84.76 | 82.28 | 6.67 | 8.8 | 7.71 | 10.57 | 4.67 | 7.9 | 9.67 | 13.16 | 7.34 | 3.23 | 73.26 | 83.85 | 81.36 | 6.05 | 8.04 | 11.43 | 4.72
| Primary | 1-99 | 181 | 641.83 | 198.48 | 98.72 | 34.08 | 72 | 43.58 | 87.34 | 85.64 | 9.08 | 11.18 | 8.32 | 8.31 | 4.35 | 7.63 | 8.81 | 17.09 | 5.03 | 3.28 | 47.34 | 87.81 | 86.1 | 7.59 | 9.71 | 8.31 | 3.89
|  | 100-199 | 255 | 973 | 174.45 | 98.91 | 41.2 | 68.69 | 59.13 | 87 | 84.26 | 5.82 | 8.05 | 6.47 | 9.35 | 3.66 | 6.84 | 8.48 | 12.79 | 6.16 | 3.18 | 59.97 | 86.87 | 84.12 | 5.74 | 8.02 | 9.49 | 3.65
|  | 200-299 | 131 | 538.17 | 457.36 | 97.1 | 44.44 | 70.2 | 63.1 | 81.57 | 78.59 | 9.65 | 12.26 | 10.86 | 11.69 | 6.74 | 10.61 | 12.78 | 17.27 | 7.82 | 3.87 | 63.3 | 81.9 | 78.93 | 9.31 | 11.91 | 11.6 | 6.5
|  | 300-399 | 71 | 320.25 | 500.6 | 96.2 | 51.34 | 73.18 | 69.92 | 83.32 | 80.81 | 6.27 | 8.56 | 7.83 | 12 | 4.67 | 7.82 | 9.81 | 12.59 | 8.86 | 3.14 | 70.15 | 83.44 | 80.96 | 6.22 | 8.48 | 11.9 | 4.66
|  | 400-599 | 152 | 685.33 | 585.57 | 96.89 | 61.19 | 78.2 | 78.24 | 84.18 | 81.51 | 5.67 | 7.85 | 7.51 | 11.12 | 4.7 | 7.52 | 9.54 | 11.12 | 8.31 | 2.81 | 78.24 | 84.13 | 81.42 | 5.69 | 7.92 | 11.14 | 4.72
|  | 600-799 | 120 | 519.17 | 682.34 | 96.7 | 61.52 | 79.11 | 77.6 | 84.31 | 81.86 | 5.56 | 7.4 | 7.05 | 11.12 | 4.57 | 7.56 | 9.48 | 11.12 | 8.13 | 2.99 | 77.76 | 84.35 | 81.9 | 5.56 | 7.4 | 11.08 | 4.57
|  | 800-999 | 45 | 205.42 | 730.39 | 95.5 | 61.23 | 79.63 | 76.84 | 82.98 | 81.19 | 5.98 | 7.47 | 7.15 | 12.13 | 4.89 | 7.92 | 9.56 | 11.28 | 9.1 | 3.03 | 76.89 | 83.19 | 81.43 | 5.89 | 7.35 | 12 | 4.82
|  | 1000 Plus | 15 | 60 | 827.08 | 92.18 | 62.1 | 81.9 | 75.64 | 78.99 | 76.25 | 5.71 | 7.03 | 6.83 | 16.43 | 4.58 | 10.08 | 11.68 | 13.63 | 10.93 | 5.5 | 75.83 | 79 | 76.35 | 5.69 | 7.01 | 16.43 | 4.57
| Oil | All Sizes | 114 | 351.5 | 87.73 | 98.69 | 8.33 | 42.93 | 27.12 | 84.35 | 83.25 | 12.42 | 15.04 | 9.03 | 11.81 | 3.84 | 7.32 | 8.28 | 23.89 | 8.33 | 3.48 | 19.41 | 79.64 | 78.72 | 17.76 | 20.28 | 16.17 | 4.19
| Primary | 1-99 | 32 | 119.83 | 80.58 | 99.22 | 24.8 | 46.75 | 45.95 | 89.5 | 87.87 | 4.15 | 6.85 | 4.43 | 8.51 | 1.99 | 6.1 | 7.57 | 14.52 | 4.4 | 4.11 | 53.05 | 88.6 | 86.67 | 3.58 | 6.5 | 9.42 | 1.97
|  | 100-199 | 24 | 78.75 | 109.79 | 98.66 | 9.64 | 50.01 | 17.3 | 85.21 | 84.29 | 28.45 | 31.39 | 16.63 | 7.91 | 6.88 | 9.13 | 10 | 37.44 | 5.66 | 2.25 | 19.29 | 84.82 | 83.84 | 25.13 | 28.06 | 8.71 | 6.47
|  | 200-299 | 5 | 6.5 | 67.92 | 82.74 | 3.91 | 55.58 | 6.65 | 94.21 | 93.92 | 17.88 | 21.44 | 14.97 | 4.34 | 1.45 | 2.19 | 2.48 | 28.04 | 3.6 | 0.74 | 7.04 | 93.88 | 93.57 | 17.76 | 21.34 | 4.6 | 1.52
|  | 300-399 | 15 | 59.33 | 167.06 | 97.44 | 12.39 | 42.89 | 28.35 | 80.38 | 79.78 | 7.68 | 8.98 | 6.62 | 17.26 | 2.36 | 5.06 | 5.51 | 16.41 | 14.57 | 2.7 | 28.88 | 80.36 | 79.76 | 7.4 | 8.68 | 17.33 | 2.31
|  | 400-599 | 18 | 41.42 | 66.66 | 98.73 | 4.24 | 30.92 | 12.98 | 82.37 | 81.24 | 34.87 | 37.75 | 19.56 | 10.68 | 6.95 | 11.45 | 12.35 | 49.54 | 6.18 | 4.5 | 13.73 | 81.7 | 80.58 | 35.95 | 38.59 | 10.59 | 7.71
|  | 600-799 | 13 | 27.08 | 32.67 | 97.74 | 4.71 | 47.44 | 10.17 | 80.27 | 79.55 | 18.72 | 22.97 | 14.63 | 17.39 | 2.34 | 7.33 | 7.97 | 44.55 | 12.4 | 4.99 | 9.93 | 78.96 | 78.2 | 18.1 | 22.81 | 18.85 | 2.19
|  | 800-999 | 6 | 13.58 | 39.88 | 92.17 | 0.32 | 19.8 | 1.61 | 69.72 | 69.72 | 12.56 | 12.85 | 8.4 | 30.05 | 0.23 | 2.06 | 2.06 | 56.32 | 28.22 | 1.83 | 1.6 | 70.21 | 70.2 | 12.73 | 13.03 | 29.56 | 0.23
| Gas | All Sizes | 460 | 1605.25 | 59.65 | 98.94 | 11.77 | 38 | 27.49 | 82.66 | 81.05 | 16.23 | 19.34 | 10.26 | 12.02 | 5.32 | 7.89 | 9.13 | 25.4 | 9.45 | 2.57 | 30.98 | 80.92 | 78.97 | 14.4 | 18.24 | 13.87 | 5.21
| Primary | 1-99 | 146 | 504.25 | 66.72 | 98.84 | 9.82 | 43.37 | 18.37 | 84.56 | 83.46 | 26.98 | 28.8 | 12.44 | 8.65 | 6.79 | 8.74 | 9.38 | 33.95 | 6.7 | 1.95 | 22.64 | 83.7 | 82.45 | 23.1 | 24.84 | 9.5 | 6.8
|  | 100-199 | 121 | 448.5 | 45.62 | 99.32 | 11.85 | 40.3 | 28.45 | 83.67 | 82 | 11.68 | 14.67 | 7.64 | 12.57 | 3.76 | 5.88 | 7.02 | 20.17 | 10.45 | 2.11 | 29.42 | 83.06 | 81.26 | 11.51 | 14.58 | 13.11 | 3.83
|  | 200-299 | 61 | 174.83 | 71.51 | 99.23 | 14.56 | 35.81 | 40.64 | 81.24 | 79.65 | 10.32 | 13.15 | 8.41 | 14.08 | 4.68 | 7.87 | 9.34 | 19.03 | 10.89 | 3.19 | 40.65 | 81.04 | 79.49 | 10.19 | 12.94 | 14.34 | 4.61
|  | 300-399 | 45 | 159.33 | 62.07 | 98.6 | 10.02 | 33.79 | 29.75 | 82.5 | 81.16 | 14.47 | 16.79 | 9.87 | 12.47 | 5.03 | 7.45 | 8.45 | 22.36 | 10.05 | 2.42 | 29.64 | 82.37 | 81.05 | 14.37 | 16.67 | 12.65 | 4.98
|  | 400-599 | 65 | 236.25 | 79.44 | 98.24 | 12.87 | 38.36 | 33.45 | 79.16 | 76.49 | 16.61 | 21.76 | 13.45 | 14.17 | 6.66 | 10.55 | 12.96 | 29.05 | 10.29 | 3.89 | 33.56 | 79.03 | 76.33 | 17.05 | 22.22 | 14.07 | 6.9
|  | 600-799 | 15 | 50.67 | 186.85 | 94.63 | 11.96 | 42.39 | 27.37 | 78.03 | 75.57 | 15.93 | 21.91 | 14.96 | 16.78 | 5.19 | 8.99 | 11.45 | 30.46 | 12.98 | 3.8 | 28.21 | 78.52 | 76.06 | 15.33 | 21.25 | 16.37 | 5.11
|  | 800-999 | 7 | 31.42 | 23.05 | 99.13 | 8.02 | 33.78 | 23.57 | 81.83 | 80.99 | 4.83 | 7.8 | 3.57 | 16.97 | 1.2 | 5 | 5.82 | 19.85 | 13.17 | 3.81 | 23.75 | 81.7 | 80.86 | 4.74 | 7.68 | 17.12 | 1.18
| Lignite Primary | All Sizes | 34 | 130.25 | 55.63 | 99.58 | 67.31 | 82.6 | 81.54 | 87.26 | 83.77 | 4.29 | 7.55 | 7.1 | 9.09 | 3.66 | 5.35 | 8.31 | 9.56 | 7.39 | 1.69 | 81.49 | 87.32 | 83.62 | 4.68 | 8.41 | 8.68 | 4
| Oil/Gas | All Sizes | 539 | 1956.75 | 63.32 | 98.9 | 11.03 | 38.73 | 27.42 | 82.97 | 81.45 | 15.56 | 18.59 | 10.03 | 11.98 | 5.05 | 7.79 | 8.97 | 25.13 | 9.24 | 2.73 | 28.49 | 80.64 | 78.92 | 14.91 | 18.55 | 14.36 | 4.99
| Primary | 1-99 | 174 | 624.08 | 71.48 | 98.98 | 13.19 | 44.74 | 23.93 | 85.55 | 84.35 | 19.57 | 21.73 | 10.34 | 8.62 | 5.82 | 8.21 | 9.02 | 27.68 | 6.24 | 2.39 | 29.48 | 84.8 | 83.4 | 16.24 | 18.44 | 9.48 | 5.71
|  | 100-199 | 140 | 527.25 | 48.25 | 99.3 | 11.54 | 41.25 | 26.84 | 83.89 | 82.33 | 13.57 | 16.55 | 8.42 | 11.89 | 4.21 | 6.35 | 7.45 | 22.15 | 9.76 | 2.13 | 27.97 | 83.32 | 81.63 | 13.07 | 16.12 | 12.48 | 4.21
|  | 200-299 | 63 | 181.33 | 71.49 | 99.09 | 14.16 | 35.95 | 39.39 | 81.72 | 80.17 | 10.37 | 13.2 | 8.35 | 13.72 | 4.56 | 7.66 | 9.09 | 19.1 | 10.62 | 3.1 | 39.39 | 81.52 | 80.02 | 10.25 | 13 | 13.98 | 4.5
|  | 300-399 | 54 | 218.67 | 74.09 | 98.48 | 10.69 | 36.32 | 29.38 | 81.93 | 80.79 | 12.81 | 14.9 | 9.1 | 13.75 | 4.32 | 6.81 | 7.66 | 20.9 | 11.26 | 2.49 | 29.43 | 81.8 | 80.68 | 12.54 | 14.59 | 13.98 | 4.22
|  | 400-599 | 73 | 277.67 | 78.39 | 98.29 | 11.5 | 37.83 | 30.18 | 79.67 | 77.25 | 18.19 | 23.15 | 13.83 | 13.62 | 6.71 | 10.7 | 12.86 | 31.02 | 9.63 | 3.98 | 30.4 | 79.46 | 77 | 18.78 | 23.73 | 13.51 | 7.03
|  | 600-799 | 25 | 77.75 | 103.96 | 96.23 | 9.57 | 43.14 | 21.29 | 78.82 | 76.98 | 16.42 | 22.1 | 14.55 | 16.99 | 4.18 | 8.4 | 10.22 | 33.37 | 12.77 | 4.22 | 22.19 | 78.66 | 76.77 | 15.75 | 21.49 | 17.19 | 4.15
|  | 800-999 | 9 | 45 | 23.33 | 99 | 5.62 | 33.37 | 16.94 | 78.17 | 77.59 | 5.07 | 7.95 | 3.34 | 20.92 | 0.91 | 4.11 | 4.69 | 21.72 | 17.71 | 3.21 | 16.84 | 78.12 | 77.54 | 5 | 7.85 | 21 | 0.89
| NUCLEAR | All Sizes | 106 | 503 | 3996.59 | 98.01 | 89.13 | 98.48 | 90.27 | 90.28 | 88.47 | 2.94 | 3.51 | 3.51 | 6.98 | 2.73 | 3.16 | 3.95 | 4.23 | 6.56 | 0.43 | 90.51 | 90.52 | 88.73 | 2.8 | 3.35 | 6.87 | 2.61
| All Types | 400-799 | 15 | 70 | 3156.22 | 99.58 | 84.72 | 96.9 | 86.93 | 87 | 84.47 | 5.11 | 6.12 | 6.12 | 8.32 | 4.68 | 5.36 | 6.59 | 7.14 | 7.64 | 0.68 | 87.42 | 87.49 | 84.95 | 4.48 | 5.54 | 8.4 | 4.1
|  | 800-999 | 36 | 171 | 4522.72 | 97.24 | 90.91 | 99.56 | 91.23 | 91.23 | 89.89 | 2.17 | 2.62 | 2.62 | 6.75 | 2.02 | 2.37 | 3.03 | 3.23 | 6.4 | 0.35 | 91.31 | 91.31 | 90.01 | 2.17 | 2.62 | 6.66 | 2.03
|  | 1000 Plus | 55 | 262 | 3952.42 | 98.52 | 88.87 | 98.15 | 90.53 | 90.54 | 88.61 | 2.88 | 3.41 | 3.41 | 6.78 | 2.68 | 3.09 | 3.86 | 4.12 | 6.37 | 0.41 | 90.55 | 90.55 | 88.62 | 2.88 | 3.42 | 6.77 | 2.68
| PWR | All Sizes | 65 | 313 | 4085.25 | 97.44 | 88.37 | 98.68 | 89.1 | 89.11 | 87.73 | 3.82 | 4.22 | 4.22 | 7.36 | 3.53 | 3.85 | 4.36 | 4.69 | 7.05 | 0.31 | 89.55 | 89.56 | 88.16 | 3.5 | 3.92 | 7.2 | 3.25
|  | 400-799 | 5 | 25 | 2765.2 | 100 | 81.53 | 99.14 | 81 | 81 | 79.35 | 10.93 | 11.11 | 11.11 | 9.07 | 9.93 | 11.09 | 11.58 | 12.58 | 7.91 | 1.16 | 82.24 | 82.24 | 80.66 | 9.39 | 9.57 | 9.24 | 8.52
|  | 800-999 | 23 | 112 | 4377.39 | 96.76 | 90 | 99.84 | 90.04 | 90.04 | 89.01 | 2.68 | 3.02 | 3.02 | 7.48 | 2.48 | 2.72 | 3.15 | 3.39 | 7.24 | 0.23 | 90.14 | 90.14 | 89.13 | 2.7 | 3.03 | 7.36 | 2.5
|  | 1000 Plus | 37 | 176 | 4155.43 | 97.41 | 88.08 | 98.09 | 89.66 | 89.67 | 88.11 | 3.54 | 4.02 | 4.02 | 7.04 | 3.29 | 3.53 | 4.1 | 4.39 | 6.8 | 0.24 | 89.79 | 89.79 | 88.23 | 3.47 | 3.96 | 6.97 | 3.23
| BWR | All Sizes | 34 | 162 | 3844.66 | 99.07 | 91.21 | 98.38 | 92.94 | 92.94 | 90.44 | 1.43 | 2.21 | 2.21 | 5.71 | 1.35 | 1.96 | 3.22 | 3.4 | 5.1 | 0.61 | 92.71 | 92.71 | 90.24 | 1.52 | 2.25 | 5.86 | 1.43
|  | 400-799 | 5 | 23 | 2826.28 | 98.63 | 89.29 | 96.51 | 92.5 | 92.5 | 89.5 | 2.21 | 3.58 | 3.58 | 5.41 | 2.09 | 2.64 | 4.46 | 4.69 | 4.86 | 0.55 | 92.52 | 92.52 | 89.57 | 2.25 | 3.61 | 5.35 | 2.13
|  | 800-999 | 11 | 53 | 5227.27 | 96.34 | 93.42 | 99.2 | 94.18 | 94.18 | 92.17 | 0.92 | 1.66 | 1.66 | 4.95 | 0.87 | 1.29 | 2.45 | 2.56 | 4.53 | 0.42 | 94.18 | 94.18 | 92.24 | 0.93 | 1.65 | 4.94 | 0.89
|  | 1000 Plus | 18 | 86 | 3613.56 | 100 | 90.46 | 98.26 | 92.3 | 92.3 | 89.63 | 1.54 | 2.19 | 2.19 | 6.26 | 1.44 | 2.19 | 3.37 | 3.57 | 5.51 | 0.75 | 92.06 | 92.06 | 89.4 | 1.69 | 2.34 | 6.36 | 1.58
| CANDU | All Sizes | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | **** | ****
| JET | All Sizes | 326 | 1462.08 | 4.79 | 98.59 | 4.15 | 79.06 | 3.81 | 89.86 | 88.67 | 45.79 | 47.25 | 11.63 | 5.87 | 4.27 | 7.44 | 7.78 | 59.98 | 2.7 | 3.17 | 5.25 | 89.24 | 87.65 | 41.33 | 43.54 | 6.06 | 4.7
| ENGINE** | 1-19 | 38 | 172.08 | 2.51 | 95.72 | 0.23 | 77.25 | 0.33 | 91.57 | 90.77 | 89.97 | 90.74 | 21.16 | 5.49 | 2.93 | 6.39 | 6.65 | 95.38 | 2.04 | 3.46 | 0.3 | 90.99 | 90.14 | 91.81 | 92.36 | 5.62 | 3.39
|  | 20 Plus | 288 | 1290 | 4.84 | 98.63 | 4.35 | 79.07 | 4.26 | 89.63 | 88.39 | 43.92 | 45.3 | 11.54 | 5.92 | 4.45 | 7.58 | 7.93 | 57.63 | 2.79 | 3.13 | 5.5 | 89.15 | 87.52 | 40.53 | 42.74 | 6.08 | 4.77
| GAS | All Sizes | 826 | 3733.75 | 8.62 | 98.08 | 4.82 | 73.08 | 3.97 | 89.8 | 87.57 | 50.67 | 51.77 | 11.28 | 6.09 | 4.11 | 6.42 | 6.6 | 62.28 | 3.77 | 2.31 | 6.59 | 90.48 | 88.6 | 32.59 | 33.8 | 6.32 | 3.2
| TURBINE** | 1-19 | 155 | 637 | 3.25 | 96.24 | 0.67 | 65.83 | 0.97 | 86.83 | 85.55 | 87.58 | 87.79 | 18.6 | 6.33 | 6.84 | 10.22 | 10.32 | 91.44 | 2.95 | 3.38 | 1.01 | 86.67 | 85.29 | 87.2 | 87.41 | 6.44 | 6.89
|  | 20-49 | 194 | 788.25 | 5.12 | 98.02 | 2.3 | 78.12 | 2 | 90.89 | 85.96 | 70.97 | 71.52 | 12.97 | 4.22 | 4.89 | 6.53 | 6.66 | 76.89 | 2.58 | 1.64 | 2.95 | 91.09 | 85.88 | 58.52 | 59.35 | 4.76 | 4.16
|  | 50 Plus | 476 | 2305.5 | 10.27 | 98.35 | 5.26 | 72.91 | 5.42 | 90.21 | 88.63 | 36.53 | 38.07 | 9.29 | 6.64 | 3.15 | 5.4 | 5.62 | 50.72 | 4.39 | 2.26 | 7.22 | 90.59 | 89.03 | 28.79 | 30.06 | 6.48 | 2.93
| COMB. CYCLE (BLOCK REPORTED UNITS ONLY | All Sizes | 301 | 1354.25 | 77.12 | 98.66 | 53.04 | 79.27 | 55.62 | 87.68 | 84.83 | 4.5 | 5.53 | 4.29 | 9.7 | 2.62 | 4.24 | 5.03 | 8.36 | 8.08 | 1.62 | 66.91 | 88.51 | 85.57 | 2.71 | 3.69 | 9.63 | 1.86
| HYDRO | All Sizes | 1121 | 5107.5 | 29.88 | 99.94 | 39.71 | 65.9 | 57.88 | 81.58 | 81.19 | 8.11 | 8.28 | 7.15 | 12.79 | 5.63 | 7.35 | 7.47 | 10.51 | 11.07 | 1.72 | 60.25 | 82.59 | 82.24 | 3.96 | 4.07 | 14.77 | 2.64
|  | 1-29 | 454 | 2063.83 | 103.26 | 99.83 | 34.31 | 61.18 | 54.52 | 77.98 | 77.65 | 13.57 | 13.84 | 12.81 | 12.22 | 9.79 | 11.37 | 11.58 | 15.7 | 10.65 | 1.58 | 56.08 | 83.53 | 83.12 | 6.3 | 6.71 | 12.02 | 4.44
|  | 30 Plus | 667 | 3043.67 | 20.83 | 99.95 | 40.09 | 66.21 | 60.14 | 84.01 | 83.58 | 4.16 | 4.27 | 3.55 | 13.18 | 2.81 | 4.63 | 4.7 | 6.78 | 11.36 | 1.82 | 60.55 | 82.53 | 82.18 | 3.79 | 3.87 | 14.96 | 2.51
| PUMPED STORAGE | All Sizes | 114 | 525.92 | 7.98 | 99.92 | 8.05 | 43.47 | 26.93 | 82.36 | 82.15 | 8.5 | 8.54 | 6.02 | 13.67 | 3.97 | 5.74 | 5.77 | 11.9 | 11.89 | 1.78 | 18.52 | 80.66 | 80.06 | 10.27 | 10.46 | 15.29 | 4.05
| MULTIBOILER/MULTI-TURBINE | All Sizes | 24 | 106 | 420.99 | 99.26 | 48.68 | 66.21 | 78.83 | 89.07 | 82.34 | 2.23 | 7 | 6.35 | 9.13 | 1.79 | 3.89 | 8.9 | 10.72 | 7.03 | 2.1 | 73.53 | 87 | 82.2 | 2.52 | 5.93 | 11.1 | 1.9
| DIESEL** | All Sizes | 161 | 654.25 | 14.69 | 99.22 | 9.69 | 61.84 | 7.19 | 94.72 | 93.94 | 19.73 | 21.69 | 5.83 | 3.51 | 1.77 | 3.39 | 3.65 | 33.98 | 1.88 | 1.63 | 15.67 | 94.85 | 93.51 | 8.34 | 10.3 | 3.72 | 1.43
**Caution: EFOR and WEFOR values may be low since deratings during reserve shutdown periods may not have been reported for a large number of these units.
*** The two methods for calculating combined cycle units is not available at this time.
**** Less than three generating companies are reporting this type of unit. To retain confidentiality of the data, no data is reported here.