## Parameters
WESTERN INTERCONNECTION CALCULATIONS
Balancing | Freq | 2016 Interconnection | 2016 | Eastern Interconnection |  |  | Epsilon1 | Epsilon10
Authority | Bias | Bias | L10 |  | FTL_Low | FTL_High | (Hz) | (Hz)
BA-01 | -100 | -1636.44 | 48.7256 |  | 59.9316 | 60.0684 | 0.0228 | 0.0073
Enter Balancing Authority Acronym in cell "A4" and its Frequency Bias setting (negative number) in cell "B4"
ACE | Freq_Error | Frequency Bias | Actual_Freq | Sched_Freq | BAAL_Low at 60 Hz SF | BAAL_Low at 59.98 Hz SF | BAAL_Low at 60.02 Hz SF | BAAL_High at 60 Hz SF | BAAL_High at 59.98 Hz SF | BAAL_High at 60.02 Hz SF | CPS1 Bound at 60 Hz SF | CPS1 Bound at 59.98 Hz SF | CPS1 Bound at 60.02 Hz SF | Old L10 | Old L10 | CPS1 BAAL 60 | CPS1 BAAL 59.98 | CPS1 BAAL 60.02
-23.3928 | -0.2 | -100 | 59.8 | 60 | -23.3928 | -25.992 | -21.2662 |  |  |  | -2.5992 | -2.888 | -2.3629 | -48.7256 | 48.7256 | -700 | -700 | -700
-23.5104 | -0.199 | -100 | 59.801 | 60 | -23.5104 | -26.1372 | -21.3633 |  |  |  | -2.6123 | -2.9041 | -2.3737 | -48.7256 | 48.7256 | -700 | -700 | -700
-23.6291 | -0.198 | -100 | 59.802 | 60 | -23.6291 | -26.284 | -21.4613 |  |  |  | -2.6255 | -2.9204 | -2.3846 | -48.7256 | 48.7256 | -700 | -700 | -700
-23.749 | -0.197 | -100 | 59.803 | 60 | -23.749 | -26.4325 | -21.5602 |  |  |  | -2.6388 | -2.9369 | -2.3956 | -48.7256 | 48.7256 | -700 | -700 | -700
-23.8702 | -0.196 | -100 | 59.804 | 60 | -23.8702 | -26.5827 | -21.66 |  |  |  | -2.6522 | -2.9536 | -2.4067 | -48.7256 | 48.7256 | -700 | -700 | -700
-23.9926 | -0.195 | -100 | 59.805 | 60 | -23.9926 | -26.7346 | -21.7607 |  |  |  | -2.6658 | -2.9705 | -2.4179 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.1163 | -0.194 | -100 | 59.806 | 60 | -24.1163 | -26.8883 | -21.8624 |  |  |  | -2.6796 | -2.9876 | -2.4292 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.2412 | -0.193 | -100 | 59.807 | 60 | -24.2412 | -27.0437 | -21.9651 |  |  |  | -2.6935 | -3.0049 | -2.4406 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.3675 | -0.192 | -100 | 59.808 | 60 | -24.3675 | -27.2009 | -22.0687 |  |  |  | -2.7075 | -3.0223 | -2.4521 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.4951 | -0.191 | -100 | 59.809 | 60 | -24.4951 | -27.36 | -22.1733 |  |  |  | -2.7217 | -3.04 | -2.4637 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.624 | -0.19 | -100 | 59.81 | 60 | -24.624 | -27.5209 | -22.2789 |  |  |  | -2.736 | -3.0579 | -2.4754 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.7543 | -0.189 | -100 | 59.811 | 60 | -24.7543 | -27.6838 | -22.3855 |  |  |  | -2.7505 | -3.076 | -2.4873 | -48.7256 | 48.7256 | -700 | -700 | -700
-24.886 | -0.188 | -100 | 59.812 | 60 | -24.886 | -27.8486 | -22.4931 |  |  |  | -2.7651 | -3.0943 | -2.4992 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.019 | -0.187 | -100 | 59.813 | 60 | -25.019 | -28.0153 | -22.6017 |  |  |  | -2.7799 | -3.1128 | -2.5113 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.1535 | -0.186 | -100 | 59.814 | 60 | -25.1535 | -28.1841 | -22.7115 |  |  |  | -2.7948 | -3.1316 | -2.5235 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.2895 | -0.185 | -100 | 59.815 | 60 | -25.2895 | -28.3549 | -22.8222 |  |  |  | -2.8099 | -3.1505 | -2.5358 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.427 | -0.184 | -100 | 59.816 | 60 | -25.427 | -28.5278 | -22.9341 |  |  |  | -2.8252 | -3.1698 | -2.5482 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.5659 | -0.183 | -100 | 59.817 | 60 | -25.5659 | -28.7028 | -23.0471 |  |  |  | -2.8407 | -3.1892 | -2.5608 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.7064 | -0.182 | -100 | 59.818 | 60 | -25.7064 | -28.88 | -23.1612 |  |  |  | -2.8563 | -3.2089 | -2.5735 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.8484 | -0.181 | -100 | 59.819 | 60 | -25.8484 | -29.0594 | -23.2764 |  |  |  | -2.872 | -3.2288 | -2.5863 | -48.7256 | 48.7256 | -700 | -700 | -700
-25.992 | -0.18 | -100 | 59.82 | 60 | -25.992 | -29.241 | -23.3928 |  |  |  | -2.888 | -3.249 | -2.5992 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.1372 | -0.179 | -100 | 59.821 | 60 | -26.1372 | -29.4249 | -23.5104 |  |  |  | -2.9041 | -3.2694 | -2.6123 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.284 | -0.178 | -100 | 59.822 | 60 | -26.284 | -29.6111 | -23.6291 |  |  |  | -2.9204 | -3.2901 | -2.6255 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.4325 | -0.177 | -100 | 59.823 | 60 | -26.4325 | -29.7997 | -23.749 |  |  |  | -2.9369 | -3.3111 | -2.6388 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.5827 | -0.176 | -100 | 59.824 | 60 | -26.5827 | -29.9908 | -23.8702 |  |  |  | -2.9536 | -3.3323 | -2.6522 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.7346 | -0.175 | -100 | 59.825 | 60 | -26.7346 | -30.1843 | -23.9926 |  |  |  | -2.9705 | -3.3538 | -2.6658 | -48.7256 | 48.7256 | -700 | -700 | -700
-26.8883 | -0.174 | -100 | 59.826 | 60 | -26.8883 | -30.3803 | -24.1163 |  |  |  | -2.9876 | -3.3756 | -2.6796 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.0437 | -0.173 | -100 | 59.827 | 60 | -27.0437 | -30.5788 | -24.2412 |  |  |  | -3.0049 | -3.3976 | -2.6935 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.2009 | -0.172 | -100 | 59.828 | 60 | -27.2009 | -30.78 | -24.3675 |  |  |  | -3.0223 | -3.42 | -2.7075 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.36 | -0.171 | -100 | 59.829 | 60 | -27.36 | -30.9838 | -24.4951 |  |  |  | -3.04 | -3.4426 | -2.7217 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.5209 | -0.17 | -100 | 59.83 | 60 | -27.5209 | -31.1904 | -24.624 |  |  |  | -3.0579 | -3.4656 | -2.736 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.6838 | -0.169 | -100 | 59.831 | 60 | -27.6838 | -31.3997 | -24.7543 |  |  |  | -3.076 | -3.4889 | -2.7505 | -48.7256 | 48.7256 | -700 | -700 | -700
-27.8486 | -0.168 | -100 | 59.832 | 60 | -27.8486 | -31.6119 | -24.886 |  |  |  | -3.0943 | -3.5124 | -2.7651 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.0153 | -0.167 | -100 | 59.833 | 60 | -28.0153 | -31.8269 | -25.019 |  |  |  | -3.1128 | -3.5363 | -2.7799 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.1841 | -0.166 | -100 | 59.834 | 60 | -28.1841 | -32.0449 | -25.1535 |  |  |  | -3.1316 | -3.5605 | -2.7948 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.3549 | -0.165 | -100 | 59.835 | 60 | -28.3549 | -32.2659 | -25.2895 |  |  |  | -3.1505 | -3.5851 | -2.8099 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.5278 | -0.164 | -100 | 59.836 | 60 | -28.5278 | -32.49 | -25.427 |  |  |  | -3.1698 | -3.61 | -2.8252 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.7028 | -0.163 | -100 | 59.837 | 60 | -28.7028 | -32.7172 | -25.5659 |  |  |  | -3.1892 | -3.6352 | -2.8407 | -48.7256 | 48.7256 | -700 | -700 | -700
-28.88 | -0.162 | -100 | 59.838 | 60 | -28.88 | -32.9476 | -25.7064 |  |  |  | -3.2089 | -3.6608 | -2.8563 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.0594 | -0.161 | -100 | 59.839 | 60 | -29.0594 | -33.1813 | -25.8484 |  |  |  | -3.2288 | -3.6868 | -2.872 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.241 | -0.16 | -100 | 59.84 | 60 | -29.241 | -33.4183 | -25.992 |  |  |  | -3.249 | -3.7131 | -2.888 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.4249 | -0.159 | -100 | 59.841 | 60 | -29.4249 | -33.6587 | -26.1372 |  |  |  | -3.2694 | -3.7399 | -2.9041 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.6111 | -0.158 | -100 | 59.842 | 60 | -29.6111 | -33.9026 | -26.284 |  |  |  | -3.2901 | -3.767 | -2.9204 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.7997 | -0.157 | -100 | 59.843 | 60 | -29.7997 | -34.1501 | -26.4325 |  |  |  | -3.3111 | -3.7945 | -2.9369 | -48.7256 | 48.7256 | -700 | -700 | -700
-29.9908 | -0.156 | -100 | 59.844 | 60 | -29.9908 | -34.4012 | -26.5827 |  |  |  | -3.3323 | -3.8224 | -2.9536 | -48.7256 | 48.7256 | -700 | -700 | -700
-30.1843 | -0.155 | -100 | 59.845 | 60 | -30.1843 | -34.656 | -26.7346 |  |  |  | -3.3538 | -3.8507 | -2.9705 | -48.7256 | 48.7256 | -700 | -700 | -700
-30.3803 | -0.154 | -100 | 59.846 | 60 | -30.3803 | -34.9146 | -26.8883 |  |  |  | -3.3756 | -3.8794 | -2.9876 | -48.7256 | 48.7256 | -700 | -700 | -700
-30.5788 | -0.153 | -100 | 59.847 | 60 | -30.5788 | -35.1771 | -27.0437 |  |  |  | -3.3976 | -3.9086 | -3.0049 | -48.7256 | 48.7256 | -700 | -700 | -700
-30.78 | -0.152 | -100 | 59.848 | 60 | -30.78 | -35.4436 | -27.2009 |  |  |  | -3.42 | -3.9382 | -3.0223 | -48.7256 | 48.7256 | -700 | -700 | -700
-30.9838 | -0.151 | -100 | 59.849 | 60 | -30.9838 | -35.7142 | -27.36 |  |  |  | -3.4426 | -3.9682 | -3.04 | -48.7256 | 48.7256 | -700 | -700 | -700
-31.1904 | -0.15 | -100 | 59.85 | 60 | -31.1904 | -35.9889 | -27.5209 |  |  |  | -3.4656 | -3.9988 | -3.0579 | -48.7256 | 48.7256 | -700 | -700 | -700
-31.3997 | -0.149 | -100 | 59.851 | 60 | -31.3997 | -36.2679 | -27.6838 |  |  |  | -3.4889 | -4.0298 | -3.076 | -48.7256 | 48.7256 | -700 | -700 | -700
-31.6119 | -0.148 | -100 | 59.852 | 60 | -31.6119 | -36.5512 | -27.8486 |  |  |  | -3.5124 | -4.0613 | -3.0943 | -48.7256 | 48.7256 | -700 | -700 | -700
-31.8269 | -0.147 | -100 | 59.853 | 60 | -31.8269 | -36.8391 | -28.0153 |  |  |  | -3.5363 | -4.0932 | -3.1128 | -48.7256 | 48.7256 | -700 | -700 | -700
-32.0449 | -0.146 | -100 | 59.854 | 60 | -32.0449 | -37.1314 | -28.1841 |  |  |  | -3.5605 | -4.1257 | -3.1316 | -48.7256 | 48.7256 | -700 | -700 | -700
-32.2659 | -0.145 | -100 | 59.855 | 60 | -32.2659 | -37.4285 | -28.3549 |  |  |  | -3.5851 | -4.1587 | -3.1505 | -48.7256 | 48.7256 | -700 | -700 | -700
-32.49 | -0.144 | -100 | 59.856 | 60 | -32.49 | -37.7303 | -28.5278 |  |  |  | -3.61 | -4.1923 | -3.1698 | -48.7256 | 48.7256 | -700 | -700 | -700
-32.7172 | -0.143 | -100 | 59.857 | 60 | -32.7172 | -38.0371 | -28.7028 |  |  |  | -3.6352 | -4.2263 | -3.1892 | -48.7256 | 48.7256 | -700 | -700 | -700
-32.9476 | -0.142 | -100 | 59.858 | 60 | -32.9476 | -38.3489 | -28.88 |  |  |  | -3.6608 | -4.261 | -3.2089 | -48.7256 | 48.7256 | -700 | -700 | -700
-33.1813 | -0.141 | -100 | 59.859 | 60 | -33.1813 | -38.6658 | -29.0594 |  |  |  | -3.6868 | -4.2962 | -3.2288 | -48.7256 | 48.7256 | -700 | -700 | -700
-33.4183 | -0.14 | -100 | 59.86 | 60 | -33.4183 | -38.988 | -29.241 |  |  |  | -3.7131 | -4.332 | -3.249 | -48.7256 | 48.7256 | -700 | -700 | -700
-33.6587 | -0.139 | -100 | 59.861 | 60 | -33.6587 | -39.3156 | -29.4249 |  |  |  | -3.7399 | -4.3684 | -3.2694 | -48.7256 | 48.7256 | -700 | -700 | -700
-33.9026 | -0.138 | -100 | 59.862 | 60 | -33.9026 | -39.6488 | -29.6111 |  |  |  | -3.767 | -4.4054 | -3.2901 | -48.7256 | 48.7256 | -700 | -700 | -700
-34.1501 | -0.137 | -100 | 59.863 | 60 | -34.1501 | -39.9877 | -29.7997 |  |  |  | -3.7945 | -4.4431 | -3.3111 | -48.7256 | 48.7256 | -700 | -700 | -700
-34.4012 | -0.136 | -100 | 59.864 | 60 | -34.4012 | -40.3324 | -29.9908 |  |  |  | -3.8224 | -4.4814 | -3.3323 | -48.7256 | 48.7256 | -700 | -700 | -700
-34.656 | -0.135 | -100 | 59.865 | 60 | -34.656 | -40.6831 | -30.1843 |  |  |  | -3.8507 | -4.5203 | -3.3538 | -48.7256 | 48.7256 | -700 | -700 | -700
-34.9146 | -0.134 | -100 | 59.866 | 60 | -34.9146 | -41.04 | -30.3803 |  |  |  | -3.8794 | -4.56 | -3.3756 | -48.7256 | 48.7256 | -700 | -700 | -700
-35.1771 | -0.133 | -100 | 59.867 | 60 | -35.1771 | -41.4032 | -30.5788 |  |  |  | -3.9086 | -4.6004 | -3.3976 | -48.7256 | 48.7256 | -700 | -700 | -700
-35.4436 | -0.132 | -100 | 59.868 | 60 | -35.4436 | -41.7729 | -30.78 |  |  |  | -3.9382 | -4.6414 | -3.42 | -48.7256 | 48.7256 | -700 | -700 | -700
-35.7142 | -0.131 | -100 | 59.869 | 60 | -35.7142 | -42.1492 | -30.9838 |  |  |  | -3.9682 | -4.6832 | -3.4426 | -48.7256 | 48.7256 | -700 | -700 | -700
-35.9889 | -0.13 | -100 | 59.87 | 60 | -35.9889 | -42.5324 | -31.1904 |  |  |  | -3.9988 | -4.7258 | -3.4656 | -48.7256 | 48.7256 | -700 | -700 | -700
-36.2679 | -0.129 | -100 | 59.871 | 60 | -36.2679 | -42.9226 | -31.3997 |  |  |  | -4.0298 | -4.7692 | -3.4889 | -48.7256 | 48.7256 | -700 | -700 | -700
-36.5512 | -0.128 | -100 | 59.872 | 60 | -36.5512 | -43.32 | -31.6119 |  |  |  | -4.0613 | -4.8133 | -3.5124 | -48.7256 | 48.7256 | -700 | -700 | -700
-36.8391 | -0.127 | -100 | 59.873 | 60 | -36.8391 | -43.7249 | -31.8269 |  |  |  | -4.0932 | -4.8583 | -3.5363 | -48.7256 | 48.7256 | -700 | -700 | -700
-37.1314 | -0.126 | -100 | 59.874 | 60 | -37.1314 | -44.1374 | -32.0449 |  |  |  | -4.1257 | -4.9042 | -3.5605 | -48.7256 | 48.7256 | -700 | -700 | -700
-37.4285 | -0.125 | -100 | 59.875 | 60 | -37.4285 | -44.5577 | -32.2659 |  |  |  | -4.1587 | -4.9509 | -3.5851 | -48.7256 | 48.7256 | -700 | -700 | -700
-37.7303 | -0.124 | -100 | 59.876 | 60 | -37.7303 | -44.9862 | -32.49 |  |  |  | -4.1923 | -4.9985 | -3.61 | -48.7256 | 48.7256 | -700 | -700 | -700
-38.0371 | -0.123 | -100 | 59.877 | 60 | -38.0371 | -45.4229 | -32.7172 |  |  |  | -4.2263 | -5.047 | -3.6352 | -48.7256 | 48.7256 | -700 | -700 | -700
-38.3489 | -0.122 | -100 | 59.878 | 60 | -38.3489 | -45.8682 | -32.9476 |  |  |  | -4.261 | -5.0965 | -3.6608 | -48.7256 | 48.7256 | -700 | -700 | -700
-38.6658 | -0.121 | -100 | 59.879 | 60 | -38.6658 | -46.3224 | -33.1813 |  |  |  | -4.2962 | -5.1469 | -3.6868 | -48.7256 | 48.7256 | -700 | -700 | -700
-38.988 | -0.12 | -100 | 59.88 | 60 | -38.988 | -46.7856 | -33.4183 |  |  |  | -4.332 | -5.1984 | -3.7131 | -48.7256 | 48.7256 | -700 | -700 | -700
-39.3156 | -0.119 | -100 | 59.881 | 60 | -39.3156 | -47.2582 | -33.6587 |  |  |  | -4.3684 | -5.2509 | -3.7399 | -48.7256 | 48.7256 | -700 | -700 | -700
-39.6488 | -0.118 | -100 | 59.882 | 60 | -39.6488 | -47.7404 | -33.9026 |  |  |  | -4.4054 | -5.3045 | -3.767 | -48.7256 | 48.7256 | -700 | -700 | -700
-39.9877 | -0.117 | -100 | 59.883 | 60 | -39.9877 | -48.2326 | -34.1501 |  |  |  | -4.4431 | -5.3592 | -3.7945 | -48.7256 | 48.7256 | -700 | -700 | -700
-40.3324 | -0.116 | -100 | 59.884 | 60 | -40.3324 | -48.735 | -34.4012 |  |  |  | -4.4814 | -5.415 | -3.8224 | -48.7256 | 48.7256 | -700 | -700 | -700
-40.6831 | -0.115 | -100 | 59.885 | 60 | -40.6831 | -49.248 | -34.656 |  |  |  | -4.5203 | -5.472 | -3.8507 | -48.7256 | 48.7256 | -700 | -700 | -700
-41.04 | -0.114 | -100 | 59.886 | 60 | -41.04 | -49.7719 | -34.9146 |  |  |  | -4.56 | -5.5302 | -3.8794 | -48.7256 | 48.7256 | -700 | -700 | -700
-41.4032 | -0.113 | -100 | 59.887 | 60 | -41.4032 | -50.3071 | -35.1771 |  |  |  | -4.6004 | -5.5897 | -3.9086 | -48.7256 | 48.7256 | -700 | -700 | -700
-41.7729 | -0.112 | -100 | 59.888 | 60 | -41.7729 | -50.8539 | -35.4436 |  |  |  | -4.6414 | -5.6504 | -3.9382 | -48.7256 | 48.7256 | -700 | -700 | -700
-42.1492 | -0.111 | -100 | 59.889 | 60 | -42.1492 | -51.4127 | -35.7142 |  |  |  | -4.6832 | -5.7125 | -3.9682 | -48.7256 | 48.7256 | -700 | -700 | -700
-42.5324 | -0.11 | -100 | 59.89 | 60 | -42.5324 | -51.984 | -35.9889 |  |  |  | -4.7258 | -5.776 | -3.9988 | -48.7256 | 48.7256 | -700 | -700 | -700
-42.9226 | -0.109 | -100 | 59.891 | 60 | -42.9226 | -52.5681 | -36.2679 |  |  |  | -4.7692 | -5.8409 | -4.0298 | -48.7256 | 48.7256 | -700 | -700 | -700
-43.32 | -0.108 | -100 | 59.892 | 60 | -43.32 | -53.1655 | -36.5512 |  |  |  | -4.8133 | -5.9073 | -4.0613 | -48.7256 | 48.7256 | -700 | -700 | -700
-43.7249 | -0.107 | -100 | 59.893 | 60 | -43.7249 | -53.7766 | -36.8391 |  |  |  | -4.8583 | -5.9752 | -4.0932 | -48.7256 | 48.7256 | -700 | -700 | -700
-44.1374 | -0.106 | -100 | 59.894 | 60 | -44.1374 | -54.4019 | -37.1314 |  |  |  | -4.9042 | -6.0447 | -4.1257 | -48.7256 | 48.7256 | -700 | -700 | -700
-44.5577 | -0.105 | -100 | 59.895 | 60 | -44.5577 | -55.0419 | -37.4285 |  |  |  | -4.9509 | -6.1158 | -4.1587 | -48.7256 | 48.7256 | -700 | -700 | -700
-44.9862 | -0.104 | -100 | 59.896 | 60 | -44.9862 | -55.6971 | -37.7303 |  |  |  | -4.9985 | -6.1886 | -4.1923 | -48.7256 | 48.7256 | -700 | -700 | -700
-45.4229 | -0.103 | -100 | 59.897 | 60 | -45.4229 | -56.3682 | -38.0371 |  |  |  | -5.047 | -6.2631 | -4.2263 | -48.7256 | 48.7256 | -700 | -700 | -700
-45.8682 | -0.102 | -100 | 59.898 | 60 | -45.8682 | -57.0556 | -38.3489 |  |  |  | -5.0965 | -6.3395 | -4.261 | -48.7256 | 48.7256 | -700 | -700 | -700
-46.3224 | -0.101 | -100 | 59.899 | 60 | -46.3224 | -57.76 | -38.6658 |  |  |  | -5.1469 | -6.4178 | -4.2962 | -48.7256 | 48.7256 | -700 | -700 | -700
-46.7856 | -0.1 | -100 | 59.9 | 60 | -46.7856 | -58.482 | -38.988 |  |  |  | -5.1984 | -6.498 | -4.332 | -48.7256 | 48.7256 | -700 | -700 | -700
-47.2582 | -0.099 | -100 | 59.901 | 60 | -47.2582 | -59.2223 | -39.3156 |  |  |  | -5.2509 | -6.5803 | -4.3684 | -48.7256 | 48.7256 | -700 | -700 | -700
-47.7404 | -0.098 | -100 | 59.902 | 60 | -47.7404 | -59.9815 | -39.6488 |  |  |  | -5.3045 | -6.6646 | -4.4054 | -48.7256 | 48.7256 | -700 | -700 | -700
-48.2326 | -0.097 | -100 | 59.903 | 60 | -48.2326 | -60.7605 | -39.9877 |  |  |  | -5.3592 | -6.7512 | -4.4431 | -48.7256 | 48.7256 | -700 | -700 | -700
-48.735 | -0.096 | -100 | 59.904 | 60 | -48.735 | -61.56 | -40.3324 |  |  |  | -5.415 | -6.84 | -4.4814 | -48.7256 | 48.7256 | -700 | -700 | -700
-49.248 | -0.095 | -100 | 59.905 | 60 | -49.248 | -62.3808 | -40.6831 |  |  |  | -5.472 | -6.9312 | -4.5203 | -48.7256 | 48.7256 | -700 | -700 | -700
-49.7719 | -0.094 | -100 | 59.906 | 60 | -49.7719 | -63.2238 | -41.04 |  |  |  | -5.5302 | -7.0249 | -4.56 | -48.7256 | 48.7256 | -700 | -700 | -700
-50.3071 | -0.093 | -100 | 59.907 | 60 | -50.3071 | -64.0899 | -41.4032 |  |  |  | -5.5897 | -7.1211 | -4.6004 | -48.7256 | 48.7256 | -700 | -700 | -700
-50.8539 | -0.092 | -100 | 59.908 | 60 | -50.8539 | -64.98 | -41.7729 |  |  |  | -5.6504 | -7.22 | -4.6414 | -48.7256 | 48.7256 | -700 | -700 | -700
-51.4127 | -0.091 | -100 | 59.909 | 60 | -51.4127 | -65.8952 | -42.1492 |  |  |  | -5.7125 | -7.3217 | -4.6832 | -48.7256 | 48.7256 | -700 | -700 | -700
-51.984 | -0.09 | -100 | 59.91 | 60 | -51.984 | -66.8366 | -42.5324 |  |  |  | -5.776 | -7.4263 | -4.7258 | -48.7256 | 48.7256 | -700 | -700 | -700
-52.5681 | -0.089 | -100 | 59.911 | 60 | -52.5681 | -67.8052 | -42.9226 |  |  |  | -5.8409 | -7.5339 | -4.7692 | -48.7256 | 48.7256 | -700 | -700 | -700
-53.1655 | -0.088 | -100 | 59.912 | 60 | -53.1655 | -68.8024 | -43.32 |  |  |  | -5.9073 | -7.6447 | -4.8133 | -48.7256 | 48.7256 | -700 | -700 | -700
-53.7766 | -0.087 | -100 | 59.913 | 60 | -53.7766 | -69.8293 | -43.7249 |  |  |  | -5.9752 | -7.7588 | -4.8583 | -48.7256 | 48.7256 | -700 | -700 | -700
-54.4019 | -0.086 | -100 | 59.914 | 60 | -54.4019 | -70.8873 | -44.1374 |  |  |  | -6.0447 | -7.8764 | -4.9042 | -48.7256 | 48.7256 | -700 | -700 | -700
-55.0419 | -0.085 | -100 | 59.915 | 60 | -55.0419 | -71.9778 | -44.5577 |  |  |  | -6.1158 | -7.9975 | -4.9509 | -48.7256 | 48.7256 | -700 | -700 | -700
-55.6971 | -0.084 | -100 | 59.916 | 60 | -55.6971 | -73.1025 | -44.9862 |  |  |  | -6.1886 | -8.1225 | -4.9985 | -48.7256 | 48.7256 | -700 | -700 | -700
-56.3682 | -0.083 | -100 | 59.917 | 60 | -56.3682 | -74.2629 | -45.4229 |  |  |  | -6.2631 | -8.2514 | -5.047 | -48.7256 | 48.7256 | -700 | -700 | -700
-57.0556 | -0.082 | -100 | 59.918 | 60 | -57.0556 | -75.4606 | -45.8682 |  |  |  | -6.3395 | -8.3845 | -5.0965 | -48.7256 | 48.7256 | -700 | -700 | -700
-57.76 | -0.081 | -100 | 59.919 | 60 | -57.76 | -76.6977 | -46.3224 |  |  |  | -6.4178 | -8.522 | -5.1469 | -48.7256 | 48.7256 | -700 | -700 | -700
-58.482 | -0.08 | -100 | 59.92 | 60 | -58.482 | -77.976 | -46.7856 |  |  |  | -6.498 | -8.664 | -5.1984 | -48.7256 | 48.7256 | -700 | -700 | -700
-59.2223 | -0.079 | -100 | 59.921 | 60 | -59.2223 | -79.2976 | -47.2582 |  |  |  | -6.5803 | -8.8108 | -5.2509 | -48.7256 | 48.7256 | -700 | -700 | -700
-59.9815 | -0.078 | -100 | 59.922 | 60 | -59.9815 | -80.6648 | -47.7404 |  |  |  | -6.6646 | -8.9628 | -5.3045 | -48.7256 | 48.7256 | -700 | -700 | -700
-60.7605 | -0.077 | -100 | 59.923 | 60 | -60.7605 | -82.08 | -48.2326 |  |  |  | -6.7512 | -9.12 | -5.3592 | -48.7256 | 48.7256 | -700 | -700 | -700
-61.56 | -0.076 | -100 | 59.924 | 60 | -61.56 | -83.5457 | -48.735 |  |  |  | -6.84 | -9.2829 | -5.415 | -48.7256 | 48.7256 | -700 | -700 | -700
-62.3808 | -0.075 | -100 | 59.925 | 60 | -62.3808 | -85.0647 | -49.248 |  |  |  | -6.9312 | -9.4516 | -5.472 | -48.7256 | 48.7256 | -700 | -700 | -700
-63.2238 | -0.074 | -100 | 59.926 | 60 | -63.2238 | -86.64 | -49.7719 |  |  |  | -7.0249 | -9.6267 | -5.5302 | -48.7256 | 48.7256 | -700 | -700 | -700
-64.0899 | -0.073 | -100 | 59.927 | 60 | -64.0899 | -88.2747 | -50.3071 |  |  |  | -7.1211 | -9.8083 | -5.5897 | -48.7256 | 48.7256 | -700 | -700 | -700
-64.98 | -0.072 | -100 | 59.928 | 60 | -64.98 | -89.9723 | -50.8539 |  |  |  | -7.22 | -9.9969 | -5.6504 | -48.7256 | 48.7256 | -700 | -700 | -700
-65.8952 | -0.071 | -100 | 59.929 | 60 | -65.8952 | -91.7365 | -51.4127 |  |  |  | -7.3217 | -10.1929 | -5.7125 | -48.7256 | 48.7256 | -700 | -700 | -700
-66.8366 | -0.07 | -100 | 59.93 | 60 | -66.8366 | -93.5712 | -51.984 |  |  |  | -7.4263 | -10.3968 | -5.776 | -48.7256 | 48.7256 | -700 | -700 | -700
-67.8052 | -0.069 | -100 | 59.931 | 60 | -67.8052 | -95.4808 | -52.5681 |  |  |  | -7.5339 | -10.609 | -5.8409 | -48.7256 | 48.7256 | -700 | -700 | -700
-68.8024 | -0.068 | -100 | 59.932 | 60 | -68.8024 | -97.47 | -53.1655 |  |  |  | -7.6447 | -10.83 | -5.9073 | -48.7256 | 48.7256 | -700 | -700 | -700
-69.8293 | -0.067 | -100 | 59.933 | 60 | -69.8293 | -99.5438 | -53.7766 |  |  |  | -7.7588 | -11.0604 | -5.9752 | -48.7256 | 48.7256 | -700 | -700 | -700
-70.8873 | -0.066 | -100 | 59.934 | 60 | -70.8873 | -101.7078 | -54.4019 |  |  |  | -7.8764 | -11.3009 | -6.0447 | -48.7256 | 48.7256 | -700 | -700 | -700
-71.9778 | -0.065 | -100 | 59.935 | 60 | -71.9778 | -103.968 | -55.0419 |  |  |  | -7.9975 | -11.552 | -6.1158 | -48.7256 | 48.7256 | -700 | -700 | -700
-73.1025 | -0.064 | -100 | 59.936 | 60 | -73.1025 | -106.3309 | -55.6971 |  |  |  | -8.1225 | -11.8145 | -6.1886 | -48.7256 | 48.7256 | -700 | -700 | -700
-74.2629 | -0.063 | -100 | 59.937 | 60 | -74.2629 | -108.8037 | -56.3682 |  |  |  | -8.2514 | -12.0893 | -6.2631 | -48.7256 | 48.7256 | -700 | -700 | -700
-75.4606 | -0.062 | -100 | 59.938 | 60 | -75.4606 | -111.3943 | -57.0556 |  |  |  | -8.3845 | -12.3771 | -6.3395 | -48.7256 | 48.7256 | -700 | -700 | -700
-76.6977 | -0.061 | -100 | 59.939 | 60 | -76.6977 | -114.1112 | -57.76 |  |  |  | -8.522 | -12.679 | -6.4178 | -48.7256 | 48.7256 | -700 | -700 | -700
-77.976 | -0.06 | -100 | 59.94 | 60 | -77.976 | -116.964 | -58.482 |  |  |  | -8.664 | -12.996 | -6.498 | -48.7256 | 48.7256 | -700 | -700 | -700
-79.2976 | -0.059 | -100 | 59.941 | 60 | -79.2976 | -119.9631 | -59.2223 |  |  |  | -8.8108 | -13.3292 | -6.5803 | -48.7256 | 48.7256 | -700 | -700 | -700
-80.6648 | -0.058 | -100 | 59.942 | 60 | -80.6648 | -123.12 | -59.9815 |  |  |  | -8.9628 | -13.68 | -6.6646 | -48.7256 | 48.7256 | -700 | -700 | -700
-82.08 | -0.057 | -100 | 59.943 | 60 | -82.08 | -126.4476 | -60.7605 |  |  |  | -9.12 | -14.0497 | -6.7512 | -48.7256 | 48.7256 | -700 | -700 | -700
-83.5457 | -0.056 | -100 | 59.944 | 60 | -83.5457 | -129.96 | -61.56 |  |  |  | -9.2829 | -14.44 | -6.84 | -48.7256 | 48.7256 | -700 | -700 | -700
-85.0647 | -0.055 | -100 | 59.945 | 60 | -85.0647 | -133.6731 | -62.3808 |  |  |  | -9.4516 | -14.8526 | -6.9312 | -48.7256 | 48.7256 | -700 | -700 | -700
-86.64 | -0.054 | -100 | 59.946 | 60 | -86.64 | -137.6047 | -63.2238 |  |  |  | -9.6267 | -15.2894 | -7.0249 | -48.7256 | 48.7256 | -700 | -700 | -700
-88.2747 | -0.053 | -100 | 59.947 | 60 | -88.2747 | -141.7745 | -64.0899 |  |  |  | -9.8083 | -15.7527 | -7.1211 | -48.7256 | 48.7256 | -700 | -700 | -700
-89.9723 | -0.052 | -100 | 59.948 | 60 | -89.9723 | -146.205 | -64.98 |  |  |  | -9.9969 | -16.245 | -7.22 | -48.7256 | 48.7256 | -700 | -700 | -700
-91.7365 | -0.051 | -100 | 59.949 | 60 | -91.7365 | -150.9213 | -65.8952 |  |  |  | -10.1929 | -16.769 | -7.3217 | -48.7256 | 48.7256 | -700 | -700 | -700
-93.5712 | -0.05 | -100 | 59.95 | 60 | -93.5712 | -155.952 | -66.8366 |  |  |  | -10.3968 | -17.328 | -7.4263 | -48.7256 | 48.7256 | -700 | -700 | -700
-95.4808 | -0.049 | -100 | 59.951 | 60 | -95.4808 | -161.3296 | -67.8052 |  |  |  | -10.609 | -17.9255 | -7.5339 | -48.7256 | 48.7256 | -700 | -700 | -700
-97.47 | -0.048 | -100 | 59.952 | 60 | -97.47 | -167.0914 | -68.8024 |  |  |  | -10.83 | -18.5657 | -7.6447 | -48.7256 | 48.7256 | -700 | -700 | -700
-99.5438 | -0.047 | -100 | 59.953 | 60 | -99.5438 | -173.28 | -69.8293 |  |  |  | -11.0604 | -19.2533 | -7.7588 | -48.7256 | 48.7256 | -700 | -700 | -700
-101.7078 | -0.046 | -100 | 59.954 | 60 | -101.7078 | -179.9446 | -70.8873 |  |  |  | -11.3009 | -19.9938 | -7.8764 | -48.7256 | 48.7256 | -700 | -700 | -700
-103.968 | -0.045 | -100 | 59.955 | 60 | -103.968 | -187.1424 | -71.9778 |  |  |  | -11.552 | -20.7936 | -7.9975 | -48.7256 | 48.7256 | -700 | -700 | -700
-106.3309 | -0.044 | -100 | 59.956 | 60 | -106.3309 | -194.94 | -73.1025 |  |  |  | -11.8145 | -21.66 | -8.1225 | -48.7256 | 48.7256 | -700 | -700 | -700
-108.8037 | -0.043 | -100 | 59.957 | 60 | -108.8037 | -203.4156 | -74.2629 |  |  |  | -12.0893 | -22.6017 | -8.2514 | -48.7256 | 48.7256 | -700 | -700 | -700
-111.3943 | -0.042 | -100 | 59.958 | 60 | -111.3943 | -212.6618 | -75.4606 |  |  |  | -12.3771 | -23.6291 | -8.3845 | -48.7256 | 48.7256 | -700 | -700 | -700
-114.1112 | -0.041 | -100 | 59.959 | 60 | -114.1112 | -222.7886 | -76.6977 |  |  |  | -12.679 | -24.7543 | -8.522 | -48.7256 | 48.7256 | -700 | -700 | -700
-116.964 | -0.04 | -100 | 59.96 | 60 | -116.964 | -233.928 | -77.976 |  |  |  | -12.996 | -25.992 | -8.664 | -48.7256 | 48.7256 | -700 | -700 | -700
-119.9631 | -0.039 | -100 | 59.961 | 60 | -119.9631 | -246.24 | -79.2976 |  |  |  | -13.3292 | -27.36 | -8.8108 | -48.7256 | 48.7256 | -700 | -700 | -700
-123.12 | -0.038 | -100 | 59.962 | 60 | -123.12 | -259.92 | -80.6648 |  |  |  | -13.68 | -28.88 | -8.9628 | -48.7256 | 48.7256 | -700 | -700 | -700
-126.4476 | -0.037 | -100 | 59.963 | 60 | -126.4476 | -275.2094 | -82.08 |  |  |  | -14.0497 | -30.5788 | -9.12 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-129.96 | -0.036 | -100 | 59.964 | 60 | -129.96 | -292.41 | -83.5457 |  |  |  | -14.44 | -32.49 | -9.2829 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-133.6731 | -0.035 | -100 | 59.965 | 60 | -133.6731 | -311.904 | -85.0647 |  |  |  | -14.8526 | -34.656 | -9.4516 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-137.6047 | -0.034 | -100 | 59.966 | 60 | -137.6047 | -334.1828 | -86.64 |  |  |  | -15.2894 | -37.1314 | -9.6267 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-141.7745 | -0.033 | -100 | 59.967 | 60 | -141.7745 | -359.8892 | -88.2747 |  |  |  | -15.7527 | -39.9877 | -9.8083 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-146.205 | -0.032 | -100 | 59.968 | 60 | -146.205 | -389.88 | -89.9723 |  |  |  | -16.245 | -43.32 | -9.9969 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-150.9213 | -0.031 | -100 | 59.969 | 60 | -150.9213 | -425.3236 | -91.7365 |  |  |  | -16.769 | -47.2582 | -10.1929 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-155.952 | -0.03 | -100 | 59.97 | 60 | -155.952 | -467.856 | -93.5712 |  |  |  | -17.328 | -51.984 | -10.3968 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-161.3296 | -0.029 | -100 | 59.971 | 60 | -161.3296 | -519.8399 | -95.4808 |  |  |  | -17.9255 | -57.76 | -10.609 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-167.0914 | -0.028 | -100 | 59.972 | 60 | -167.0914 | -584.8199 | -97.47 |  |  |  | -18.5657 | -64.98 | -10.83 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-173.28 | -0.027 | -100 | 59.973 | 60 | -173.28 | -668.3656 | -99.5438 |  |  |  | -19.2533 | -74.2629 | -11.0604 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-179.9446 | -0.026 | -100 | 59.974 | 60 | -179.9446 | -779.7599 | -101.7078 |  |  |  | -19.9938 | -86.64 | -11.3009 | -48.7256 | 48.7256 | -700 | -699.9999 | -700
-187.1424 | -0.025 | -100 | 59.975 | 60 | -187.1424 | -935.7118 | -103.968 |  |  |  | -20.7936 | -103.968 | -11.552 | -48.7256 | 48.7256 | -700 | -699.9998 | -700
-194.94 | -0.024 | -100 | 59.976 | 60 | -194.94 | -1169.6397 | -106.3309 |  |  |  | -21.66 | -129.96 | -11.8145 | -48.7256 | 48.7256 | -700 | -699.9998 | -700
-203.4156 | -0.023 | -100 | 59.977 | 60 | -203.4156 | -1559.5195 | -108.8037 |  |  |  | -22.6017 | -173.28 | -12.0893 | -48.7256 | 48.7256 | -700 | -699.9997 | -700
-212.6618 | -0.022 | -100 | 59.978 | 60 | -212.6618 | -2339.2788 | -111.3943 |  |  |  | -23.6291 | -259.92 | -12.3771 | -48.7256 | 48.7256 | -700 | -699.9996 | -700
-222.7886 | -0.021 | -100 | 59.979 | 60 | -222.7886 | -4678.5553 | -114.1112 |  |  |  | -24.7543 | -519.84 | -12.679 | -48.7256 | 48.7256 | -700 | -699.9991 | -700
-228.2224 | -0.0205 | -100 | 59.9795 | 60 | -228.2224 | -9357.1013 | -115.52 |  |  |  | -25.358 | -1039.68 | -12.8356 | -48.7256 | 48.7256 | -700 | -699.9982 | -700
-232.7642 | -0.0201 | -100 | 59.9799 | 60 | -232.7642 | -46785.1322 | -116.6723 |  |  |  | -25.8627 | -5198.4 | -12.9636 | -48.7256 | 48.7256 | -700 | -699.991 | -700
-233.928 | -0.02 | -100 | 59.98 | 60 | -233.928 |  | -116.964 |  | 5.1846e+12 |  | -25.992 | 578073183274.005 | -12.996 | -48.7256 | 48.7256 | -700 | -696.8823 | -700
-235.1035 | -0.0199 | -100 | 59.9801 | 60 | -235.1035 |  | -117.2571 |  | 46785.6 |  | -26.1226 | 5198.4 | -13.0286 | -48.7256 | 48.7256 | -700 | -700 | -700
-239.9261 | -0.0195 | -100 | 59.9805 | 60 | -239.9261 |  | -118.4446 |  | 9357.12 |  | -26.6585 | 1039.68 | -13.1605 | -48.7256 | 48.7256 | -700 | -700 | -700
-246.24 | -0.019 | -100 | 59.981 | 60 | -246.24 |  | -119.9631 |  | 4678.56 |  | -27.36 | 519.84 | -13.3292 | -48.7256 | 48.7256 | -700 | -700 | -700
-259.92 | -0.018 | -100 | 59.982 | 60 | -259.92 |  | -123.12 |  | 2339.28 |  | -28.88 | 259.92 | -13.68 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-275.2094 | -0.017 | -100 | 59.983 | 60 | -275.2094 |  | -126.4476 |  | 1559.52 |  | -30.5788 | 173.28 | -14.0497 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-292.41 | -0.016 | -100 | 59.984 | 60 | -292.41 |  | -129.96 |  | 1169.64 |  | -32.49 | 129.96 | -14.44 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-311.904 | -0.015 | -100 | 59.985 | 60 | -311.904 |  | -133.6731 |  | 935.712 |  | -34.656 | 103.968 | -14.8526 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-334.1828 | -0.014 | -100 | 59.986 | 60 | -334.1828 |  | -137.6047 |  | 779.76 |  | -37.1314 | 86.64 | -15.2894 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-359.8892 | -0.013 | -100 | 59.987 | 60 | -359.8892 |  | -141.7745 |  | 668.3657 |  | -39.9877 | 74.2629 | -15.7527 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-389.88 | -0.012 | -100 | 59.988 | 60 | -389.88 |  | -146.205 |  | 584.82 |  | -43.32 | 64.98 | -16.245 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-425.3236 | -0.011 | -100 | 59.989 | 60 | -425.3236 |  | -150.9213 |  | 519.84 |  | -47.2582 | 57.76 | -16.769 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-467.856 | -0.01 | -100 | 59.99 | 60 | -467.856 |  | -155.952 |  | 467.856 |  | -51.984 | 51.984 | -17.328 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-519.8399 | -0.009 | -100 | 59.991 | 60 | -519.8399 |  | -161.3296 |  | 425.3236 |  | -57.76 | 47.2582 | -17.9255 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-584.8199 | -0.008 | -100 | 59.992 | 60 | -584.8199 |  | -167.0914 |  | 389.88 |  | -64.98 | 43.32 | -18.5657 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-668.3656 | -0.007 | -100 | 59.993 | 60 | -668.3656 |  | -173.28 |  | 359.8892 |  | -74.2629 | 39.9877 | -19.2533 | -48.7256 | 48.7256 | -699.9999 | -700 | -700
-779.7599 | -0.006 | -100 | 59.994 | 60 | -779.7599 |  | -179.9446 |  | 334.1829 |  | -86.64 | 37.1314 | -19.9938 | -48.7256 | 48.7256 | -699.9998 | -700 | -700
-935.7118 | -0.005 | -100 | 59.995 | 60 | -935.7118 |  | -187.1424 |  | 311.904 |  | -103.968 | 34.656 | -20.7936 | -48.7256 | 48.7256 | -699.9998 | -700 | -700
-1169.6397 | -0.004 | -100 | 59.996 | 60 | -1169.6397 |  | -194.94 |  | 292.41 |  | -129.96 | 32.49 | -21.66 | -48.7256 | 48.7256 | -699.9998 | -700 | -700
-1559.5195 | -0.003 | -100 | 59.997 | 60 | -1559.5195 |  | -203.4156 |  | 275.2094 |  | -173.28 | 30.5788 | -22.6017 | -48.7256 | 48.7256 | -699.9997 | -700 | -700
-2339.2788 | -0.002 | -100 | 59.998 | 60 | -2339.2788 |  | -212.6618 |  | 259.92 |  | -259.92 | 28.88 | -23.6291 | -48.7256 | 48.7256 | -699.9996 | -700 | -700
-4678.5553 | -0.001 | -100 | 59.999 | 60 | -4678.5553 |  | -222.7886 |  | 246.24 |  | -519.84 | 27.36 | -24.7543 | -48.7256 | 48.7256 | -699.9991 | -700 | -700
-9357.1013 | -0.0005 | -100 | 59.9995 | 60 | -9357.1013 |  | -228.2224 |  | 239.9262 |  | -1039.68 | 26.6585 | -25.358 | -48.7256 | 48.7256 | -699.9982 | -700 | -700
-46785.1321 | -0.0001 | -100 | 59.9999 | 60 | -46785.1321 |  | -232.7642 |  | 235.1035 |  | -5198.4 | 26.1226 | -25.8627 | -48.7256 | 48.7256 | -699.991 | -700 | -700
46785.6 | 0.0001 | -100 | 60.0001 | 60 |  |  | -235.1035 | 46785.6 | 232.7642 |  | 5198.4 | 25.8627 | -26.1226 | -48.7256 | 48.7256 | -700 | -700 | -700
9357.12 | 0.0005 | -100 | 60.0005 | 60 |  |  | -239.9261 | 9357.12 | 228.2224 |  | 1039.68 | 25.358 | -26.6585 | -48.7256 | 48.7256 | -700 | -700 | -700
4678.56 | 0.001 | -100 | 60.001 | 60 |  |  | -246.24 | 4678.56 | 222.7886 |  | 519.84 | 24.7543 | -27.36 | -48.7256 | 48.7256 | -700 | -700 | -700
2339.28 | 0.002 | -100 | 60.002 | 60 |  |  | -259.92 | 2339.28 | 212.6618 |  | 259.92 | 23.6291 | -28.88 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
1559.52 | 0.003 | -100 | 60.003 | 60 |  |  | -275.2094 | 1559.52 | 203.4157 |  | 173.28 | 22.6017 | -30.5788 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
1169.64 | 0.004 | -100 | 60.004 | 60 |  |  | -292.41 | 1169.64 | 194.94 |  | 129.96 | 21.66 | -32.49 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
935.712 | 0.005 | -100 | 60.005 | 60 |  |  | -311.904 | 935.712 | 187.1424 |  | 103.968 | 20.7936 | -34.656 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
779.76 | 0.006 | -100 | 60.006 | 60 |  |  | -334.1828 | 779.76 | 179.9446 |  | 86.64 | 19.9938 | -37.1314 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
668.3657 | 0.007 | -100 | 60.007 | 60 |  |  | -359.8892 | 668.3657 | 173.28 |  | 74.2629 | 19.2533 | -39.9877 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
584.82 | 0.008 | -100 | 60.008 | 60 |  |  | -389.88 | 584.82 | 167.0914 |  | 64.98 | 18.5657 | -43.32 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
519.84 | 0.009 | -100 | 60.009 | 60 |  |  | -425.3236 | 519.84 | 161.3297 |  | 57.76 | 17.9255 | -47.2582 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
467.856 | 0.01 | -100 | 60.01 | 60 |  |  | -467.856 | 467.856 | 155.952 |  | 51.984 | 17.328 | -51.984 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
425.3236 | 0.011 | -100 | 60.011 | 60 |  |  | -519.8399 | 425.3236 | 150.9213 |  | 47.2582 | 16.769 | -57.76 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
389.88 | 0.012 | -100 | 60.012 | 60 |  |  | -584.8199 | 389.88 | 146.205 |  | 43.32 | 16.245 | -64.98 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
359.8892 | 0.013 | -100 | 60.013 | 60 |  |  | -668.3656 | 359.8892 | 141.7745 |  | 39.9877 | 15.7527 | -74.2629 | -48.7256 | 48.7256 | -700 | -700 | -699.9999
334.1829 | 0.014 | -100 | 60.014 | 60 |  |  | -779.7599 | 334.1829 | 137.6047 |  | 37.1314 | 15.2894 | -86.64 | -48.7256 | 48.7256 | -700 | -700 | -699.9998
311.904 | 0.015 | -100 | 60.015 | 60 |  |  | -935.7118 | 311.904 | 133.6731 |  | 34.656 | 14.8526 | -103.968 | -48.7256 | 48.7256 | -700 | -700 | -699.9998
292.41 | 0.016 | -100 | 60.016 | 60 |  |  | -1169.6397 | 292.41 | 129.96 |  | 32.49 | 14.44 | -129.96 | -48.7256 | 48.7256 | -700 | -700 | -699.9998
275.2094 | 0.017 | -100 | 60.017 | 60 |  |  | -1559.5195 | 275.2094 | 126.4476 |  | 30.5788 | 14.0497 | -173.28 | -48.7256 | 48.7256 | -700 | -700 | -699.9997
259.92 | 0.018 | -100 | 60.018 | 60 |  |  | -2339.2788 | 259.92 | 123.12 |  | 28.88 | 13.68 | -259.92 | -48.7256 | 48.7256 | -700 | -700 | -699.9995
246.24 | 0.019 | -100 | 60.019 | 60 |  |  | -4678.5553 | 246.24 | 119.9631 |  | 27.36 | 13.3292 | -519.84 | -48.7256 | 48.7256 | -700 | -700 | -699.9991
239.9262 | 0.0195 | -100 | 60.0195 | 60 |  |  | -9357.1013 | 239.9262 | 118.4446 |  | 26.6585 | 13.1605 | -1039.68 | -48.7256 | 48.7256 | -700 | -700 | -699.9982
235.1035 | 0.0199 | -100 | 60.0199 | 60 |  |  | -46785.1321 | 235.1035 | 117.2571 |  | 26.1226 | 13.0286 | -5198.4 | -48.7256 | 48.7256 | -700 | -700 | -699.991
233.928 | 0.02 | -100 | 60.02 | 60 |  |  |  | 233.928 | 116.964 | 4.7032e+12 | 25.992 | 12.996 | 520941373330.549 | -48.7256 | 48.7256 | -700 | -700 | -702.8282
232.7642 | 0.0201 | -100 | 60.0201 | 60 |  |  |  | 232.7642 | 116.6723 | 46785.6 | 25.8627 | 12.9636 | 5198.4 | -48.7256 | 48.7256 | -700 | -700 | -700
228.2224 | 0.0205 | -100 | 60.0205 | 60 |  |  |  | 228.2224 | 115.52 | 9357.12 | 25.358 | 12.8356 | 1039.68 | -48.7256 | 48.7256 | -700 | -700 | -700
222.7886 | 0.021 | -100 | 60.021 | 60 |  |  |  | 222.7886 | 114.1112 | 4678.56 | 24.7543 | 12.679 | 519.84 | -48.7256 | 48.7256 | -700 | -700 | -700
212.6618 | 0.022 | -100 | 60.022 | 60 |  |  |  | 212.6618 | 111.3943 | 2339.28 | 23.6291 | 12.3771 | 259.92 | -48.7256 | 48.7256 | -700 | -700 | -700
203.4157 | 0.023 | -100 | 60.023 | 60 |  |  |  | 203.4157 | 108.8037 | 1559.52 | 22.6017 | 12.0893 | 173.28 | -48.7256 | 48.7256 | -700 | -700 | -700
194.94 | 0.024 | -100 | 60.024 | 60 |  |  |  | 194.94 | 106.3309 | 1169.64 | 21.66 | 11.8145 | 129.96 | -48.7256 | 48.7256 | -700 | -700 | -700
187.1424 | 0.025 | -100 | 60.025 | 60 |  |  |  | 187.1424 | 103.968 | 935.712 | 20.7936 | 11.552 | 103.968 | -48.7256 | 48.7256 | -700 | -700 | -700
179.9446 | 0.026 | -100 | 60.026 | 60 |  |  |  | 179.9446 | 101.7078 | 779.76 | 19.9938 | 11.3009 | 86.64 | -48.7256 | 48.7256 | -700 | -700 | -700
173.28 | 0.027 | -100 | 60.027 | 60 |  |  |  | 173.28 | 99.5438 | 668.3657 | 19.2533 | 11.0604 | 74.2629 | -48.7256 | 48.7256 | -700 | -700 | -700
167.0914 | 0.028 | -100 | 60.028 | 60 |  |  |  | 167.0914 | 97.47 | 584.82 | 18.5657 | 10.83 | 64.98 | -48.7256 | 48.7256 | -700 | -700 | -700
161.3297 | 0.029 | -100 | 60.029 | 60 |  |  |  | 161.3297 | 95.4808 | 519.84 | 17.9255 | 10.609 | 57.76 | -48.7256 | 48.7256 | -700 | -700 | -700
155.952 | 0.03 | -100 | 60.03 | 60 |  |  |  | 155.952 | 93.5712 | 467.856 | 17.328 | 10.3968 | 51.984 | -48.7256 | 48.7256 | -700 | -700 | -700
150.9213 | 0.031 | -100 | 60.031 | 60 |  |  |  | 150.9213 | 91.7365 | 425.3236 | 16.769 | 10.1929 | 47.2582 | -48.7256 | 48.7256 | -700 | -700 | -700
146.205 | 0.032 | -100 | 60.032 | 60 |  |  |  | 146.205 | 89.9723 | 389.88 | 16.245 | 9.9969 | 43.32 | -48.7256 | 48.7256 | -700 | -700 | -700
141.7745 | 0.033 | -100 | 60.033 | 60 |  |  |  | 141.7745 | 88.2747 | 359.8892 | 15.7527 | 9.8083 | 39.9877 | -48.7256 | 48.7256 | -700 | -700 | -700
137.6047 | 0.034 | -100 | 60.034 | 60 |  |  |  | 137.6047 | 86.64 | 334.1829 | 15.2894 | 9.6267 | 37.1314 | -48.7256 | 48.7256 | -700 | -700 | -700
133.6731 | 0.035 | -100 | 60.035 | 60 |  |  |  | 133.6731 | 85.0647 | 311.904 | 14.8526 | 9.4516 | 34.656 | -48.7256 | 48.7256 | -700 | -700 | -700
129.96 | 0.036 | -100 | 60.036 | 60 |  |  |  | 129.96 | 83.5457 | 292.41 | 14.44 | 9.2829 | 32.49 | -48.7256 | 48.7256 | -700 | -700 | -700
126.4476 | 0.037 | -100 | 60.037 | 60 |  |  |  | 126.4476 | 82.08 | 275.2094 | 14.0497 | 9.12 | 30.5788 | -48.7256 | 48.7256 | -700 | -700 | -700
123.12 | 0.038 | -100 | 60.038 | 60 |  |  |  | 123.12 | 80.6648 | 259.92 | 13.68 | 8.9628 | 28.88 | -48.7256 | 48.7256 | -700 | -700 | -700
119.9631 | 0.039 | -100 | 60.039 | 60 |  |  |  | 119.9631 | 79.2976 | 246.24 | 13.3292 | 8.8108 | 27.36 | -48.7256 | 48.7256 | -700 | -700 | -700
116.964 | 0.04 | -100 | 60.04 | 60 |  |  |  | 116.964 | 77.976 | 233.928 | 12.996 | 8.664 | 25.992 | -48.7256 | 48.7256 | -700 | -700 | -700
114.1112 | 0.041 | -100 | 60.041 | 60 |  |  |  | 114.1112 | 76.6977 | 222.7886 | 12.679 | 8.522 | 24.7543 | -48.7256 | 48.7256 | -700 | -700 | -700
111.3943 | 0.042 | -100 | 60.042 | 60 |  |  |  | 111.3943 | 75.4606 | 212.6618 | 12.3771 | 8.3845 | 23.6291 | -48.7256 | 48.7256 | -700 | -700 | -700
108.8037 | 0.043 | -100 | 60.043 | 60 |  |  |  | 108.8037 | 74.2629 | 203.4157 | 12.0893 | 8.2514 | 22.6017 | -48.7256 | 48.7256 | -700 | -700 | -700
106.3309 | 0.044 | -100 | 60.044 | 60 |  |  |  | 106.3309 | 73.1025 | 194.94 | 11.8145 | 8.1225 | 21.66 | -48.7256 | 48.7256 | -700 | -700 | -700
103.968 | 0.045 | -100 | 60.045 | 60 |  |  |  | 103.968 | 71.9778 | 187.1424 | 11.552 | 7.9975 | 20.7936 | -48.7256 | 48.7256 | -700 | -700 | -700
101.7078 | 0.046 | -100 | 60.046 | 60 |  |  |  | 101.7078 | 70.8873 | 179.9446 | 11.3009 | 7.8764 | 19.9938 | -48.7256 | 48.7256 | -700 | -700 | -700
99.5438 | 0.047 | -100 | 60.047 | 60 |  |  |  | 99.5438 | 69.8293 | 173.28 | 11.0604 | 7.7588 | 19.2533 | -48.7256 | 48.7256 | -700 | -700 | -700
97.47 | 0.048 | -100 | 60.048 | 60 |  |  |  | 97.47 | 68.8024 | 167.0914 | 10.83 | 7.6447 | 18.5657 | -48.7256 | 48.7256 | -700 | -700 | -700
95.4808 | 0.049 | -100 | 60.049 | 60 |  |  |  | 95.4808 | 67.8052 | 161.3297 | 10.609 | 7.5339 | 17.9255 | -48.7256 | 48.7256 | -700 | -700 | -700
93.5712 | 0.05 | -100 | 60.05 | 60 |  |  |  | 93.5712 | 66.8366 | 155.952 | 10.3968 | 7.4263 | 17.328 | -48.7256 | 48.7256 | -700 | -700 | -700
91.7365 | 0.051 | -100 | 60.051 | 60 |  |  |  | 91.7365 | 65.8952 | 150.9213 | 10.1929 | 7.3217 | 16.769 | -48.7256 | 48.7256 | -700 | -700 | -700
89.9723 | 0.052 | -100 | 60.052 | 60 |  |  |  | 89.9723 | 64.98 | 146.205 | 9.9969 | 7.22 | 16.245 | -48.7256 | 48.7256 | -700 | -700 | -700
88.2747 | 0.053 | -100 | 60.053 | 60 |  |  |  | 88.2747 | 64.0899 | 141.7745 | 9.8083 | 7.1211 | 15.7527 | -48.7256 | 48.7256 | -700 | -700 | -700
86.64 | 0.054 | -100 | 60.054 | 60 |  |  |  | 86.64 | 63.2238 | 137.6047 | 9.6267 | 7.0249 | 15.2894 | -48.7256 | 48.7256 | -700 | -700 | -700
85.0647 | 0.055 | -100 | 60.055 | 60 |  |  |  | 85.0647 | 62.3808 | 133.6731 | 9.4516 | 6.9312 | 14.8526 | -48.7256 | 48.7256 | -700 | -700 | -700
83.5457 | 0.056 | -100 | 60.056 | 60 |  |  |  | 83.5457 | 61.56 | 129.96 | 9.2829 | 6.84 | 14.44 | -48.7256 | 48.7256 | -700 | -700 | -700
82.08 | 0.057 | -100 | 60.057 | 60 |  |  |  | 82.08 | 60.7605 | 126.4476 | 9.12 | 6.7512 | 14.0497 | -48.7256 | 48.7256 | -700 | -700 | -700
80.6648 | 0.058 | -100 | 60.058 | 60 |  |  |  | 80.6648 | 59.9815 | 123.12 | 8.9628 | 6.6646 | 13.68 | -48.7256 | 48.7256 | -700 | -700 | -700
79.2976 | 0.059 | -100 | 60.059 | 60 |  |  |  | 79.2976 | 59.2223 | 119.9631 | 8.8108 | 6.5803 | 13.3292 | -48.7256 | 48.7256 | -700 | -700 | -700
77.976 | 0.06 | -100 | 60.06 | 60 |  |  |  | 77.976 | 58.482 | 116.964 | 8.664 | 6.498 | 12.996 | -48.7256 | 48.7256 | -700 | -700 | -700
76.6977 | 0.061 | -100 | 60.061 | 60 |  |  |  | 76.6977 | 57.76 | 114.1112 | 8.522 | 6.4178 | 12.679 | -48.7256 | 48.7256 | -700 | -700 | -700
75.4606 | 0.062 | -100 | 60.062 | 60 |  |  |  | 75.4606 | 57.0556 | 111.3943 | 8.3845 | 6.3395 | 12.3771 | -48.7256 | 48.7256 | -700 | -700 | -700
74.2629 | 0.063 | -100 | 60.063 | 60 |  |  |  | 74.2629 | 56.3682 | 108.8037 | 8.2514 | 6.2631 | 12.0893 | -48.7256 | 48.7256 | -700 | -700 | -700
73.1025 | 0.064 | -100 | 60.064 | 60 |  |  |  | 73.1025 | 55.6971 | 106.3309 | 8.1225 | 6.1886 | 11.8145 | -48.7256 | 48.7256 | -700 | -700 | -700
71.9778 | 0.065 | -100 | 60.065 | 60 |  |  |  | 71.9778 | 55.0419 | 103.968 | 7.9975 | 6.1158 | 11.552 | -48.7256 | 48.7256 | -700 | -700 | -700
70.8873 | 0.066 | -100 | 60.066 | 60 |  |  |  | 70.8873 | 54.4019 | 101.7078 | 7.8764 | 6.0447 | 11.3009 | -48.7256 | 48.7256 | -700 | -700 | -700
69.8293 | 0.067 | -100 | 60.067 | 60 |  |  |  | 69.8293 | 53.7766 | 99.5438 | 7.7588 | 5.9752 | 11.0604 | -48.7256 | 48.7256 | -700 | -700 | -700
68.8024 | 0.068 | -100 | 60.068 | 60 |  |  |  | 68.8024 | 53.1655 | 97.47 | 7.6447 | 5.9073 | 10.83 | -48.7256 | 48.7256 | -700 | -700 | -700
67.8052 | 0.069 | -100 | 60.069 | 60 |  |  |  | 67.8052 | 52.5681 | 95.4808 | 7.5339 | 5.8409 | 10.609 | -48.7256 | 48.7256 | -700 | -700 | -700
66.8366 | 0.07 | -100 | 60.07 | 60 |  |  |  | 66.8366 | 51.984 | 93.5712 | 7.4263 | 5.776 | 10.3968 | -48.7256 | 48.7256 | -700 | -700 | -700
65.8952 | 0.071 | -100 | 60.071 | 60 |  |  |  | 65.8952 | 51.4127 | 91.7365 | 7.3217 | 5.7125 | 10.1929 | -48.7256 | 48.7256 | -700 | -700 | -700
64.98 | 0.072 | -100 | 60.072 | 60 |  |  |  | 64.98 | 50.8539 | 89.9723 | 7.22 | 5.6504 | 9.9969 | -48.7256 | 48.7256 | -700 | -700 | -700
64.0899 | 0.073 | -100 | 60.073 | 60 |  |  |  | 64.0899 | 50.3071 | 88.2747 | 7.1211 | 5.5897 | 9.8083 | -48.7256 | 48.7256 | -700 | -700 | -700
63.2238 | 0.074 | -100 | 60.074 | 60 |  |  |  | 63.2238 | 49.7719 | 86.64 | 7.0249 | 5.5302 | 9.6267 | -48.7256 | 48.7256 | -700 | -700 | -700
62.3808 | 0.075 | -100 | 60.075 | 60 |  |  |  | 62.3808 | 49.248 | 85.0647 | 6.9312 | 5.472 | 9.4516 | -48.7256 | 48.7256 | -700 | -700 | -700
61.56 | 0.076 | -100 | 60.076 | 60 |  |  |  | 61.56 | 48.735 | 83.5457 | 6.84 | 5.415 | 9.2829 | -48.7256 | 48.7256 | -700 | -700 | -700
60.7605 | 0.077 | -100 | 60.077 | 60 |  |  |  | 60.7605 | 48.2326 | 82.08 | 6.7512 | 5.3592 | 9.12 | -48.7256 | 48.7256 | -700 | -700 | -700
59.9815 | 0.078 | -100 | 60.078 | 60 |  |  |  | 59.9815 | 47.7404 | 80.6648 | 6.6646 | 5.3045 | 8.9628 | -48.7256 | 48.7256 | -700 | -700 | -700
59.2223 | 0.079 | -100 | 60.079 | 60 |  |  |  | 59.2223 | 47.2582 | 79.2976 | 6.5803 | 5.2509 | 8.8108 | -48.7256 | 48.7256 | -700 | -700 | -700
58.482 | 0.08 | -100 | 60.08 | 60 |  |  |  | 58.482 | 46.7856 | 77.976 | 6.498 | 5.1984 | 8.664 | -48.7256 | 48.7256 | -700 | -700 | -700
57.76 | 0.081 | -100 | 60.081 | 60 |  |  |  | 57.76 | 46.3224 | 76.6977 | 6.4178 | 5.1469 | 8.522 | -48.7256 | 48.7256 | -700 | -700 | -700
57.0556 | 0.082 | -100 | 60.082 | 60 |  |  |  | 57.0556 | 45.8682 | 75.4606 | 6.3395 | 5.0965 | 8.3845 | -48.7256 | 48.7256 | -700 | -700 | -700
56.3682 | 0.083 | -100 | 60.083 | 60 |  |  |  | 56.3682 | 45.4229 | 74.2629 | 6.2631 | 5.047 | 8.2514 | -48.7256 | 48.7256 | -700 | -700 | -700
55.6971 | 0.084 | -100 | 60.084 | 60 |  |  |  | 55.6971 | 44.9862 | 73.1025 | 6.1886 | 4.9985 | 8.1225 | -48.7256 | 48.7256 | -700 | -700 | -700
55.0419 | 0.085 | -100 | 60.085 | 60 |  |  |  | 55.0419 | 44.5577 | 71.9778 | 6.1158 | 4.9509 | 7.9975 | -48.7256 | 48.7256 | -700 | -700 | -700
54.4019 | 0.086 | -100 | 60.086 | 60 |  |  |  | 54.4019 | 44.1374 | 70.8873 | 6.0447 | 4.9042 | 7.8764 | -48.7256 | 48.7256 | -700 | -700 | -700
53.7766 | 0.087 | -100 | 60.087 | 60 |  |  |  | 53.7766 | 43.7249 | 69.8293 | 5.9752 | 4.8583 | 7.7588 | -48.7256 | 48.7256 | -700 | -700 | -700
53.1655 | 0.088 | -100 | 60.088 | 60 |  |  |  | 53.1655 | 43.32 | 68.8024 | 5.9073 | 4.8133 | 7.6447 | -48.7256 | 48.7256 | -700 | -700 | -700
52.5681 | 0.089 | -100 | 60.089 | 60 |  |  |  | 52.5681 | 42.9226 | 67.8052 | 5.8409 | 4.7692 | 7.5339 | -48.7256 | 48.7256 | -700 | -700 | -700
51.984 | 0.09 | -100 | 60.09 | 60 |  |  |  | 51.984 | 42.5324 | 66.8366 | 5.776 | 4.7258 | 7.4263 | -48.7256 | 48.7256 | -700 | -700 | -700
51.4127 | 0.091 | -100 | 60.091 | 60 |  |  |  | 51.4127 | 42.1492 | 65.8952 | 5.7125 | 4.6832 | 7.3217 | -48.7256 | 48.7256 | -700 | -700 | -700
50.8539 | 0.092 | -100 | 60.092 | 60 |  |  |  | 50.8539 | 41.7729 | 64.98 | 5.6504 | 4.6414 | 7.22 | -48.7256 | 48.7256 | -700 | -700 | -700
50.3071 | 0.093 | -100 | 60.093 | 60 |  |  |  | 50.3071 | 41.4032 | 64.0899 | 5.5897 | 4.6004 | 7.1211 | -48.7256 | 48.7256 | -700 | -700 | -700
49.7719 | 0.094 | -100 | 60.094 | 60 |  |  |  | 49.7719 | 41.04 | 63.2238 | 5.5302 | 4.56 | 7.0249 | -48.7256 | 48.7256 | -700 | -700 | -700
49.248 | 0.095 | -100 | 60.095 | 60 |  |  |  | 49.248 | 40.6831 | 62.3808 | 5.472 | 4.5203 | 6.9312 | -48.7256 | 48.7256 | -700 | -700 | -700
48.735 | 0.096 | -100 | 60.096 | 60 |  |  |  | 48.735 | 40.3324 | 61.56 | 5.415 | 4.4814 | 6.84 | -48.7256 | 48.7256 | -700 | -700 | -700
48.2326 | 0.097 | -100 | 60.097 | 60 |  |  |  | 48.2326 | 39.9877 | 60.7605 | 5.3592 | 4.4431 | 6.7512 | -48.7256 | 48.7256 | -700 | -700 | -700
47.7404 | 0.098 | -100 | 60.098 | 60 |  |  |  | 47.7404 | 39.6488 | 59.9815 | 5.3045 | 4.4054 | 6.6646 | -48.7256 | 48.7256 | -700 | -700 | -700
47.2582 | 0.099 | -100 | 60.099 | 60 |  |  |  | 47.2582 | 39.3156 | 59.2223 | 5.2509 | 4.3684 | 6.5803 | -48.7256 | 48.7256 | -700 | -700 | -700
46.7856 | 0.1 | -100 | 60.1 | 60 |  |  |  | 46.7856 | 38.988 | 58.482 | 5.1984 | 4.332 | 6.498 | -48.7256 | 48.7256 | -700 | -700 | -700
46.3224 | 0.101 | -100 | 60.101 | 60 |  |  |  | 46.3224 | 38.6658 | 57.76 | 5.1469 | 4.2962 | 6.4178 | -48.7256 | 48.7256 | -700 | -700 | -700
45.8682 | 0.102 | -100 | 60.102 | 60 |  |  |  | 45.8682 | 38.3489 | 57.0556 | 5.0965 | 4.261 | 6.3395 | -48.7256 | 48.7256 | -700 | -700 | -700
45.4229 | 0.103 | -100 | 60.103 | 60 |  |  |  | 45.4229 | 38.0371 | 56.3682 | 5.047 | 4.2263 | 6.2631 | -48.7256 | 48.7256 | -700 | -700 | -700
44.9862 | 0.104 | -100 | 60.104 | 60 |  |  |  | 44.9862 | 37.7303 | 55.6971 | 4.9985 | 4.1923 | 6.1886 | -48.7256 | 48.7256 | -700 | -700 | -700
44.5577 | 0.105 | -100 | 60.105 | 60 |  |  |  | 44.5577 | 37.4285 | 55.0419 | 4.9509 | 4.1587 | 6.1158 | -48.7256 | 48.7256 | -700 | -700 | -700
44.1374 | 0.106 | -100 | 60.106 | 60 |  |  |  | 44.1374 | 37.1314 | 54.4019 | 4.9042 | 4.1257 | 6.0447 | -48.7256 | 48.7256 | -700 | -700 | -700
43.7249 | 0.107 | -100 | 60.107 | 60 |  |  |  | 43.7249 | 36.8391 | 53.7766 | 4.8583 | 4.0932 | 5.9752 | -48.7256 | 48.7256 | -700 | -700 | -700
43.32 | 0.108 | -100 | 60.108 | 60 |  |  |  | 43.32 | 36.5512 | 53.1655 | 4.8133 | 4.0612 | 5.9073 | -48.7256 | 48.7256 | -700 | -700 | -700
42.9226 | 0.109 | -100 | 60.109 | 60 |  |  |  | 42.9226 | 36.2679 | 52.5681 | 4.7692 | 4.0298 | 5.8409 | -48.7256 | 48.7256 | -700 | -700 | -700
42.5324 | 0.11 | -100 | 60.11 | 60 |  |  |  | 42.5324 | 35.9889 | 51.984 | 4.7258 | 3.9988 | 5.776 | -48.7256 | 48.7256 | -700 | -700 | -700
42.1492 | 0.111 | -100 | 60.111 | 60 |  |  |  | 42.1492 | 35.7142 | 51.4127 | 4.6832 | 3.9682 | 5.7125 | -48.7256 | 48.7256 | -700 | -700 | -700
41.7729 | 0.112 | -100 | 60.112 | 60 |  |  |  | 41.7729 | 35.4436 | 50.8539 | 4.6414 | 3.9382 | 5.6504 | -48.7256 | 48.7256 | -700 | -700 | -700
41.4032 | 0.113 | -100 | 60.113 | 60 |  |  |  | 41.4032 | 35.1771 | 50.3071 | 4.6004 | 3.9086 | 5.5897 | -48.7256 | 48.7256 | -700 | -700 | -700
41.04 | 0.114 | -100 | 60.114 | 60 |  |  |  | 41.04 | 34.9146 | 49.7719 | 4.56 | 3.8794 | 5.5302 | -48.7256 | 48.7256 | -700 | -700 | -700
40.6831 | 0.115 | -100 | 60.115 | 60 |  |  |  | 40.6831 | 34.656 | 49.248 | 4.5203 | 3.8507 | 5.472 | -48.7256 | 48.7256 | -700 | -700 | -700
40.3324 | 0.116 | -100 | 60.116 | 60 |  |  |  | 40.3324 | 34.4012 | 48.735 | 4.4814 | 3.8224 | 5.415 | -48.7256 | 48.7256 | -700 | -700 | -700
39.9877 | 0.117 | -100 | 60.117 | 60 |  |  |  | 39.9877 | 34.1501 | 48.2326 | 4.4431 | 3.7945 | 5.3592 | -48.7256 | 48.7256 | -700 | -700 | -700
39.6488 | 0.118 | -100 | 60.118 | 60 |  |  |  | 39.6488 | 33.9026 | 47.7404 | 4.4054 | 3.767 | 5.3045 | -48.7256 | 48.7256 | -700 | -700 | -700
39.3156 | 0.119 | -100 | 60.119 | 60 |  |  |  | 39.3156 | 33.6587 | 47.2582 | 4.3684 | 3.7399 | 5.2509 | -48.7256 | 48.7256 | -700 | -700 | -700
38.988 | 0.12 | -100 | 60.12 | 60 |  |  |  | 38.988 | 33.4183 | 46.7856 | 4.332 | 3.7131 | 5.1984 | -48.7256 | 48.7256 | -700 | -700 | -700
38.6658 | 0.121 | -100 | 60.121 | 60 |  |  |  | 38.6658 | 33.1813 | 46.3224 | 4.2962 | 3.6868 | 5.1469 | -48.7256 | 48.7256 | -700 | -700 | -700
38.3489 | 0.122 | -100 | 60.122 | 60 |  |  |  | 38.3489 | 32.9476 | 45.8682 | 4.261 | 3.6608 | 5.0965 | -48.7256 | 48.7256 | -700 | -700 | -700
38.0371 | 0.123 | -100 | 60.123 | 60 |  |  |  | 38.0371 | 32.7172 | 45.4229 | 4.2263 | 3.6352 | 5.047 | -48.7256 | 48.7256 | -700 | -700 | -700
37.7303 | 0.124 | -100 | 60.124 | 60 |  |  |  | 37.7303 | 32.49 | 44.9862 | 4.1923 | 3.61 | 4.9985 | -48.7256 | 48.7256 | -700 | -700 | -700
37.4285 | 0.125 | -100 | 60.125 | 60 |  |  |  | 37.4285 | 32.2659 | 44.5577 | 4.1587 | 3.5851 | 4.9509 | -48.7256 | 48.7256 | -700 | -700 | -700
37.1314 | 0.126 | -100 | 60.126 | 60 |  |  |  | 37.1314 | 32.0449 | 44.1374 | 4.1257 | 3.5605 | 4.9042 | -48.7256 | 48.7256 | -700 | -700 | -700
36.8391 | 0.127 | -100 | 60.127 | 60 |  |  |  | 36.8391 | 31.8269 | 43.7249 | 4.0932 | 3.5363 | 4.8583 | -48.7256 | 48.7256 | -700 | -700 | -700
36.5512 | 0.128 | -100 | 60.128 | 60 |  |  |  | 36.5512 | 31.6119 | 43.32 | 4.0612 | 3.5124 | 4.8133 | -48.7256 | 48.7256 | -700 | -700 | -700
36.2679 | 0.129 | -100 | 60.129 | 60 |  |  |  | 36.2679 | 31.3997 | 42.9226 | 4.0298 | 3.4889 | 4.7692 | -48.7256 | 48.7256 | -700 | -700 | -700
35.9889 | 0.13 | -100 | 60.13 | 60 |  |  |  | 35.9889 | 31.1904 | 42.5324 | 3.9988 | 3.4656 | 4.7258 | -48.7256 | 48.7256 | -700 | -700 | -700
35.7142 | 0.131 | -100 | 60.131 | 60 |  |  |  | 35.7142 | 30.9838 | 42.1492 | 3.9682 | 3.4426 | 4.6832 | -48.7256 | 48.7256 | -700 | -700 | -700
35.4436 | 0.132 | -100 | 60.132 | 60 |  |  |  | 35.4436 | 30.78 | 41.7729 | 3.9382 | 3.42 | 4.6414 | -48.7256 | 48.7256 | -700 | -700 | -700
35.1771 | 0.133 | -100 | 60.133 | 60 |  |  |  | 35.1771 | 30.5788 | 41.4032 | 3.9086 | 3.3976 | 4.6004 | -48.7256 | 48.7256 | -700 | -700 | -700
34.9146 | 0.134 | -100 | 60.134 | 60 |  |  |  | 34.9146 | 30.3803 | 41.04 | 3.8794 | 3.3756 | 4.56 | -48.7256 | 48.7256 | -700 | -700 | -700
34.656 | 0.135 | -100 | 60.135 | 60 |  |  |  | 34.656 | 30.1843 | 40.6831 | 3.8507 | 3.3538 | 4.5203 | -48.7256 | 48.7256 | -700 | -700 | -700
34.4012 | 0.136 | -100 | 60.136 | 60 |  |  |  | 34.4012 | 29.9908 | 40.3324 | 3.8224 | 3.3323 | 4.4814 | -48.7256 | 48.7256 | -700 | -700 | -700
34.1501 | 0.137 | -100 | 60.137 | 60 |  |  |  | 34.1501 | 29.7997 | 39.9877 | 3.7945 | 3.3111 | 4.4431 | -48.7256 | 48.7256 | -700 | -700 | -700
33.9026 | 0.138 | -100 | 60.138 | 60 |  |  |  | 33.9026 | 29.6111 | 39.6488 | 3.767 | 3.2901 | 4.4054 | -48.7256 | 48.7256 | -700 | -700 | -700
33.6587 | 0.139 | -100 | 60.139 | 60 |  |  |  | 33.6587 | 29.4249 | 39.3156 | 3.7399 | 3.2694 | 4.3684 | -48.7256 | 48.7256 | -700 | -700 | -700
33.4183 | 0.14 | -100 | 60.14 | 60 |  |  |  | 33.4183 | 29.241 | 38.988 | 3.7131 | 3.249 | 4.332 | -48.7256 | 48.7256 | -700 | -700 | -700
33.1813 | 0.141 | -100 | 60.141 | 60 |  |  |  | 33.1813 | 29.0594 | 38.6658 | 3.6868 | 3.2288 | 4.2962 | -48.7256 | 48.7256 | -700 | -700 | -700
32.9476 | 0.142 | -100 | 60.142 | 60 |  |  |  | 32.9476 | 28.88 | 38.3489 | 3.6608 | 3.2089 | 4.261 | -48.7256 | 48.7256 | -700 | -700 | -700
32.7172 | 0.143 | -100 | 60.143 | 60 |  |  |  | 32.7172 | 28.7028 | 38.0371 | 3.6352 | 3.1892 | 4.2263 | -48.7256 | 48.7256 | -700 | -700 | -700
32.49 | 0.144 | -100 | 60.144 | 60 |  |  |  | 32.49 | 28.5278 | 37.7303 | 3.61 | 3.1698 | 4.1923 | -48.7256 | 48.7256 | -700 | -700 | -700
32.2659 | 0.145 | -100 | 60.145 | 60 |  |  |  | 32.2659 | 28.3549 | 37.4285 | 3.5851 | 3.1505 | 4.1587 | -48.7256 | 48.7256 | -700 | -700 | -700
32.0449 | 0.146 | -100 | 60.146 | 60 |  |  |  | 32.0449 | 28.1841 | 37.1314 | 3.5605 | 3.1316 | 4.1257 | -48.7256 | 48.7256 | -700 | -700 | -700
31.8269 | 0.147 | -100 | 60.147 | 60 |  |  |  | 31.8269 | 28.0153 | 36.8391 | 3.5363 | 3.1128 | 4.0932 | -48.7256 | 48.7256 | -700 | -700 | -700
31.6119 | 0.148 | -100 | 60.148 | 60 |  |  |  | 31.6119 | 27.8486 | 36.5512 | 3.5124 | 3.0943 | 4.0612 | -48.7256 | 48.7256 | -700 | -700 | -700
31.3997 | 0.149 | -100 | 60.149 | 60 |  |  |  | 31.3997 | 27.6838 | 36.2679 | 3.4889 | 3.076 | 4.0298 | -48.7256 | 48.7256 | -700 | -700 | -700
31.1904 | 0.15 | -100 | 60.15 | 60 |  |  |  | 31.1904 | 27.5209 | 35.9889 | 3.4656 | 3.0579 | 3.9988 | -48.7256 | 48.7256 | -700 | -700 | -700
30.9838 | 0.151 | -100 | 60.151 | 60 |  |  |  | 30.9838 | 27.36 | 35.7142 | 3.4426 | 3.04 | 3.9682 | -48.7256 | 48.7256 | -700 | -700 | -700
30.78 | 0.152 | -100 | 60.152 | 60 |  |  |  | 30.78 | 27.2009 | 35.4436 | 3.42 | 3.0223 | 3.9382 | -48.7256 | 48.7256 | -700 | -700 | -700
30.5788 | 0.153 | -100 | 60.153 | 60 |  |  |  | 30.5788 | 27.0437 | 35.1771 | 3.3976 | 3.0049 | 3.9086 | -48.7256 | 48.7256 | -700 | -700 | -700
30.3803 | 0.154 | -100 | 60.154 | 60 |  |  |  | 30.3803 | 26.8883 | 34.9146 | 3.3756 | 2.9876 | 3.8794 | -48.7256 | 48.7256 | -700 | -700 | -700
30.1843 | 0.155 | -100 | 60.155 | 60 |  |  |  | 30.1843 | 26.7346 | 34.656 | 3.3538 | 2.9705 | 3.8507 | -48.7256 | 48.7256 | -700 | -700 | -700
29.9908 | 0.156 | -100 | 60.156 | 60 |  |  |  | 29.9908 | 26.5827 | 34.4012 | 3.3323 | 2.9536 | 3.8224 | -48.7256 | 48.7256 | -700 | -700 | -700
29.7997 | 0.157 | -100 | 60.157 | 60 |  |  |  | 29.7997 | 26.4325 | 34.1501 | 3.3111 | 2.9369 | 3.7945 | -48.7256 | 48.7256 | -700 | -700 | -700
29.6111 | 0.158 | -100 | 60.158 | 60 |  |  |  | 29.6111 | 26.284 | 33.9026 | 3.2901 | 2.9204 | 3.767 | -48.7256 | 48.7256 | -700 | -700 | -700
29.4249 | 0.159 | -100 | 60.159 | 60 |  |  |  | 29.4249 | 26.1372 | 33.6587 | 3.2694 | 2.9041 | 3.7399 | -48.7256 | 48.7256 | -700 | -700 | -700
29.241 | 0.16 | -100 | 60.16 | 60 |  |  |  | 29.241 | 25.992 | 33.4183 | 3.249 | 2.888 | 3.7131 | -48.7256 | 48.7256 | -700 | -700 | -700
29.0594 | 0.161 | -100 | 60.161 | 60 |  |  |  | 29.0594 | 25.8484 | 33.1813 | 3.2288 | 2.872 | 3.6868 | -48.7256 | 48.7256 | -700 | -700 | -700
28.88 | 0.162 | -100 | 60.162 | 60 |  |  |  | 28.88 | 25.7064 | 32.9476 | 3.2089 | 2.8563 | 3.6608 | -48.7256 | 48.7256 | -700 | -700 | -700
28.7028 | 0.163 | -100 | 60.163 | 60 |  |  |  | 28.7028 | 25.5659 | 32.7172 | 3.1892 | 2.8407 | 3.6352 | -48.7256 | 48.7256 | -700 | -700 | -700
28.5278 | 0.164 | -100 | 60.164 | 60 |  |  |  | 28.5278 | 25.427 | 32.49 | 3.1698 | 2.8252 | 3.61 | -48.7256 | 48.7256 | -700 | -700 | -700
28.3549 | 0.165 | -100 | 60.165 | 60 |  |  |  | 28.3549 | 25.2895 | 32.2659 | 3.1505 | 2.8099 | 3.5851 | -48.7256 | 48.7256 | -700 | -700 | -700
28.1841 | 0.166 | -100 | 60.166 | 60 |  |  |  | 28.1841 | 25.1535 | 32.0449 | 3.1316 | 2.7948 | 3.5605 | -48.7256 | 48.7256 | -700 | -700 | -700
28.0153 | 0.167 | -100 | 60.167 | 60 |  |  |  | 28.0153 | 25.019 | 31.8269 | 3.1128 | 2.7799 | 3.5363 | -48.7256 | 48.7256 | -700 | -700 | -700
27.8486 | 0.168 | -100 | 60.168 | 60 |  |  |  | 27.8486 | 24.886 | 31.6119 | 3.0943 | 2.7651 | 3.5124 | -48.7256 | 48.7256 | -700 | -700 | -700
27.6838 | 0.169 | -100 | 60.169 | 60 |  |  |  | 27.6838 | 24.7543 | 31.3997 | 3.076 | 2.7505 | 3.4889 | -48.7256 | 48.7256 | -700 | -700 | -700
27.5209 | 0.17 | -100 | 60.17 | 60 |  |  |  | 27.5209 | 24.624 | 31.1904 | 3.0579 | 2.736 | 3.4656 | -48.7256 | 48.7256 | -700 | -700 | -700
27.36 | 0.171 | -100 | 60.171 | 60 |  |  |  | 27.36 | 24.4951 | 30.9838 | 3.04 | 2.7217 | 3.4426 | -48.7256 | 48.7256 | -700 | -700 | -700
27.2009 | 0.172 | -100 | 60.172 | 60 |  |  |  | 27.2009 | 24.3675 | 30.78 | 3.0223 | 2.7075 | 3.42 | -48.7256 | 48.7256 | -700 | -700 | -700
27.0437 | 0.173 | -100 | 60.173 | 60 |  |  |  | 27.0437 | 24.2412 | 30.5788 | 3.0049 | 2.6935 | 3.3976 | -48.7256 | 48.7256 | -700 | -700 | -700
26.8883 | 0.174 | -100 | 60.174 | 60 |  |  |  | 26.8883 | 24.1163 | 30.3803 | 2.9876 | 2.6796 | 3.3756 | -48.7256 | 48.7256 | -700 | -700 | -700
26.7346 | 0.175 | -100 | 60.175 | 60 |  |  |  | 26.7346 | 23.9926 | 30.1843 | 2.9705 | 2.6658 | 3.3538 | -48.7256 | 48.7256 | -700 | -700 | -700
26.5827 | 0.176 | -100 | 60.176 | 60 |  |  |  | 26.5827 | 23.8702 | 29.9908 | 2.9536 | 2.6522 | 3.3323 | -48.7256 | 48.7256 | -700 | -700 | -700
26.4325 | 0.177 | -100 | 60.177 | 60 |  |  |  | 26.4325 | 23.749 | 29.7997 | 2.9369 | 2.6388 | 3.3111 | -48.7256 | 48.7256 | -700 | -700 | -700
26.284 | 0.178 | -100 | 60.178 | 60 |  |  |  | 26.284 | 23.6291 | 29.6111 | 2.9204 | 2.6255 | 3.2901 | -48.7256 | 48.7256 | -700 | -700 | -700
26.1372 | 0.179 | -100 | 60.179 | 60 |  |  |  | 26.1372 | 23.5104 | 29.4249 | 2.9041 | 2.6123 | 3.2694 | -48.7256 | 48.7256 | -700 | -700 | -700
25.992 | 0.18 | -100 | 60.18 | 60 |  |  |  | 25.992 | 23.3928 | 29.241 | 2.888 | 2.5992 | 3.249 | -48.7256 | 48.7256 | -700 | -700 | -700
25.8484 | 0.181 | -100 | 60.181 | 60 |  |  |  | 25.8484 | 23.2764 | 29.0594 | 2.872 | 2.5863 | 3.2288 | -48.7256 | 48.7256 | -700 | -700 | -700
25.7064 | 0.182 | -100 | 60.182 | 60 |  |  |  | 25.7064 | 23.1612 | 28.88 | 2.8563 | 2.5735 | 3.2089 | -48.7256 | 48.7256 | -700 | -700 | -700
25.5659 | 0.183 | -100 | 60.183 | 60 |  |  |  | 25.5659 | 23.0471 | 28.7028 | 2.8407 | 2.5608 | 3.1892 | -48.7256 | 48.7256 | -700 | -700 | -700
25.427 | 0.184 | -100 | 60.184 | 60 |  |  |  | 25.427 | 22.9341 | 28.5278 | 2.8252 | 2.5482 | 3.1698 | -48.7256 | 48.7256 | -700 | -700 | -700
25.2895 | 0.185 | -100 | 60.185 | 60 |  |  |  | 25.2895 | 22.8222 | 28.3549 | 2.8099 | 2.5358 | 3.1505 | -48.7256 | 48.7256 | -700 | -700 | -700
25.1535 | 0.186 | -100 | 60.186 | 60 |  |  |  | 25.1535 | 22.7115 | 28.1841 | 2.7948 | 2.5235 | 3.1316 | -48.7256 | 48.7256 | -700 | -700 | -700
25.019 | 0.187 | -100 | 60.187 | 60 |  |  |  | 25.019 | 22.6017 | 28.0153 | 2.7799 | 2.5113 | 3.1128 | -48.7256 | 48.7256 | -700 | -700 | -700
24.886 | 0.188 | -100 | 60.188 | 60 |  |  |  | 24.886 | 22.4931 | 27.8486 | 2.7651 | 2.4992 | 3.0943 | -48.7256 | 48.7256 | -700 | -700 | -700
24.7543 | 0.189 | -100 | 60.189 | 60 |  |  |  | 24.7543 | 22.3855 | 27.6838 | 2.7505 | 2.4873 | 3.076 | -48.7256 | 48.7256 | -700 | -700 | -700
24.624 | 0.19 | -100 | 60.19 | 60 |  |  |  | 24.624 | 22.2789 | 27.5209 | 2.736 | 2.4754 | 3.0579 | -48.7256 | 48.7256 | -700 | -700 | -700
24.4951 | 0.191 | -100 | 60.191 | 60 |  |  |  | 24.4951 | 22.1733 | 27.36 | 2.7217 | 2.4637 | 3.04 | -48.7256 | 48.7256 | -700 | -700 | -700
24.3675 | 0.192 | -100 | 60.192 | 60 |  |  |  | 24.3675 | 22.0687 | 27.2009 | 2.7075 | 2.4521 | 3.0223 | -48.7256 | 48.7256 | -700 | -700 | -700
24.2412 | 0.193 | -100 | 60.193 | 60 |  |  |  | 24.2412 | 21.9651 | 27.0437 | 2.6935 | 2.4406 | 3.0049 | -48.7256 | 48.7256 | -700 | -700 | -700
24.1163 | 0.194 | -100 | 60.194 | 60 |  |  |  | 24.1163 | 21.8624 | 26.8883 | 2.6796 | 2.4292 | 2.9876 | -48.7256 | 48.7256 | -700 | -700 | -700
23.9926 | 0.195 | -100 | 60.195 | 60 |  |  |  | 23.9926 | 21.7607 | 26.7346 | 2.6658 | 2.4179 | 2.9705 | -48.7256 | 48.7256 | -700 | -700 | -700
23.8702 | 0.196 | -100 | 60.196 | 60 |  |  |  | 23.8702 | 21.66 | 26.5827 | 2.6522 | 2.4067 | 2.9536 | -48.7256 | 48.7256 | -700 | -700 | -700
23.749 | 0.197 | -100 | 60.197 | 60 |  |  |  | 23.749 | 21.5602 | 26.4325 | 2.6388 | 2.3956 | 2.9369 | -48.7256 | 48.7256 | -700 | -700 | -700
23.6291 | 0.198 | -100 | 60.198 | 60 |  |  |  | 23.6291 | 21.4613 | 26.284 | 2.6255 | 2.3846 | 2.9204 | -48.7256 | 48.7256 | -700 | -700 | -700
23.5104 | 0.199 | -100 | 60.199 | 60 |  |  |  | 23.5104 | 21.3633 | 26.1372 | 2.6123 | 2.3737 | 2.9041 | -48.7256 | 48.7256 | -700 | -700 | -700
23.3928 | 0.2 | -100 | 60.2 | 60 |  |  |  | 23.3928 | 21.2662 | 25.992 | 2.5992 | 2.3629 | 2.888 | -48.7256 | 48.7256 | -700 | -700 | -700

## 60
BA-01
-100
MW/0.1 Hz Frequency Bias

## 59.98
BA-01
-100
MW/0.1 Hz Frequency Bias

## 60.02
BA-01
-100
MW/0.1 Hz Frequency Bias