## PARAMETERS
WESTERN INTERCONNECTION CALCULATIONS
Balancing | Freq | 2016 Interconnection | 2016 | Western Interconnection
Authority | Bias | Bias | L10 | 0.001 x E1 | FTL_Low | FTL_High | ATL_Low | ATL_High
BA | -50 | -1636.44 | 34.4542 | 0.0228 | 59.9316 | 60.0684 | -137.8167 | 137.8167
Enter Balancing Authority Acronym in cell "A4" and its Frequency Bias setting (negative number) in cell "B4"
NOTE: Interconnection Bias and Balancing Authority Frequency Bias must be valid for the data time period.
If ATL_Low and ATL_High are not applicable, set at -9999 and 9999 respectively.
REVISION INFORMATION | EFFECTIVE DATE | COMMENTS
Workbook modified to reflect proposed implementation of the BAAL to use Scheduled Frequency. FTL for all Interconnections are to use bounds based upon 3 X Epsilon1 offset from 60 Hz. | 2013-04-01 | If ATL_Low and ATL_High are not applicable, set at -9999 and 9999 respectively.
Frequency Bias Setting Updated | 2016-04-05

## SAMPLE
BA | DATE | TIME | TIMEZONE | ACE | FREQERROR | FREQBIAS | ACTFREQ | SCHEDFREQ | AQC | FQC | CACE | ADIAdj | BAALlow | MinCtLow | BAALhigh | MinCtHigh | CPS1 | ACPS1 | ATLlow | MinCtLow2 | ATLhigh | MinCtHigh2 | LowLimitCt | HighLimitCt
BA-05 | 2004-07-01 | 23:55 | EST | -80 | -0.1 | -311 | 59.9 | 60 | 0 | 0 | -60 | 0 | -145.5032 | 0 |  | 0 | -294.8344 | -294.8344 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-01 | 23:56 | EST | -81 | -0.0975 | -311 | 59.9025 | 60 | 0 | 0 | -61 | 0 | -149.2341 | 0 |  | 0 | -288.4944 | -288.4944 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-01 | 23:57 | EST | -85 | -0.095 | -311 | 59.905 | 60 | 0 | 0 | -65 | 0 | -153.1613 | 0 |  | 0 | -299.4735 | -299.4735 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-01 | 23:58 | EST | -84.0541 | -0.0925 | -311 | 59.9075 | 60 | 0 | 0 | -64.0541 | 0 | -157.3008 | 0 |  | 0 | -280.9172 | -280.9172 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-01 | 23:59 | EST | -86.3889 | -0.09 | -311 | 59.91 | 60 | 0 | 0 | -66.3889 | 0 | -161.6702 | 0 |  | 0 | -280.9172 | -280.9172 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:00 | EST | -88.8571 | -0.0675 | -311 | 59.9125 | 59.98 | 0 | 0 | -53.8571 | 0 | -215.5603 | 0 |  | 0 | -170.9933 | -170.9933 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:01 | EST | -92 | -0.065 | -311 | 59.915 | 59.98 | 0 | 0 | -57 | 0 | -223.8511 | 0 |  | 0 | -169.8887 | -169.8887 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:02 | EST | -94.2424 | -0.0625 | -311 | 59.9175 | 59.98 | 0 | 0 | -59.2424 | 0 | -232.8051 | 0 |  | 0 | -164.3312 | -164.3312 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:03 | EST | -97.1875 | 0.03 | -311 | 60.01 | 59.98 | 0 | 0 | -62.1875 | 0 |  | 0 | 485.0107 | 0 | 380.3439 | 380.3439 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:04 | EST | -100.3226 | 0.07 | -311 | 60.05 | 59.98 | 0 | 0 | -65.3226 | 0 |  | 0 | 207.8617 | 0 | 634.3768 | 634.3768 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:05 | EST | -103.6667 | -0.055 | -311 | 59.925 | 59.98 | 0 | 0 | -68.6667 | 0 | -264.5513 | 0 |  | 0 | -152.6726 | -152.6726 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:06 | EST | -107.2414 | -0.0525 | -311 | 59.9275 | 59.98 | 0 | 0 | -72.2414 | 0 | -277.149 | 0 |  | 0 | -148.2504 | -148.2504 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:07 | EST | -111.0714 | -0.05 | -311 | 59.93 | 59.98 | 0 | 0 | -76.0714 | 0 | -291.0064 | 0 |  | 0 | -143.5123 | -143.5123 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:08 | EST | -115.1852 | -0.0475 | -311 | 59.9325 | 59.98 | 0 | 0 | -80.1852 | 0 | -306.3226 | 0 |  | 0 | -138.4232 | -138.4232 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:09 | EST | -119.6154 | -0.045 | -311 | 59.935 | 59.98 | 0 | 0 | -84.6154 | 0 | -323.3405 | 0 |  | 0 | -132.9427 | -132.9427 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:10 | EST | -124.4 | -0.0425 | -311 | 59.9375 | 59.98 | 0 | 0 | -89.4 | 0 | -342.3605 | 0 |  | 0 | -127.0237 | -127.0237 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
BA-05 | 2004-07-02 | 0:11 | EST | -129.5833 | -0.04 | -311 | 59.94 | 59.98 | 0 | 0 | -94.5833 | 0 | -363.758 | 0 |  | 0 | -120.6115 | -120.6115 | -137.8167 | 0 | 137.8167 | 0 | 0 | 0
| INSERT DATA FOR THESE FIELDS FOR ALL CLOCK-MINUTES FOR THE MONTH | [12 empty] | COPY THESE CELLS DOWN FOR ALL CLOCK-MINUTES
Note on E1: Clock-Minute average of ACE used for NERC CPS1. Sometimes referred to as "NERC ACE"
Note on L1: Clock-Minute average of Control ACE per BAL-004-WECC-01
Note on M1: Clock-Minute average of the Pseudo-Tie included in ACE for ACE Diversity Interchange (ADI), otherwise 0.

## DISCLAIMER
DISCLAIMER:
THE USE OF THIS BAAL WORKBOOK IS PROVIDED FREE OF CHARGE AND NEITHER DUKE ENERGY CORPORATION, NOR ITS SUBSIDIARIES, AFFILIATES, EMPLOYEES OR AGENTS MAKE ANY CLAIMS, PROMISES OR GUARANTEES ABOUT THE ACCURACY, COMPLETENESS, OR ADEQUACY OF THE RESULTS OBTAINED THROUGH THE USE THEREOF AND HEREBY DISCLAIMS ANY RESPONSIBILITY OR LIABILITY WHATSOEVER FOR ANY ERRORS, OMISSIONS, OR DISCREPANCIES IN ANY SUCH RESULTS OR IN ANY WAY ASSOCIATED WITH THE USE OF THIS BAAL WORKBOOK. BY USING THE BAAL WORKBOOK THE USER AGREES TO THE TERMS OF THE DISCLAIMER AND WILL NOT HOLD DUKE ENERGY CORPORATION, ITS SUBSIDIARIES, AFFILIATES, EMPLOYEES OR AGENTS LIABLE FOR ANY ERRORS , OMISSIONS, OR DISCREPANCIES IN ANY WAY ASSOCIATED WITH THE USE OF THIS BAAL WORKBOOK.