# Attachment A

# BAL-003-1 Frequency Response & Frequency Bias Setting Standard

# Background Document

# Introduction

This draft document provides background to explain the requirements in the draft Frequency Response Standard (BAL-003-1).  This document will evolve on the basis of Industry comments on the standard and is expected to become Attachment A to the standard.

# Requirement 1

R1.  Each Balancing Authority shall achieve a Frequency Response Measure (FRM) (as calculated on BAL-003 – FRS Form 1) that is equal to or more negative than its Frequency Response Obligation.

## Frequency Bias Setting vs. Frequency Response

The Frequency Response Measure (FRM) for the upcoming year is based on the same data collected for the Balancing Authorities’ annual Frequency Bias Setting calculation.  A final listing of official events to be used in the calculation will be available from NERC by December 10 each year.  Once a list is distributed to Balancing Authorities, each BA has one month to assemble its data and calculate the FRM.

The ERO will use the following criteria for the selection of events to be analyzed.

- At least 25 events will be used for the calculation of FRM. If a year occurs in which there are not 25 events that meet the following criteria, then the most recent 25 events (as defined below) will be used for determination of an entity’s compliance with the FRM requirement and storage of SEFRD.

- Two limits will be used to determine if a frequency event has occurred for the purposes of determining FRM:

  - The time from the start of the rapid change in frequency to the settling frequency (Point B) must not exceed 18 seconds.

  - The frequency at the arresting frequency (Point C) must exceed the frequency deviation threshold specified for the Interconnection. (As of 2010, the governor deadband setting for the Eastern and Western Interconnections will be assumed to be near or greater than 36 mHz, although there is no stated requirement defined in NERC standards).  The Point C value is the minimum of frequency samples within 8 seconds after the start of the rapid change in frequency.

- Typically, the Point A frequency should be relatively steady and near 60.000 Hz. Point A is computed as an average over the period from -16 seconds to 0 seconds before initial frequency decline.

- Typically, the frequency at Point B should be trending flat or upward, but not downward, for the event to be included in the list of events.

- Events occurring during periods in which either significant interchange schedule ramping or load ramping is likely, should be excluded if other events are available for measurement purposes.

Frequency Response survey for interconnection analysis - The ERO, has the discretion to request a frequency survey for events that differ significantly from criteria 3, 4, or 5.  These events will not be included on FRS Form 1 for calculation of frequency response.

The report will be done via FRS Form 1.

Sliding of the reporting deadline from that found in previous versions of BAL-003 is due to the increased number of samples required and is intended to avoid burdening NERC and the Balancing Authorities with working over holiday periods for no added value to reliability.

Frequency Bias Settings and acceptable Frequency Response are negative numbers by definition.  In other words, as frequency drops, the Balancing Authority is expected to contribute MWs to the Interconnection (or take fewer MWs in).

The current BAL-003 has a minimum Frequency Bias Setting (in MW/0.1Hz) that is in absolute terms equal to 1% of the Balancing Authority’s projected peak.  An early researcher noted that the ideal state is where the Frequency Bias Setting is exactly equal to natural Frequency Response.  Researchers have also noted that over-bias is preferable to under-bias.   The current –(1% of peak) /0.1Hz floor for the Frequency Bias Setting is significantly more negative than most Balancing Authorities’ natural Frequency Response.  This can lead to over-control , particularly in the Eastern Interconnection, and  force the  industry to require too much secondary control resulting in degraded performance and increased operating cost compared to requiring an appropriate balance of primary and secondary control.

Changes to the Frequency Bias Setting that move it closer to the natural Frequency Response will improve the quality and accuracy of ACE and all ACE based systems and measures, including: the CERTS Automatic Frequency Events Identification and Frequency Response Evaluation System; the CPS1 measure; the CPS2 measure; the DCS measure; the BAAL measure; and, AGC Systems in general.

### Frequency Bias Setting Floor

The FR SDT is proposing a gradual transition to bring Frequency Bias Settings and natural Frequency Response closer.  The Frequency Response Standard Field Trial Document describes the gradual replacement of a floor by natural Frequency Response for Frequency Bias Setting.

### Frequency Response Obligation and Allocation

The SDT is initially proposing that the Interconnection Frequency Response Obligation (FRO) be a discretely administered determination, but it is evaluating a risk-based determination.

For the administered approach each Interconnection will have a target contingency protection criteria based on the largest category C event (N-2).  The protection criteria will assure that Point C will not encroach on the first step UFLS.

Under development – The SDT is evaluating a risk based approach to establish an Interconnection Frequency Response Obligation which can be based on a probability function.

The ERO and the NERC RS will manage the administrative procedure to assign an FRO to each BA for the upcoming year.

Each Balancing Authority will receive a proportional slice of the Interconnection’s Frequency Response Obligation based on (peak generation + peak load)/2.   The reasoning for this allocation method is that Balancing Authorities carry differing proportions of load and generation.  In fact, some Balancing Authorities have only load with no native generation, while others have only generation with no native load.  One of the reasons for using 2010 event data as part of a field trial of the standard is to evaluate the allocation methodology.

### Methods of Obtaining Response

There are two reasons for the option of meeting compliance by participation in a Reserve Sharing Group (RSG).  First, although spinning reserve is not a part of this standard it should be noted that RSGs typically define the amount of spinning reserve carried by Balancing Authorities.  The second reason is to address the FERC Order No. 693 directive to define methods of obtaining frequency response.

As long as all BAs within the RSG use the same events for calculating FRM, BAs within the RSG may allocate a portion of their FRM to another RSG participant.

The SDT is soliciting comments on methods of obtaining Frequency Response to meet the Order 693 directive (markets, incentive programs, tariff changes, interconnection agreements, innovative technology, resource standard).

## Measure and Compliance Information

M1. The Balancing Authority shall retain its FRS Form 1 to document that its Frequency Response Measure is equal to or more negative than its assigned Frequency Response Obligation as posted on the Frequency Bias Setting Report for the applicable period.

A Balancing Authority may elect to fulfill its Frequency Response Obligation by participating as a member of a Reserve Sharing Group.

# Requirement 2

R2.  Each Balancing Authority shall implement its current year Frequency Bias Setting as directed by the ERO.

## Background and Rationale

The traditional process for implementing new Frequency Bias Settings is for Balancing Authorities to submit their upcoming annual Frequency Bias Setting value by January 1.  NERC and the Resources Subcommittee validate Frequency Bias Setting values, perform error checking and use these values to calculate L10 values for CPS2.  Once the L10 values are validated, NERC posts the L10 values and sends a letter to Balancing Authorities giving a date on which to implement the new Frequency Bias Settings.  This data collection and validation process can take up to two months.  It is expected NERC will send out the L10 and Frequency Bias Setting notification generally in February for March 1 implementation.

## Measure and Compliance Information

M2. The Balancing Authority shall show that it implemented in its EMS its current year Frequency Bias Setting as directed by the ERO in accordance with Requirement R2.  Balancing Authorities with a variable Frequency Bias Setting shall have a 12 month average Frequency Bias Setting equal to or more negative than their Frequency Response Obligation.

In general the annual implementation of Frequency Bias Settings will occur on February 1 or March 1 as directed by NERC.  The dates may change to meet the needs of the Interconnection.  Implementation dates vary due to the time needed to validate reported Frequency Bias Settings and to calculate and validate CPS L10 and FRO limits.

There may be an occasional need for NERC to implement new CPS L10 and FRO limits during the year.  The most likely reasons are Balancing Authority boundary changes or decommissioning.  Balancing Authorities requesting a mid-year change to Frequency Bias Settings for these reasons should send their request to balancing@nerc.com.

NERC will notify all affected Balancing Authorities of new mid-year changes to Frequency Bias Settings and CPS L10 and FRO limits.  For any directed changes of Frequency Bias Settings, NERC will provide at least 10 days advance notification.

# Requirement 3

R3.  Each Balancing Authority shall operate its Automatic Generation Control (AGC) on Tie Line Bias, unless such operation is adverse to the Balancing Authority’s system reliability.

## Background and Rationale

This requirement has existed in NERC Policy 1 and BAL-003 for years.  Operating out of Tie Line Bias control can lead to uncoordinated control that may result in unreliable operations.

## Measure and Compliance Information

M3.  The Balancing Authority’s AGC was found to be operating in Tie Line Bias control.

Note:  Calculated ACE for a single Balancing Authority Interconnection operating under Tie Line Bias is the same as under Flat Frequency Control.  Either mode of operation is acceptable for a single Balancing Authority Interconnection.

Cohn, Nathan. Control of Generation and Power Flow on Interconnected Systems. (New York: John Wiley & Sons, 1966)