Standard Development Roadmap

This section is maintained by the drafting team during the development of the standard and will be removed when the standard becomes effective.

Development Steps Completed:

SAR authorized by Standards Committee for development as a reliability standard July 12, 2007.

Standard Drafting Team appointed by Standards Committee September 11, 2007.

Proposed Action Plan and Description of Current Draft:

This is the second draft of the proposed standard and includes requirements with violation risk factors, time horizons and measures; and Violation Severity Levels.   This second posting of the standard is for a 45-day comment period and ballot from July 31through September 15, 2010.

Future Development Plan:

| Anticipated Actions | Anticipated Date |
| --- | --- |
| - Post response to comments and second version of standard for comment and ballot. | July 2010 |
| - Post response to comments and conduct recirculation ballot. | October 2010 |
| - BOT adoption. | November 2010 |
| - File with regulatory authorities. | December 2010 |

# Definitions of Terms Used in Standard

This section includes all newly defined or revised terms used in the proposed standard.  Terms already defined in the Reliability Standards Glossary of Terms are not repeated here.  New or revised definitions listed below become approved when the proposed standard is approved.  When the standard becomes effective, these defined terms will be removed from the individual standard and added to the Glossary.

- Frequency Excursion – an exceedance of system frequency beyond a continuous operating band; 60±0.5 Hertz.

Voltage Excursion – an exceedance of system voltage beyond a continuous operating band; ±5% of scheduled voltage.

Exhibit A

Notes from December 11, 2008 Meeting with FERC Staff

Generator Verification SDT January 6-8, 2009 Meeting Notes

Introduction

Title:	Generator Performance During Frequency and Voltage Excursions

Number:	PRC-024-1

Purpose:	Ensure generating units remain connected during frequency and voltage excursions and ensure expected generating unit performance during frequency and voltage excursions is communicated to Reliability Coordinators, Planning Coordinators, Transmission Operators and Transmission Planners for accurate system modeling.

Applicability

  - Functional entities:

- Generator Owner

Effective Dates: The standard is effective the first day of the first calendar quarter after applicable regulatory approvals (or the standard otherwise becomes effective the first day of the first calendar quarter after NERC Board of Trustees adoption in those jurisdictions where regulatory approval is not required).

- Each Generator Owner’s applicable unit(s) shall be compliant with the standard based on the following phased implementation schedule:

  - No less than 33% of a Generator Owner’s units shall be fully compliant with the standard within 1 year of the effective date of the standard.

  - No less than 66% of a Generator Owner’s units shall be fully compliant with the standard within 2 years of the effective date of the standard.

  - No less than 100% of a Generator Owner’s units shall be fully compliant with the standard within 3 years of the effective date of the standard.

Requirements

Each Generator Owner that has frequency protective relaying activated to trip its new or existing generating unit shall set such protective relaying not to trip per the following operating conditions and relay settings unless the Generator Owner has documented and communicated a non-protection system equipment limitation in accordance with Requirement R3 for an existing generating unit:

- (Violation Risk Factors: Medium ) (Time Horizon – Operations Planning)

  - When operating within a frequency range of 59.5 Hz to 60.5 Hz, inclusive.

  - During the off-nominal frequency excursions specified in PRC-024-1 Attachment 1.

  - By instantaneous  underfrequency relays set at a frequency higher than 57.8 Hz.

  - By instantaneous overfrequency relays set at a frequency lower than 62.2 Hz.

  - When the transmission system frequency rate of change is less than 2.5 Hz/second with a total change of up to 1.0 Hz

Each Generator Owner that has voltage protective relaying activated to trip its new or existing unit or generating plant/facility shall set its protective relaying not to trip as a result of a voltage excursion at the point of interconnection, caused by an event external to the plant per the following operating conditions and relay settings unless the Generator Owner has documented and communicated a non-protection system equipment limitation in accordance with Requirement R3 for an existing unit or generating plant/facility:

- (Violation Risk Factors: Medium )  (Time Horizon – Operations Planning)

  - When operating within 95% to 105% of rated generator terminal voltage and during the transmission system operating conditions as defined in PRC-024-1 Attachment 2, with the following clarifications:

    - For three-phase transmission system zone 1 faults with Normal Clearing, set voltage relays based on actual fault clearing times, not to exceed 9 cycles.

    - If a Transmission Planner’s study (based on the location specific voltage recovery characteristics) recommends less stringent voltage relay settings than those in PRC-024-Attachment 2, set voltage relays either to the Transmission Planner’s settings or the settings in PRC-024-Attachment 2.

    - If a Special Protection System (SPS) or Remedial Action Scheme (RAS) includes tripping a generator after fault initiation, then the SPS or RAS relays may be set to trip the generator even if in the “no trip zone” in PRC-024-Attachment 2.

    - If clearing a system fault necessitates disconnecting a generator, then relays may be set to trip the generator even if in the “no trip zone” in PRC-024-Attachment 2.

Each Generator Owner of an existing generating unit or generating plant/facility shall document any non-protection system equipment limitation that prevents compliance with Requirement R1 or R2 and communicate the documented limitation to its Reliability Coordinator, Planning Coordinator, Transmission Operator and Transmission Planner within 30 days of identifying the limitation to ensure the accuracy of planning studies and system modeling studies.  (Violation Risk Factor – Lower) (Time Horizon – Operations Planning)

  - Each Generator Owner shall provide a written response to the commenting entity within 90 calendar days of receipt of written comments from a Reliability Coordinator, Planning Coordinator, Transmission Operator or Transmission Planner regarding an equipment limitation.

- The equipment limitation expires coincident with either of the following conditions:

    - The equipment causing the limitation is repaired or replaced with equipment that removes the limitation

    - The existing generating unit increases the nameplate capacity rating greater than 10%.

Each Generator Owner of an existing unit or generating plant/facility shall provide an estimate of that unit’s performance during Frequency/Voltage Excursions to the requesting entity (Reliability Coordinators, Planning Coordinators, Transmission Operators and Transmission Planners that monitor or model the associated unit) within 30 days of a written request to ensure the accuracy of planning studies and system modeling studies.  The documentation shall include: (Violation Risk Factors: Medium)  (Time Horizon – Operations Planning)

  - An estimate of the time duration the existing unit or generating plant/facility will remain connected as a result of a Frequency/Voltage Excursion similar to the curves in PRC-024-Attachments 1 and 2.

  - An estimated/approximate probability in 25% increments that the existing unit or generating plant/facility will remain connected during Frequency/Voltage Excursions similar to the curves in PRC-024-Attachments 1 and 2.

  - Identification of whether the existing unit or generating plant/facility estimates were developed based on experience, actual event histories, sound engineering judgment, or other applicable information.

Each Generator Owner shall keep its new unit or new generating plant/facility connected following a Frequency Excursion or Voltage Excursion at the Point of Interconnection, caused by an event external to the plant, within the parameters set forth in PRC-024-Attachment 1 and Attachment 2 and in accordance with the following conditions and exceptions:

- (Violation Risk Factor: Medium) (Time Horizon – Real-Time)

  - When the unit or generating plant/facility is operating at or above the minimum sustainable generation.

    - For a generating plant/facility consisting of multiple units with total generation > 75 MVA (gross aggregate nameplate rating), when the facility is producing at least 20% of the facility’s rated capacity and the voltage support equipment is in service.

  - For a new generating plant/facility consisting of multiple units less than 20 MVA each with total facility generation > 75 MVA (gross aggregate nameplate rating), at least 90% of the individual generating units shall remain connected.

  - A unit or generating plant/facility may operate to a less stringent voltage ride-through performance criterion than the duration curve based on the location specific voltage recovery characteristics as specified by the Transmission Planner.

  - A unit or generating plant/facility may trip if this action is designed as part of a Special Protection System (SPS) or Remedial Action Scheme (RAS).

  - A unit or generating plant/facility may trip if clearing a system fault necessitates disconnecting the unit or generating plant/facility.

  - A unit or generating plant/facility may trip if the Generator Owner has a temporary exemption granted by its Reliability Coordinator based on a documented equipment limitation.

  - A unit or generating plant/facility may trip due to loss of synchronism or impending loss of synchronism.

Each Generator Owner shall provide to the Reliability Coordinators, Planning Coordinators, Transmission Operators and Transmission Planners (that monitor or model the associated unit) its generator protection trip settings as specified by Requirements R1 and R2, and documented equipment limitations as specified by Requirement R3 within 30 calendar days of any change to those trip settings or limitations, and shall provide the requesting entity the trip settings or limitations within 30 calendar days of a written request for the data to ensure the accuracy of planning studies and system modeling studies.  (Violation Risk Factor – Lower) (Time Horizon – Operations Planning)

Measures

Each Generator Owner has evidence such as setting sheets, calibration sheets, or other documentation, that generator frequency protective relays have been set in accordance with Requirement R1.  Each Generator Owner of an existing generating unit that is unable to comply with Requirement R1 due to equipment limitations (Protection System excluded) has evidence or other documentation that explains the equipment limitation of the unit(s).

Each Generator Owner has evidence such as setting sheets, voltage-time curves, calibration sheets, coordination plots or dynamic simulation studies, that generator voltage protective relays have been set in accordance with Requirement R2.  Each Generator Owner of an existing generating unit that is unable to comply with Requirement R2 due to equipment limitations (Protection System excluded) has evidence or other documentation that explains the equipment limitation of the unit(s).

Each Generator Owner has evidence that it has documented and communicated any equipment limitation(s) that resulted in an exception to Requirements R1 or R2 in accordance with Requirement R3 such as a dated email or letter that contain such documentation as study results, experience from an actual event, or manufacturers’ advisory.

Each Generator Owner has evidence such as dated e-mails, mail receipts or other documentation that an estimate(s) of the performance of its existing generating unit(s) as a result of Frequency/Voltage Excursions has been communicated in accordance with Requirement R4.

Each Generator Owner has evidence such as unit output records, trip investigation reports or disturbance monitoring records that its new generating units/facilities did not trip during a Frequency/Voltage Excursion in accordance with Requirement R5.

Each Generator Owner has evidence such as dated e-mails, mail receipts or other evidence that it communicated generator protective relay settings or equipment limitations to a requesting entity within 30 calendar days of a request or change in setting(s) in accordance with Requirement R6.

- Compliance

1.	Compliance Monitoring Process

    - Compliance Enforcement Authority

- Regional Entity

    - Compliance Monitoring and Enforcement Processes:

- Compliance Audits

- Self-Certifications

- Spot Checking

- Compliance Violation Investigations

- Self-Reporting

- Complaints

    - Data Retention

- The Generator Owner shall keep data or evidence to show compliance as identified below unless directed by its Compliance Enforcement Authority to retain specific evidence for a longer period of time as part of an investigation:

      - The Generator Owner shall retain and have always available, its current, in force document(s) for Requirements R1 through R4 and Measures M1 through M4.

      - The Generator Owner shall retain the documentation since the last compliance audit for Requirements R5 and R6 and Measures M5 and M6.

      - If a Generator Owner is found non-compliant, it shall keep information related to the non-compliance until found compliant or for the duration specified above, whichever is longer.

      - The Compliance Enforcement Authority shall keep the last audit records and all requested and submitted subsequent audit records.

2.	Additional Compliance Information

None

- 3.	Violation Severity Levels

| - R# | - Violation Risk Factor | - Violation Severity Level |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | - Lower | - Moderate | - High | - Severe |
| - R1 | - Medium | - N/A | - N/A | - N/A | - A Generator Owner’s under or over frequency relaying is set to operate outside the parameters in R1 and PRC-024-Attachment 1 without a documented equipment limitation for the setting as described in R3. |
| - R2 | - Medium | - N/A | - N/A | - N/A | - A Generator Owner’s voltage relaying is set to operate outside the parameters in R2 and PRC-024-Attachment 2 without a documented equipment limitation for the setting as described in R3. |
| - R3 | - Lower | - The Generator Owner provided a written response to written comments provided by the Reliability Coordinator, Planning Coordinator, Transmission Operator, or Transmission Planner regarding a request for exception to the requirements of R1 and R2 more than 90 days but within 180 days after receipt of the written comments.(R3, Part 3.1) | - The Generator Owner communicated the documented limitation to its RC, PC, TOP and TP more than 30 days but within 60 days of identifying a limitation.(R3) | - The Generator Owner did not provide a written response to written comments provided by the Reliability Coordinator, Planning Coordinator, Transmission Operator, or Transmission Planner within 180 days from the date it was requested regarding a request for exception to the requirements of R1 and R2. (R3, Part 3.1) | - The Generator Owner did not communicate the documented limitation to its RC, PC, TOP and TP within 60 days of identifying a limitation. (R3) |
| - R4 | - Medium | - The Generator Owner supplied the information on estimated generator performance during excursions to the requesting entities more than 30 days but within 45 days from the date it was requested. | - The Generator Owner supplied the information on estimated generator performance during excursions to the requesting entities more than 45 days but within 60 days from the date it was requested. | - The Generator Owner supplied the information on estimated generator performance during excursions to the requesting entities more than 60 days but within 75 days from the date it was requested. | - The Generator Owner did not supply the information on estimated generator performance during excursions to the requesting entities within 75 days from the date it was requested. |
| - R5 | - Medium | - N/A | - A Generator Owner’s generating unit or generating plant/facility tripped off line after 20 seconds of the start of a Voltage Excursion within the No Trip Zone of Attachment 2 in accordance with R5. | - A Generator Owner’s generating unit or generating plant/facility tripped off line after the first 4 seconds and within 20 seconds of the start of a Voltage Excursion within the No Trip Zone of Attachment 2 in accordance with R5. - OR - A Generator Owner’s generating unit or generating plant/facility tripped off line due to a high Frequency Excursion within the No Trip Zone of Attachment 1 in accordance with R5. | - A Generator Owner’s generating unit or generating plant/facility tripped off line during the first 4 seconds of the start of a Voltage Excursion within the No Trip Zone of Attachment 2 in accordance with R5. - OR - A Generator Owner’s generating unit or generating plant/facility tripped off line due to a low Frequency Excursion within the No Trip Zone of Attachment 1 in accordance with R5. |
| - R6 | - Lower | - The Generator Owner supplied the information required in R6 more than 30 but within 45 days from the time of the change. | - The Generator Owner supplied the information required in R6 more than 45 but within 60 days from the time of the change. | - The Generator Owner supplied the information required in R6 more than 60 but within 75 days from the time of the change. | - The Generator Owner failed to supply the information required in R6 within 75 days from the time of the change. |

Regional Variances

- None

References

- “The Technical Justification for the New WECC Voltage Ride-Through (VRT) Standard, A White Paper Developed by the Wind Generation Task Force (WGTF),” dated June 13, 2007, a guideline approved by WECC Technical Studies Subcommittee.

PRC-024 — Attachment 1

No Trip

Zone

| Frequency (hertz) | 57.8 | 59.5 | 62.2 | 60.5 |
| --- | --- | --- | --- | --- |
| Time (seconds) | 0 to 2 | Over 1800 | 0 to 2 | Over 600 |

PRC-024— Attachment 2

The following data points apply to this curve:

| HVRT DURATION |  |  | LVRT DURATION |  |
| --- | --- | --- | --- | --- |
| Time (Sec) | Voltage (p.u.) |  | Time (Sec) | Voltage (p.u.) |
| 0.20 | 1.200 |  | 0.15 | 0.000 |
| 0.50 | 1.175 |  | 0.30 | 0.450 |
| 1.00 | 1.150 |  | 2.00 | 0.650 |
| 600 | 1.100 |  | 3.00 | 0.750 |
|  |  |  | 600 | 0.900 |

Voltage Ride-Through Curve Clarifications

- The per unit voltage base for this curve is the scheduled operating voltage as measured at the point of interconnection to the Bulk Electric System.

- The curves depicted in this Attachment 2 are applicable for a three-phase transmission system zone 1 faults with Normal Clearing.

- As long as the cumulative voltage duration at the point of interconnection with the Bulk Electric System is within the voltage boundaries of the curve, the generator voltage protective relaying will not trip the generator.

- The curves depicted in this Attachment 2 assume system frequency of 60 Hertz.

- Voltage protection relay setting calculations may be based on the static case, for steady state initial conditions using the following assumptions:

  - All of the units connected to the same transformer are on line and operating,

  - All of the units are at full nameplate real-power output.

  - Power factor of 0.95 lagging.

  - Scheduled voltage as measured at point of interconnection.

- Voltage protection relay settings will be calculated to comply with Attachment 2 assuming that any additional installed generating plant reactive support equipment (such as static VAr compensators, synchronous condensers, or capacitors) is available and operating normally.

- Voltage protection relay settings will be calculated to comply with Attachment 2 accounting for the actual tap settings of transformers between the generator terminals and the POI.

Each Generator Owner is not required to have frequency or voltage protective relaying (includes frequency and voltage protective functions for discrete relays, volts per hertz relays evaluated at nominal frequency, multi-function protective devices or protective functions within excitation controls that directly trip or provide tripping signals to the generator based on frequency or voltage inputs) installed or activated on its unit.

Including generators under construction, generators with an executed interconnection agreement or Power Purchase Agreement by the effective date of this standard, or generators with an executed equipment purchase contract and scheduled delivery of major components within 2 years of the effective date of version 1 of this standard.

Excluding generators in service prior to the effective date of version 1 of this standard and excluding generators referenced in Footnote 1.