## Slide 1: Project 2007-01: Under-frequency Load Shedding Standard PRC-006-2
September 14, 2010

## Slide 2: PRC-006-1 History
SAR finalized 3/15/07
PRC-006-1 Posted for public comment:
7/02/08 – 8/15/08
4/21/09 – 5/21/09
6/11/10 – 7/16/10
Initial Ballot: 7/08/10 – 7/17/10 43.1%
Second Ballot: 7/24/10 – 8/03/10 49.6%

## Slide 3: Applicability
Planning Coordinator
  SDT would have assigned overall UFLS design and assessment responsibility to regions
  FERC Order No. 672: Requirements are applicable to users, owners or operators of the Bulk Power System.
  Planning Coordinator next best option
  Attempt to define “group of Planning Coordinators” & subsequent attempt to require them to “reach concurrence” encountered unresolvable compliance issues
  Current draft assigns overall UFLS responsibility to individual Planning Coordinators

## Slide 4: Applicability
UFLS Entities
(Transmission Owner, Distribution Provider)
  In some regions, TOs who do not have end-use load connected to them implement UFLS, not DPs
  Separate applicability assigned to TOs for “automatic switching of Elements” where “Elements” are capacitors, shunt reactors, transmission lines (R10)
  Switching of “Elements” at distribution level not considered significant to BES voltage

## Slide 5: Issues from Second Ballot
Confusion on island identification
Confusion on Attachment 1 curves
UFLS Coordination at regional level
Confusion on GO applicability & PRC-024
Desire for UFLS Entities to have input
Limit of SDT involvement in EOP-003
Event Analysis & PRC-009

## Slide 6: Issues from Second Ballot
Island identification criteria
Regional islands
  PC must have some criteria (R1), though not necessary that that criteria produce islands
  One island must be the regional footprint (R2.3) so as to preserve existing coordination of UFLS at regional level

## Slide 7: Issues from Second Ballot
Attachment 1 Performance Curves
Curves are NOT for setting UFLS relays
Curves are boundaries solely for checking the frequency trajectory in simulations (R4)
Simulations should be run until frequency settles between 60.7 and 59.3 Hz; but do not need to be run longer

## Slide 8: Issues from Second Ballot
Coordination at Regional (or Interconnection) Level
Indirectly achieved by identifying regional entity footprint (or interconnection) as an island (R2.3)
A degree of coordination among PCs then required (R5)
Desire is for PCs to work together on UFLS program design (R3), UFLS design assessment (R4), but not required
  Options to satisfy R5 now explicitly appear as R5 sub-parts

## Slide 9: Issues from Second Ballot
GO Applicability & PRC-024
PRC-006 and PRC-024 are coordinated:
Same over & underfrequency generator tripping curves
No double jeopardy for Generator Owners; PRC-006 not applicable to Generator Owners
Statement of Compliance Registry thresholds for reporting trip settings (PRC-024), modeling trip settings in UFLS design assessments (PRC-006)

## Slide 10: Issues from Second Ballot
GO Applicability & PRC-024 (continued)
- Modeling of generator trip settings not enforceable until one year after PRC-024 approved (R4.1 through R4.6)
- SDT anticipates assumption of burden by UFLS Entities for any non-conforming generators will not be significant:
  1) PRC-024 curves chosen recognizing total life-time off-nominal durations advised by major generator manufacturers
  2) Similar regional curves in existence today (though generally as guides)

## Slide 11: Issues from Second Ballot
Desire for UFLS Entities to have input
Peer review procedure established (R14)
PC’s must answer any comments sent to them by UFLS Entities before finalizing their UFLS program design & implementation schedule
Peer review procedure has precedent in:
FAC-008 R2 & R3
FAC-010 R4 & R5
FAC-011 R4 & R5
It is difficult to require agreement among entities in a standard and SDT received many comments concerned with approach; but PC’s should not impose unrealistic demands on entities they are coordinating with

## Slide 12: Issues from Second Ballot
Limited Scope EOP-003
Scope of supplemental SAR SOLELY to remove automatic UFLS from EOP-003
  Thus removing conflict between PRC-006 and EOP-003
Automatic UVLS & manual load shedding remain in EOP-003
SDT acknowledges EOP-003 needs more work
  Another drafting team assigned to fix EOP-003

## Slide 13: Issues from Second Ballot
Event analysis & PRC-009
Existing PRC-009-0 is FERC approved, to be absorbed into PRC-006-1
PRC-009-0 contains no UFLS event analysis threshold; Modifying this requirement would require justification
PRC-009-0 has a ninety day period to complete analysis; PRC-006-1 has one year

## Slide 14: WECC Variance

## Slide 15: Q&A
Questions?

## Slide 16: Please Vote Affirmative!!!!!!

## Slide 17: Issue In Previous Postings
V/Hz Monitoring (R3.3)
Sole purpose is to prevent generator tripping caused by high voltage
  In shedding large amounts of load with frequency already low, potential risk of high V/Hz at generators
Threshold values from IEEE C37.102 (?check with Phil on #?)