- Requirements related to Fault Recording

- Do you agree with the other Fault Recording requirements in R4 through R6 of this proposed standard?  If no, provide specific suggestions that would make the requirements acceptable to you.

Summary Consideration:

| Organization | Yes or No | Question 9 Comment |
| --- | --- | --- |
| Northeast Power Coordinating Council | No | Referring to Requirement 4.1, the number of phases to be monitored is excessive. It will not provide any analytical benefit. Monitoring every transmission line in a ring bus is excessive. The second bullet referring to a breaker-and-a-half arrangement needs clarification. What is the "outer bus" in that arrangement? Definitions should be provided when references are made to substation designs or equipment that could have different names or designations in the industry. As we commented in Question 5, we do not feel that the 200kV threshold is an appropriate criteria for assessing criticality, nor the single or generating plant capacity specifications. This needs to be reflected in Table 4-1.Referring to Requirement R4.2, the intent of measuring neutral current needs to be clarified, specifically with regard to transformers (see R5.3 in PRC-002-2). Referring to Requirement R5, the comments to R4.1 and R4.2 are applicable. In Table 5-1 the requirements that refer to the high side of critical GSU's should be directed at Transmission Owners, not Generation Owners. Referring to Requirement R6.1, the second bullet does not provide for the recording of adequate information (see response to Question 8). |
| Response: Monitoring of all three phases is necessary for the analysis of all fault types. Monitoring all three phases, or two phases and the residual, will provide enough data to determine all three phases and the residual. An FAQ document is being developed to clarify voltage monitoring requirements on ring busses and breaker-and-a-half arrangements. The standard is also being revised to more clearly indicate what equipment each G. O. and T. O. must monitor. The standard was written to allow for the use of legacy equipment and protective relays. Newer and older DFRs and protective relays have differing capabilities, and it is very likely that information for the same event will be recorded at multiple locations. The SDT believes that in all but the most unusual circumstances that adequate information will be available to analyze an event. |  |  |
| IRC Standards Review Committee | No | The SRC agrees with the data itself. The SRC does not agree that each data item listed in R4 must be an independent requirement. The SRC supports compliance with R4, but that the suggested sub-requirements be bullet items and that those items be handled through VSLs. Similarly with R5, the data items should be bulleted rather than being shown as independent. Similarly with R6, the data items should be bulleted rather than being shown as independent. |
| Response: The SDT is revising the standard and will take your suggestions into consideration. |  |  |
| SPP System Protection and Control Working Group | Yes |  |
| Members of the WECC Disturbance Monitoring Work Group | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing the location criteria. See our answer to question 7 above. |  |  |
| Southern Company - Transmission | Yes | No further comment. |
| SERC Engineering Committee Planning Standards Subcommittee |  |  |
| SERC Protection and Controls Sub-committee | Yes | Re-label heading of Table 4-1 to indicate: for substation equipment owned by Transmission Owner? |
| Response: The SDT is revising the standard and table 4.1 will be relabeled to indicate that it is for T. O. owned equipment. |  |  |
| PacifiCorp |  |  |
| Dominion | Yes | Re-label heading of table 4-1 to indicate:" for substation equipment owned by Transmission Owner" |
| Response: The SDT is revising the standard and table 4.1 will be relabeled to indicate that it is for T. O. owned equipment. |  |  |
| Bonneville Power Administration | No | BPA does not believe the individual phase voltage of each line is required if Bus voltage at the station is recorded. We think the R4.1 may say that, but maybe change the wording order to "The three phase to neutral voltages on each main bus or monitored line as follows:", It shouldn't be required to monitor the voltages on a transfer bus in a main and auxiliary (transfer) bus scheme. The number of element criteria may be too stringent, change to 5 elements. |
| Response: The recording of every line and bus voltage is not explicitly stated. What is stated is that the voltages must be able to be determined. As long as an adequate number of voltages are recorded, such as every other bus or line on a ring bus, and circuit breaker position is known, all voltages can be determined. How an individual company chooses to comply with the requirements may vary from one G. O. or T.O. to the next. The SDT is reviewing the FR location requirements. |  |  |
| FirstEnergy | Yes |  |
| Florida Power & Light | Yes |  |
| Los Angeles Department of Water & Power |  |  |
| MRO NERC Standards Review Subcommittee | Yes | Table 5-1 has a type-o - Row 2, Column 2, bullet 1 extra 'd'. |
| Response: Thank you. This has been corrected. |  |  |
| PG&E System Protection | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing the location requirements. See the answer to question 7 above. |  |  |
| US Bureau of Reclamation | Yes |  |
| NERC | No | R4.1 It is important for forensic analysis to have both bus and line quantities for DFR quantities. Bullets 2 and 3 should read: On breaker-and-a-half arrangements, the outer bus voltages, and the individual line voltages. On straight buses, common bus voltages and the individual line voltages. |
| Response: There are multiple ways to determine every line and every bus voltage. If the two sets of bus voltages in a breaker-and-a-half scheme are recorded, and the status of every circuit breaker is known, all bus and line voltages can be determined. |  |  |
| TransAlta |  |  |
| Grant County PUD | Yes |  |
| NYISO | No | R4.1 requires monitoring of 3 phase voltages on all bus sections of ring buses. We believe this is excessive. Reduce requirements to enough to be able derive all the quantities during normal maintenance conditions (outages).R5.5, second row in table: This puts the responsibility to monitor a transmission substation on the generator owner. Change the requirement such that the substation owner needs to monitor this. |
| Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to determine all voltages without recording every line or bus individually. The SDT is revising the standard to more clearly differentiate G.O. and T. O. monitoring requirements. |  |  |
| Tri-State Generation and Transmission Association | No | The R4.1 and R5.4 ring bus requirements to monitor three-phase voltages on each transmission line seems unnecessary for reliability or for post-event analysis. Voltages from opposite locations on a ring bus should ensure that sufficient quantities are available to perform any required calculations. |
| Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to determine all voltages without recording every line or bus individually. |  |  |
| Cowlitz County PUD | Yes |  |
| Portland General Electric | No | The following comments are those filed by the DMWG which we are filing in support: Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing location requirements. See our answer to question 7 above. |  |  |
| Progress Energy Florida | No | Monitoring of GSU transformer currents on units >500MVA is the correct approach. However, peaking generation locations will have many generating units of less than 500MVA. The aggregate combination of 1500MVA will encompass many GSU transformers. Monitoring of each of the GSUs' currents (even though they are >200kV) will require extensive DME equipment additions at locations remote to the transmission network where the DME equipment is (and should be) located. We believe these total aggregate generation currents should be monitored at the location where they are introduced to the transmission network. This location may be at an exit point from a generating unit bus or a transmission line the feeds the generation power into another remote transmission substation bus. |
| Response: The SDT is reviewing your suggestion. If the SOE is on the breakers the monitoring the GSU aggregate is acceptable. NOTE: The Sub team will take the lead on determining a position on GSU monitoring to incorporate into the standard and respond to this comment. If all of the generation is connected to a single transmission line, the currents and voltages at the generation end of the transmission line may be monitored since this will be the same as the total plant output. |  |  |
| Puget Sound Energy | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing location criteria. See our response to question 7 above. |  |  |
| Schneider Electric | Yes |  |
| Independent Electricity System Operator | No | Please see our comments on R6, above. |
| Response: See our response to R6 above. |  |  |
| American Electric Power | Yes |  |
| NextEra Energy Resources (formerly FPL Energy) | No | Section R4.1Recommend changing the first bullet to read On ring buses, the voltages of bus sections connected to transmission lines, or the individual line voltages. Since they are electrically the same, the SDT doe not believe it is necessary to make a distinction between these two. Section R4.2Recommend removing the word transformer from the qualifying sentence and changing the wording to The three phase currents and the residual or neutral currents of each monitored element as noted in Table 4-1. We agree. Table 4-1Recommend changing the single generating unit level to 750MVA or higher to avoid unnecessary Fault Recording Equipment installations The is being revised. Section R5.1Recommend removal of language restricting the location of where to monitor for three phase to neutral voltages or phase to phase voltages associated with the GSU. Statement should allow for monitoring at T-line level as well. We do allow for that. Section R5.2Recommend removal of language restricting the location of where to monitor for three phase to neutral voltages or phase to phase voltages associated with the GSU. Statement should allow for monitoring at T-line level as well. We do allow for that. (same comment and response as above) The SDT believes that you mean currents, not voltages, and we do allow for that. Section R5.4Recommend changing the first bullet to read On ring buses, the voltages of bus sections connected to transmission lines, or the individual line voltages. Since they are electrically the same, the SDT doe not believe it is necessary to make a distinction between these two. Section R5.5Recommend removing the word transformer from the qualifying sentence and changing the wording to The three phase currents and the residual or neutral currents of each monitored element as noted in Table 4-1. We agree. Table 5-1Recommend changing the single generating unit level to 750MVA or higher to avoid unnecessary Fault Recording Equipment installations. The is being revised. |
| Response: The standard states that line voltages must be able to be determined. Where someone may choose to record those is up to them. The standard is specifically worded to allow recording of voltages and currents on either side of a GSU. The generating size criteria is being reviewed. Note: the Sub team will draft responses to the various wording suggestions made by the commenter. |  |  |
| National Grid |  |  |
| Manitoba Hydro | Yes |  |
| Exelon Generation LLC | No | Comments on PRC-002-2---Disturbance Monitoring and Reporting Requirements Draft 1, January 30, 2009 1. Requirement R5.4: Requirements identified in this section for monitoring bus and line voltages belong to TO and not to GO unless GO owns the Substation. The revision should clearly state that.2. Requirement R5.4: We heard during the Q&A session of the webinar on 3/12/09 that GSU neutral current can be recorded by the residual current (sum of three phase currents). The revision should clearly state that. 3. Requirement R5.4: Please clarify that recording of Generator Step Up transformer (GSU) phase currents can be done by deriving these currents from the GSU output breaker(s) currents. The revision should be modified to state this and that the GSU neutral current can be recorded by deriving this current from the GSU output breaker(s) phase currents. (Most of our GSUs are connected to the switchyard thru two output breakers in a ring bus. It makes lot more sense from a schedule and cost view point to use the quantities from the CTs of these output breakers rather than from the GSU CTs. It also makes sense from reliability viewpoint as less cabling means more reliability for the equipment, especially when with less additional cabling/wiring; we are recording the required quantities.) 4. Requirement R5.5: Requirements identified in this section for monitoring line three phase currents and the residual and monitored current belong to TO and not GO unless GO owns the Substation. The revision should clearly state that. |
| Response: 1) The standard is being revised to clearly indicate what equipment each G. O and T. O. should monitor. 2 and 3) If your GSU is delta on the low side and wye on the high side, the GSU neutral current cannot be determined by summing the three phase currents on the low side. The neutral current can be determined by summing the three phase currents on the high side. The intention of the standard is to tell each G. O. and T. O. what quantities are needed, not how to record them since each entity may use a different approach that suits their needs. 4) The standard has been modified to explicitly state what equipment a G. O. and T. O. is to monitor. |  |  |
| NV Energy | Yes |  |
| DTE Energy/Detroit Edison | No | Consider change to allow high side GSU voltage to be monitored at the high side bus of the same voltage. Present wording can be taken to imply that voltage must be monitored directly at GSU high side terminals. Also, can parallel GSUs be allowed to be monitored at a common point rather than individually? Likewise, can two GSUs connected at a common point at 200 kV or above be allowed to be monitored together at the common connection point? |
| Response: The standard has been modified to indicate that either high or low side voltages and current can be recorded. As the standard is presently written, all GSU transformers must be recorded separately. |  |  |
| Wisconsin Electric | No | In R5.4 and R5.5, the Generator Owner is required to record Fault Recording data for equipment in the substation connected to a generating station of a specified capacity, in addition to that for the GSU. This appears to be an unnecessary duplication of equipment already being monitored by the Transmission Owner in R4. If this is a correct interpretation, we believe this requirement is redundant, and technically and financially unjustified. We strongly oppose requiring duplication of monitoring equipment for the same facility by both Transmission Owners and Generator Owners. Response: The standard is being revised to clearly state that a G. O. is to monitor equipment that the G. O. owns, and the T. O. is to monitor the equipment the T. O. owns. Also, In R5.2, the statement is given that the three-phase current data from the "generator bus" is sufficient for monitoring. Does this mean that the three-phase currents from generator current transformers will meet this requirement? Response: Yes, this is the intent of Requirement 5.2 |
| Response: |  |  |
| ITC Transmission, METC | Yes |  |
| City of Tallahassee (TAL) | No | R4.1, Bullet #1 appears too restrictive for a ring bus. It will require a fault recorder on each bus section with a line going to it. This is also a potential conflict with R7, which allows a recorder up to 2 busses away.Table 4-1. Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to determine all voltages without recording every line or bus individually. R7 is only for dynamic disturbance recording, not for fault recording, so there is no conflict. Your assumption is incorrect regarding transformation and number of lines. If you have three 230 kV lines, and no transformers, you meet the “three or more elements” criteria. A substation with one 230 kV line, one 500 kV line, and a 500/230 kV transformer also meets the criteria. Am I correct in assuming that if there is no transformation with both sides >200kV, I do not need recording no matter how many lines are there. No, that is incorrect. If a substation has any sum of three or more transmission lines operated at 200 kV and above, and transformers with both low and high side voltages of 200 kV and above, monitoring is required. Note: The sub-team will come up with proposed language to address the comment. Same concern with "plant" vs. "site". Response: The standard does not address sites but rather Transmission switching stations, transmission substations, generating stations, HVAC converter stations, HVDC converter stations. |
| Response: |  |  |
| PHI (PEPCO Holdings Inc.) | Yes | FR trigering requirements are not addressed. |
| Response: After a review of triggering practices among many utilities, the SDT decided to allow companies to continue to use whatever method they have found to work well for them. What works for one T. O. or G. O. may or may not work for another T.O. or G. O. R4 and R5 states that each T. O. and G. O. must have a process in place to derive fault data, and the SDT feels that to do this triggering requirements are inherently required; however the team added performance based requirements for triggering in the second draft of the standard – TEAM WILL HAVE TO COME BACK TO THIS RESPONSE ONCE THEY HAVE DECIDED WHAT TO INCLUDE IN THE STANDARD FOR TRIGGERING |  |  |
| NV Energy (fka Sierra Pacific Resources) | No | Table 4-1 should also be modified to identify Substations containing any combination of five or more elements. See response to Q7 previous. |
| Response: The SDT is reviewing the location requirements. See our answer to Q7 previous. |  |  |
| Salt River Project | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing the location requirements. See our answer to Q7 above. |  |  |
| Pacific Northwest National Laboratory |  |  |
| Progress Energy Carolina, Inc. | No | Monitoring of GSU transformer currents on units >500MVA is the correct approach. However peaking generation locations will have many generating units of less than 500MVA. The aggregate combination of 1500MVA will encompass many GSU transformers. Monitoring of each of the GSUs' currents (even though they are >200kV) will require extensive DME equipment additions at locations remote to the transmission network where the DME equipment is (and should be) located. We believe these total aggregate generation currents should be monitored at the location where they are introduced to the transmission network. This location may be at an exit point from a generating unit bus or a transmission line the feeds the generation power into another remote transmission substation bus. |
| Response: The SDT is reviewing the criteria for generator size and aggregate combination, and your comments will be used as input for this review. |  |  |
| Hydro-Québec TransEnergie (HQT) | No | Referring to Requirement 4.1, the number of phases to be monitored is excessive. It will not provide any analytical benefit. Monitoring every transmission line in a ring bus is excessive. The second bullet referring to a breaker-and-a-half arrangement needs clarification. What is the "outer bus" in that arrangement? Definitions should be provided when references are made to substation designs or equipment that could have different names or designations in the industry. As we commented in Question 5, we do not feel that the 200kV threshold is an appropriate criteria for assessing criticality, nor the single or generating plant capacity specifications. This needs to be reflected in Table 4-1.Referring to Requirement R4.2, the intent of measuring neutral current needs to be clarified, specifically with regard to transformers (see R5.3 in PRC-002-2). Referring to Requirement R5, the comments to R4.1 and R4.2 are applicable. In Table 5-1 the requirements that refer to the high side of critical GSU's should be directed at Transmission Owners, not Generation Owners. Referring to Requirement R6.1, the second bullet does not provide for the recording of adequate information (see response to Question 8). |
| Response: Monitoring of all three phases is necessary for the analysis of all fault types. Monitoring all three phases, or two phases and the residual, will provide enough data to determine all three phases and the residual. An FAQ document is being developed to clarify voltage monitoring requirements on ring busses and breaker-and-a-half arrangements. The standard is also being revised to more clearly indicate what equipment each G. O. and T. O. must monitor. The standard was written to allow for the use of legacy equipment and protective relays. Newer and older DFRs and protective relays have differing capabilities, and it is very likely that information for the same event will be recorded at multiple locations. The SDT believes that in all but the most unusual circumstances that adequate information will be available to analyze an event. |  |  |
| Brazos Electric Power Cooperative, Inc. | No | Clarify criteria and remove Tables. |
| Response: The standard is being revised to clearly state what equipment each G. O and T. O. should monitor. The SDT will continue to strive to make the criteria as clear as possible. |  |  |
| WECC |  |  |
| Entergy Services, Inc | No | R4.1 should include provisions to exclude 3 phase potential monitoring for line/bus elements employing line protection schemes, such as current differential relaying, where 3 phase potentials are not presently available and would not needed but for the requirements. Response: Adequate fault recording requires monitoring of both voltage and current. As long as those voltages can be determined in some manner, the requirements can be met without installing monitoring on every CCVT or VT. Adjacent or remote end element monitoring should be allowable for these cases. Response: Table 4.1 allows for monitoring at remote terminals. |
| Response: |  |  |
| Northeast Utilities | No | Referring to Requirement 4.1 and 5.4, monitoring the voltage every transmission line in a ring bus is excessive. Referring to Requirement R4.2, the intent of measuring neutral current needs to be clarified, specifically with regard to transformers (see R5.3 in PRC-002-2). |
| Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to determine all voltages without recording every line or bus individually. Transformer neutral currents do not necessarily need to be monitored if they can be derived from the three phase currents. Neutral currents are frequently desirable for the analysis of ground faults. |  |  |
| San Diego Gas and Electric Co. | Yes | Agree, except for the comment made in question 7 above about changing the SOE criteria from three lines to five lines. |
| Response: See answer to question 7 above. The SDT is reviewing the location requirements. |  |  |
| New York Independent System Operator | No | (R4.1) Requiring monitoring 3 phase voltages of all ring bus bus sections is excessive. Reduce requirements to enough to be able derive all the quantities during normal maintenance conditions. Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to derive all voltages without recording every line or bus individually. (R5.5, second row of table) This puts the responsibility to monitor a transmission substation on the genertator owner. The gen owner likely does not own the transmission substation. Make monitoring this equipment the responsibility or the transmission owner.(following R6.) Response: The SDT is revising the standard to clearly state that the owner of the equipment is to do the monitoring. We note that there is no mention of FR triggering. While this is specific to the various manufacturers trigger algorithms and specific also to the location, there does need to be a statement that the FR is to trigger for near-by faults, system disturbances, and relay operations. While this type of consideration is difficult to address in a standard, it would be misleading to leave out entirely a statement that reliable FR triggering is necessary. We request that the team add a new provision stating that all required FR channels at a location should be recorded whenever a trigger asserts on any one of them. Response: The SDT agrees that since the standard states that each T. O. and each G. O. must have a process in place to derive fault data, triggering is inherently required. Rather than explicitly prescribing how to trigger records, the SDT feels that each company already knows what works, and the standard was written to allow each company to continue to do what they know works. It is not efficient to record every channel at a particular location for a single trigger when protective relays are used as DFR and at this time the SDT does not think a requirement to record all channels for a single trigger is necessary to include in the standard. We would encourage the use of a common triggering methodology such that most relays at a location would capture an event. |
| Response: |  |  |
| E.ON U.S. | Yes | The SDT should explain the applicability of this requirement to the GO. |
| Response: The standard has been revised to clearly state what equipment each G. O and T. O. should monitor |  |  |
| Arizona Public Service Co. | Yes | There should be a provision for the case if the quantities aren't able to be measured (CT not available for example). In requirement R5.3 it makes the generator owner responsible to record the neutral current of the GSU high voltage winding. Sometimes, generators that have DFRs applied do not have this quantity available as they mostly have access to the low voltage quantities. In addition, if a generator owner has a fault recorder but doesn't have available channels for this additional quantity, he shouldn't be required to drop a channel he feels is important to make room for these mandated channels. For instance, one only needs two voltages and two currents to measure MW so a generator may have fault recording that measures 2 line voltages and 2 line currents and there may not be room to add the additional channels specified. Generally with two of the values you can derive the third so why force them to record all indicated quantities. These requiremens might be acceptable for new generator installations but there are existing installations that would find this ornerous. |
| Response: The SDT wrote the current recording requirements such that the currents may be determined, not necessarily monitored. It is not possible to derive all three phase quantities and neutral current by recording only two of the four, and the standard was written accordingly. |  |  |
| JEA | Yes |  |
| Tucson Electric Power | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing location requirements. See our answer to Question 7 above. |  |  |
| Alberta Electric System Operator | No | The AESO supports the IRC SRC comments. |
| Response: As stated above to the IRC SRC, the SDT is revising the standard and will take your suggestions into consideration. |  |  |
| Beckwith Electric Co | Yes |  |
| Duke Energy | Yes |  |
| CenterPoint Energy | No | The requirements to record all three phase to neutral voltages and all four currents on each transmission line are prescriptive and excessive. The monitoring of two sets of line voltages, in all substation configurations, is a common industry practice which has met the industry’s needs. It is unnecessary and excessive to require monitoring of more than two sets of three phase to neutral voltages in any substation arrangement. |
| Response: The standard states that those voltages must be able to be determined, not that every line or bus voltage absolutely needs to be recorded. As long as an adequate number of voltages are recorded, and circuit breaker status is known, it is possible to be able to determine all voltages without recording every line or bus individually. |  |  |
| Xcel Energy | No | As with Question 7, R5 is written such that it appears that the Generator Owner will have to duplicate the fault recording assigned to the Transmission Owner in R4. We assume that was not the SDT's intent, so we recommend that the second line of Table 5-1 include a clarifying statement such as "if not already monitored by the Transmission Owner." |
| Response: See answer to question 7 above. Additionally, the standard has been revised to clearly what equipment each G. O and T. O. should monitor. |  |  |
| Utility System Efficiencies, Inc. | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements operated between 200 kV and 300 kV and for substations with three or more elements operated at voltages over 300 kV. See my response to question 7 above. |
| Response: The SDT is reviewing location requirements. See answer to question 7 above. |  |  |
| British Columbia Transmission Corporation | No | Table 4-1 should also be modified to identify Substations containing any combination of five (5) or more elements. See response to question 7 above. |
| Response: The SDT is reviewing location requirements. See answer to question 7 above. |  |  |
| Kansas City Power & Light | No | It is not necessary to require voltages on every line and bus for a ring bus configuration. Suggest requiring at least 33% with a of lines or busses for a ring bus configuration and no less than 2 will be a reasonable assurance there is a voltage collection for fault recording for events. It is unlikely under normal conditions 33% of the lines or busses in a ring would be out of service concurrently. So, for ring configuration stations with up to 6 lines, 2 voltage measures would be required. Ring configuration stations between 7 and 9 lines would require 3 voltage measures. Ring configuration stations with 10 to 12 lines, 4 voltage measures would be required. And so on. |
| Response: The recording of every line and bus voltage is not explicitly stated in the standard. What is stated is that the voltages must be able to be determined. As long as an adequate number of voltages are recorded, such as every other bus or line on a ring bus, and circuit breaker position is known, all voltages can be determined. |  |  |
| PNM | No | R5.3 requires recording current at the neutral bushing of wye-connected GSU transformer high-side windings. That does not have enough value to be a requirement. With the defined time synch. requirements and abundance of recorded voltages correlation of values is accomplished. It may have some value where only low-side generator currents are monitored but not where high-side GSU currents are monitored. |
| Response: The standard states that these values may be determined, not necessarily monitored. As written, the high side neutral current is only required if low side phase currents are recorded instead of the high side phase currents. |  |  |