## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Total Lost Generation: enter the MW data of the units that tripped as a single generator where the value typically goes to zero at t(0).
Column D: not applicable
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: not applicable
Column H: not applicable
Column I: not applicable
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 2 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with larger sample size data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 469 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A469"
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 633.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A633"
9 | In cell "R41" of the "Evaluation" spreadsheet, enter the MW value of the unit(s) that tripped (from the Master Event List). This is only necessary for the "Interconnection" evaluation if you're interested.
It is not necessary to do this for the BA evaluation but it will provide a comparison of the BA frequency response as compared to the Interconnection frequency response.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Lost | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
mm/dd/yy hh:mm:ss | Frequency | Generation | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Setting
Time (T) | Hz | MW |  | MW | MW |  |  |  | MW/0.1 Hz | MW | LaaR Tripped
2011-07-18 20:35 | 60.002 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56914.7266 | 0
2011-07-18 20:35 | 60.002 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.6016
2011-07-18 20:35 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.6016
2011-07-18 20:35 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.6016
2011-07-18 20:35 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.6016
2011-07-18 20:35 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.6016
2011-07-18 20:35 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56923.082
2011-07-18 20:35 | 59.995 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56923.082
2011-07-18 20:35 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56923.082
2011-07-18 20:35 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56923.082
2011-07-18 20:35 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56923.082
2011-07-18 20:35 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56937.9922
2011-07-18 20:35 | 59.988 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56937.9922
2011-07-18 20:35 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56937.9922
2011-07-18 20:35 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56937.9922
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56937.9922
2011-07-18 20:36 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56932.4062
2011-07-18 20:36 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56932.4062
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56932.4062
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56932.4062
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56932.4062
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.8477
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.8477
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.8477
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.8477
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.8477
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.4844
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.4844
2011-07-18 20:36 | 59.982 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.4844
2011-07-18 20:36 | 59.98 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.4844
2011-07-18 20:36 | 59.982 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.4844
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.4844
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.4844
2011-07-18 20:36 | 59.981 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.4844
2011-07-18 20:36 | 59.981 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.4844
2011-07-18 20:36 | 59.98 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56928.4844
2011-07-18 20:36 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.6992
2011-07-18 20:36 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.6992
2011-07-18 20:36 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.6992
2011-07-18 20:36 | 59.987 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.6992
2011-07-18 20:36 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.6992
2011-07-18 20:36 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56930.0898
2011-07-18 20:36 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56930.0898
2011-07-18 20:36 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56930.0898
2011-07-18 20:36 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56930.0898
2011-07-18 20:36 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56930.0898
2011-07-18 20:37 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944
2011-07-18 20:37 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944
2011-07-18 20:37 | 59.987 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944
2011-07-18 20:37 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944
2011-07-18 20:37 | 59.987 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944
2011-07-18 20:37 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56934.5273
2011-07-18 20:37 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56934.5273
2011-07-18 20:37 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56934.5273
2011-07-18 20:37 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56934.5273
2011-07-18 20:37 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56934.5273
2011-07-18 20:37 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56942.7188
2011-07-18 20:37 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56942.7188
2011-07-18 20:37 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56942.7188
2011-07-18 20:37 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56942.7188
2011-07-18 20:37 | 59.995 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56942.7188
2011-07-18 20:37 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56939.7578
2011-07-18 20:37 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56939.7578
2011-07-18 20:37 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56939.7578
2011-07-18 20:37 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56939.7578
2011-07-18 20:37 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56939.7578
2011-07-18 20:37 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.9297
2011-07-18 20:37 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.9297
2011-07-18 20:37 | 60 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.9297
2011-07-18 20:37 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.9297
2011-07-18 20:37 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56933.9297
2011-07-18 20:37 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56945.9805
2011-07-18 20:37 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56945.9805
2011-07-18 20:37 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56945.9805
2011-07-18 20:37 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56945.9805
2011-07-18 20:38 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56945.9805
2011-07-18 20:38 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56940.8633
2011-07-18 20:38 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56940.8633
2011-07-18 20:38 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56940.8633
2011-07-18 20:38 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56940.8633
2011-07-18 20:38 | 60.025 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56940.8633
2011-07-18 20:38 | 60.025 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56916.582
2011-07-18 20:38 | 60.025 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56916.582
2011-07-18 20:38 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56916.582
2011-07-18 20:38 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56916.582
2011-07-18 20:38 | 60.025 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56916.582
2011-07-18 20:38 | 60.026 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56901.207
2011-07-18 20:38 | 60.029 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56901.207
2011-07-18 20:38 | 60.03 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56901.207
2011-07-18 20:38 | 60.028 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56901.207
2011-07-18 20:38 | 60.026 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56901.207
2011-07-18 20:38 | 60.026 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56896.1211
2011-07-18 20:38 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56896.1211
2011-07-18 20:38 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56896.1211
2011-07-18 20:38 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56896.1211
2011-07-18 20:38 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56896.1211
2011-07-18 20:38 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56911.668
2011-07-18 20:38 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56911.668
2011-07-18 20:38 | 60.003 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56911.668
2011-07-18 20:38 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56911.668
2011-07-18 20:38 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56911.668
2011-07-18 20:38 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56925.8789
2011-07-18 20:38 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56925.8789
2011-07-18 20:38 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56925.8789
2011-07-18 20:38 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56925.8789
2011-07-18 20:38 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56925.8789
2011-07-18 20:39 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56950.8828
2011-07-18 20:39 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56950.8828
2011-07-18 20:39 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56950.8828
2011-07-18 20:39 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56950.8828
2011-07-18 20:39 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56950.8828
2011-07-18 20:39 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.2969
2011-07-18 20:39 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.2969
2011-07-18 20:39 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.2969
2011-07-18 20:39 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.2969
2011-07-18 20:39 | 59.988 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.2969
2011-07-18 20:39 | 59.987 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56958.9609
2011-07-18 20:39 | 59.988 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56958.9609
2011-07-18 20:39 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56958.9609
2011-07-18 20:39 | 59.989 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56958.9609
2011-07-18 20:39 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56958.9609
2011-07-18 20:39 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56949.0664
2011-07-18 20:39 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56949.0664
2011-07-18 20:39 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56949.0664
2011-07-18 20:39 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56949.0664
2011-07-18 20:39 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56949.0664
2011-07-18 20:39 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944.2031
2011-07-18 20:39 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944.2031
2011-07-18 20:39 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944.2031
2011-07-18 20:39 | 59.986 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944.2031
2011-07-18 20:39 | 59.981 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56944.2031
2011-07-18 20:39 | 59.977 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.1016
2011-07-18 20:39 | 59.973 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.1016
2011-07-18 20:39 | 59.97 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.1016
2011-07-18 20:39 | 59.968 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.1016
2011-07-18 20:40 | 59.969 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56951.1016
2011-07-18 20:40 | 59.971 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56961.1328
2011-07-18 20:40 | 59.972 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56961.1328
2011-07-18 20:40 | 59.971 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56961.1328
2011-07-18 20:40 | 59.972 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56961.1328
2011-07-18 20:40 | 59.972 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56961.1328
2011-07-18 20:40 | 59.972 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56978.7305
2011-07-18 20:40 | 59.971 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56978.7305
2011-07-18 20:40 | 59.97 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56978.7305
2011-07-18 20:40 | 59.971 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56978.7305
2011-07-18 20:40 | 59.973 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56978.7305
2011-07-18 20:40 | 59.976 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56988.2148
2011-07-18 20:40 | 59.974 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56988.2148
2011-07-18 20:40 | 59.973 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56988.2148
2011-07-18 20:40 | 59.972 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56988.2148
2011-07-18 20:40 | 59.974 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56988.2148
2011-07-18 20:40 | 59.976 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56975.8516
2011-07-18 20:40 | 59.976 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56975.8516
2011-07-18 20:40 | 59.975 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56975.8516
2011-07-18 20:40 | 59.976 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56975.8516
2011-07-18 20:40 | 59.977 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56975.8516
2011-07-18 20:40 | 59.976 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57000.3438
2011-07-18 20:40 | 59.977 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57000.3438
2011-07-18 20:40 | 59.979 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57000.3438
2011-07-18 20:40 | 59.982 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57000.3438
2011-07-18 20:40 | 59.983 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57000.3438
2011-07-18 20:40 | 59.985 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57017.8086
2011-07-18 20:40 | 59.982 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57017.8086
2011-07-18 20:40 | 59.981 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57017.8086
2011-07-18 20:40 | 59.979 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57017.8086
2011-07-18 20:40 | 59.978 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57017.8086
2011-07-18 20:41 | 59.98 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57007.3125
2011-07-18 20:41 | 59.979 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57007.3125
2011-07-18 20:41 | 59.98 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57007.3125
2011-07-18 20:41 | 59.98 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57007.3125
2011-07-18 20:41 | 59.982 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57007.3125
2011-07-18 20:41 | 59.984 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56999.6719
2011-07-18 20:41 | 59.987 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56999.6719
2011-07-18 20:41 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56999.6719
2011-07-18 20:41 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56999.6719
2011-07-18 20:41 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 56999.6719
2011-07-18 20:41 | 59.99 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.625
2011-07-18 20:41 | 59.991 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.625
2011-07-18 20:41 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.625
2011-07-18 20:41 | 59.995 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.625
2011-07-18 20:41 | 59.996 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.625
2011-07-18 20:41 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57023.5312
2011-07-18 20:41 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57023.5312
2011-07-18 20:41 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57023.5312
2011-07-18 20:41 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57023.5312
2011-07-18 20:41 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57023.5312
2011-07-18 20:41 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.7227
2011-07-18 20:41 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.7227
2011-07-18 20:41 | 59.995 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.7227
2011-07-18 20:41 | 59.993 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.7227
2011-07-18 20:41 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57028.7227
2011-07-18 20:41 | 59.992 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.7383
2011-07-18 20:41 | 59.994 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.7383
2011-07-18 20:41 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.7383
2011-07-18 20:41 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.7383
2011-07-18 20:42 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.7383
2011-07-18 20:42 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.9102
2011-07-18 20:42 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.9102
2011-07-18 20:42 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.9102
2011-07-18 20:42 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.9102
2011-07-18 20:42 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.9102
2011-07-18 20:42 | 60.003 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.418
2011-07-18 20:42 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.418
2011-07-18 20:42 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.418
2011-07-18 20:42 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.418
2011-07-18 20:42 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.418
2011-07-18 20:42 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.8438
2011-07-18 20:42 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.8438
2011-07-18 20:42 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.8438
2011-07-18 20:42 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.8438
2011-07-18 20:42 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.8438
2011-07-18 20:42 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.9961
2011-07-18 20:42 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.9961
2011-07-18 20:42 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.9961
2011-07-18 20:42 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.9961
2011-07-18 20:42 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.9961
2011-07-18 20:42 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.3203
2011-07-18 20:42 | 60.024 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.3203
2011-07-18 20:42 | 60.023 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.3203
2011-07-18 20:42 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.3203
2011-07-18 20:42 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.3203
2011-07-18 20:42 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.8047
2011-07-18 20:42 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.8047
2011-07-18 20:42 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.8047
2011-07-18 20:42 | 60.023 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.8047
2011-07-18 20:42 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.8047
2011-07-18 20:43 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57059.8672
2011-07-18 20:43 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57059.8672
2011-07-18 20:43 | 60.024 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57059.8672
2011-07-18 20:43 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57059.8672
2011-07-18 20:43 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57059.8672
2011-07-18 20:43 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.1094
2011-07-18 20:43 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.1094
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.1094
2011-07-18 20:43 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.1094
2011-07-18 20:43 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.1094
2011-07-18 20:43 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.168
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.168
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.168
2011-07-18 20:43 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.168
2011-07-18 20:43 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57044.168
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.3242
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.3242
2011-07-18 20:43 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.3242
2011-07-18 20:43 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.3242
2011-07-18 20:43 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.3242
2011-07-18 20:43 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57027.4336
2011-07-18 20:43 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57027.4336
2011-07-18 20:43 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57027.4336
2011-07-18 20:43 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57027.4336
2011-07-18 20:43 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57027.4336
2011-07-18 20:43 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.2617
2011-07-18 20:43 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.2617
2011-07-18 20:43 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.2617
2011-07-18 20:43 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.2617
2011-07-18 20:44 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57048.2617
2011-07-18 20:44 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.5547
2011-07-18 20:44 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.5547
2011-07-18 20:44 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.5547
2011-07-18 20:44 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.5547
2011-07-18 20:44 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.5547
2011-07-18 20:44 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.4922
2011-07-18 20:44 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.4922
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.4922
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.4922
2011-07-18 20:44 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.4922
2011-07-18 20:44 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57064.8516
2011-07-18 20:44 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57064.8516
2011-07-18 20:44 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57064.8516
2011-07-18 20:44 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57064.8516
2011-07-18 20:44 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57064.8516
2011-07-18 20:44 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.6758
2011-07-18 20:44 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.6758
2011-07-18 20:44 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.6758
2011-07-18 20:44 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.6758
2011-07-18 20:44 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.6758
2011-07-18 20:44 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.0352
2011-07-18 20:44 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.0352
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.0352
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.0352
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57056.0352
2011-07-18 20:44 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.1875
2011-07-18 20:44 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.1875
2011-07-18 20:44 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.1875
2011-07-18 20:44 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.1875
2011-07-18 20:44 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57060.1875
2011-07-18 20:45 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.7812
2011-07-18 20:45 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.7812
2011-07-18 20:45 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.7812
2011-07-18 20:45 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.7812
2011-07-18 20:45 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57047.7812
2011-07-18 20:45 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.332
2011-07-18 20:45 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.332
2011-07-18 20:45 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.332
2011-07-18 20:45 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.332
2011-07-18 20:45 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.332
2011-07-18 20:45 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57045.4922
2011-07-18 20:45 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57045.4922
2011-07-18 20:45 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57045.4922
2011-07-18 20:45 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57045.4922
2011-07-18 20:45 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57045.4922
2011-07-18 20:45 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57051.957
2011-07-18 20:45 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57051.957
2011-07-18 20:45 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57051.957
2011-07-18 20:45 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57051.957
2011-07-18 20:45 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57051.957
2011-07-18 20:45 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.9414
2011-07-18 20:45 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.9414
2011-07-18 20:45 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.9414
2011-07-18 20:45 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.9414
2011-07-18 20:45 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.9414
2011-07-18 20:45 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.6484
2011-07-18 20:45 | 60.003 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.6484
2011-07-18 20:45 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.6484
2011-07-18 20:45 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.6484
2011-07-18 20:46 | 60.003 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.6484
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57068.2383
2011-07-18 20:46 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57068.2383
2011-07-18 20:46 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57068.2383
2011-07-18 20:46 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57068.2383
2011-07-18 20:46 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57068.2383
2011-07-18 20:46 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.9766
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.9766
2011-07-18 20:46 | 60.003 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.9766
2011-07-18 20:46 | 60.001 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.9766
2011-07-18 20:46 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.9766
2011-07-18 20:46 | 60 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.4336
2011-07-18 20:46 | 60.002 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.4336
2011-07-18 20:46 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.4336
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.4336
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.4336
2011-07-18 20:46 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57071.0469
2011-07-18 20:46 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57071.0469
2011-07-18 20:46 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57071.0469
2011-07-18 20:46 | 60.005 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57071.0469
2011-07-18 20:46 | 60 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57071.0469
2011-07-18 20:46 | 59.997 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9609
2011-07-18 20:46 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9609
2011-07-18 20:46 | 59.998 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9609
2011-07-18 20:46 | 59.999 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9609
2011-07-18 20:46 | 60.002 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9609
2011-07-18 20:46 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.5898
2011-07-18 20:46 | 60.004 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.5898
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.5898
2011-07-18 20:46 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.5898
2011-07-18 20:46 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.5898
2011-07-18 20:47 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.7695
2011-07-18 20:47 | 60.006 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.7695
2011-07-18 20:47 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.7695
2011-07-18 20:47 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.7695
2011-07-18 20:47 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57062.7695
2011-07-18 20:47 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072
2011-07-18 20:47 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072
2011-07-18 20:47 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072
2011-07-18 20:47 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072
2011-07-18 20:47 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072
2011-07-18 20:47 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.75
2011-07-18 20:47 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.75
2011-07-18 20:47 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.75
2011-07-18 20:47 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.75
2011-07-18 20:47 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57053.75
2011-07-18 20:47 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.9141
2011-07-18 20:47 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.9141
2011-07-18 20:47 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.9141
2011-07-18 20:47 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.9141
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57041.9141
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9492
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9492
2011-07-18 20:47 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9492
2011-07-18 20:47 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9492
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57054.9492
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.4297
2011-07-18 20:47 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.4297
2011-07-18 20:47 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.4297
2011-07-18 20:47 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.4297
2011-07-18 20:48 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57061.4297
2011-07-18 20:48 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.5664
2011-07-18 20:48 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.5664
2011-07-18 20:48 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.5664
2011-07-18 20:48 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.5664
2011-07-18 20:48 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.5664
2011-07-18 20:48 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.9766
2011-07-18 20:48 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.9766
2011-07-18 20:48 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.9766
2011-07-18 20:48 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.9766
2011-07-18 20:48 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57063.9766
2011-07-18 20:48 | 60.022 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57057.7461
2011-07-18 20:48 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57057.7461
2011-07-18 20:48 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57057.7461
2011-07-18 20:48 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57057.7461
2011-07-18 20:48 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57057.7461
2011-07-18 20:48 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.8047
2011-07-18 20:48 | 60.015 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.8047
2011-07-18 20:48 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.8047
2011-07-18 20:48 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.8047
2011-07-18 20:48 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.8047
2011-07-18 20:48 | 60.019 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57052.6836
2011-07-18 20:48 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57052.6836
2011-07-18 20:48 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57052.6836
2011-07-18 20:48 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57052.6836
2011-07-18 20:48 | 60.017 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57052.6836
2011-07-18 20:48 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57049.9531
2011-07-18 20:48 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57049.9531
2011-07-18 20:48 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57049.9531
2011-07-18 20:48 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57049.9531
2011-07-18 20:49 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57049.9531
2011-07-18 20:49 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072.4961
2011-07-18 20:49 | 60.007 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072.4961
2011-07-18 20:49 | 60.008 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072.4961
2011-07-18 20:49 | 60.009 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072.4961
2011-07-18 20:49 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57072.4961
2011-07-18 20:49 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.6211
2011-07-18 20:49 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.6211
2011-07-18 20:49 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.6211
2011-07-18 20:49 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.6211
2011-07-18 20:49 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57075.6211
2011-07-18 20:49 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57081.0195
2011-07-18 20:49 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57081.0195
2011-07-18 20:49 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57081.0195
2011-07-18 20:49 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57081.0195
2011-07-18 20:49 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57081.0195
2011-07-18 20:49 | 60.013 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57074.8594
2011-07-18 20:49 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57074.8594
2011-07-18 20:49 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57074.8594
2011-07-18 20:49 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57074.8594
2011-07-18 20:49 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57074.8594
2011-07-18 20:49 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57065.5547
2011-07-18 20:49 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57065.5547
2011-07-18 20:49 | 60.021 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57065.5547
2011-07-18 20:49 | 60.02 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57065.5547
2011-07-18 20:49 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57065.5547
2011-07-18 20:49 | 60.018 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.0938
2011-07-18 20:49 | 60.016 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.0938
2011-07-18 20:49 | 60.014 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.0938
2011-07-18 20:49 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.0938
2011-07-18 20:50 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57058.0938
2011-07-18 20:50 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.5
2011-07-18 20:50 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.5
2011-07-18 20:50 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.5
2011-07-18 20:50 | 60.01 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.5
2011-07-18 20:50 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57042.5
2011-07-18 20:50 | 60.011 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.1172
2011-07-18 20:50 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.1172
2011-07-18 20:50 | 60.012 | 593.3 |  | 0 | 0 |  |  |  | -653 | 57050.1172
2011-07-18 20:50 | 60.011 | 585.6284 |  | 0 | 0 |  |  |  | -653 | 57057.2109
2011-07-18 20:50 | 60.012 | 585.6284 |  | 0 | 0 |  |  |  | -653 | 57057.2109
2011-07-18 20:50 | 60.013 | 586.143 |  | 0 | 0 |  |  |  | -653 | 57051.7422
2011-07-18 20:50 | 60.015 | 586.143 |  | 0 | 0 |  |  |  | -653 | 57051.7422
2011-07-18 20:50 | 60.016 | 586.7954 |  | 0 | 0 |  |  |  | -653 | 57051.7422
2011-07-18 20:50 | 60.015 | 586.7954 |  | 0 | 0 |  |  |  | -653 | 57051.7422
2011-07-18 20:50 | 60.014 | 585.9467 |  | 0 | 0 |  |  |  | -653 | 57037.8789
2011-07-18 20:50 | 60.013 | 585.9467 |  | 0 | 0 |  |  |  | -653 | 57037.8789
2011-07-18 20:50 | 60.012 | 585.6723 |  | 0 | 0 |  |  |  | -653 | 57050.4336
2011-07-18 20:50 | 60.012 | 585.6723 |  | 0 | 0 |  |  |  | -653 | 57050.4336
2011-07-18 20:50 | 60.012 | 585.1163 |  | 0 | 0 |  |  |  | -653 | 57029.9219
2011-07-18 20:50 | 60.013 | 585.1163 |  | 0 | 0 |  |  |  | -653 | 57029.9219
2011-07-18 20:50 | 60.015 | 584.655 |  | 0 | 0 |  |  |  | -653 | 57033.7109
2011-07-18 20:50 | 60.017 | 584.655 |  | 0 | 0 |  |  |  | -653 | 57033.7109
2011-07-18 20:50 | 60.017 | 585.3073 |  | 0 | 0 |  |  |  | -653 | 57035.5586
2011-07-18 20:50 | 60.014 | 585.3073 |  | 0 | 0 |  |  |  | -653 | 57035.5586
2011-07-18 20:50 | 60.015 | 585.2109 |  | 0 | 0 |  |  |  | -653 | 57020.6016
2011-07-18 20:50 | 60.013 | 585.2109 |  | 0 | 0 |  |  |  | -653 | 57020.6016
2011-07-18 20:50 | 60.012 | 585.9184 |  | 0 | 0 |  |  |  | -653 | 57030.3711
2011-07-18 20:50 | 60.011 | 585.9184 |  | 0 | 0 |  |  |  | -653 | 57030.3711
2011-07-18 20:50 | 60.008 | 593.2776 |  | 0 | 0 |  |  |  | -653 | 57039.1484
2011-07-18 20:50 | 60.008 | 593.2776 |  | 0 | 0 |  |  |  | -653 | 57039.1484
2011-07-18 20:51 | 60.007 | 602.7012 |  | 0 | 0 |  |  |  | -653 | 57042.2031
2011-07-18 20:51 | 60.007 | 602.7012 |  | 0 | 0 |  |  |  | -653 | 57042.2031
2011-07-18 20:51 | 60.007 | 602.7012 |  | 0 | 0 |  |  |  | -653 | 57089.3008
2011-07-18 20:51 | 60.007 | 602.7012 |  | 0 | 0 |  |  |  | -653 | 57089.3008
2011-07-18 20:51 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56704.1289
2011-07-18 20:51 | 59.918 | 0 |  | 0 | 0 |  |  |  | -653 | 56704.1289
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56763.9688
2011-07-18 20:51 | 59.872 | 0 |  | 0 | 0 |  |  |  | -653 | 56763.9688
2011-07-18 20:51 | 59.866 | 0 |  | 0 | 0 |  |  |  | -653 | 56811.1953
2011-07-18 20:51 | 59.867 | 0 |  | 0 | 0 |  |  |  | -653 | 56811.1953
2011-07-18 20:51 | 59.868 | 0 |  | 0 | 0 |  |  |  | -653 | 56864.9648
2011-07-18 20:51 | 59.874 | 0 |  | 0 | 0 |  |  |  | -653 | 56864.9648
2011-07-18 20:51 | 59.876 | 0 |  | 0 | 0 |  |  |  | -653 | 56863.4336
2011-07-18 20:51 | 59.878 | 0 |  | 0 | 0 |  |  |  | -653 | 56863.4336
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56867.5078
2011-07-18 20:51 | 59.883 | 0 |  | 0 | 0 |  |  |  | -653 | 56867.5078
2011-07-18 20:51 | 59.881 | 0 |  | 0 | 0 |  |  |  | -653 | 56878.3594
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56878.3594
2011-07-18 20:51 | 59.881 | 0 |  | 0 | 0 |  |  |  | -653 | 56886.3242
2011-07-18 20:51 | 59.881 | 0 |  | 0 | 0 |  |  |  | -653 | 56886.3242
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56893.1289
2011-07-18 20:51 | 59.878 | 0 |  | 0 | 0 |  |  |  | -653 | 56893.1289
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56875.6172
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56875.6172
2011-07-18 20:51 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56890.8242
2011-07-18 20:51 | 59.882 | 0 |  | 0 | 0 |  |  |  | -653 | 56890.8242
2011-07-18 20:51 | 59.883 | 0 |  | 0 | 0 |  |  |  | -653 | 56891.0664
2011-07-18 20:51 | 59.882 | 0 |  | 0 | 0 |  |  |  | -653 | 56891.0664
2011-07-18 20:51 | 59.883 | 0 |  | 0 | 0 |  |  |  | -653 | 56899.4688
2011-07-18 20:52 | 59.88 | 0 |  | 0 | 0 |  |  |  | -653 | 56899.4688
2011-07-18 20:52 | 59.881 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.9023
2011-07-18 20:52 | 59.884 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.9023
2011-07-18 20:52 | 59.892 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.8125
2011-07-18 20:52 | 59.894 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.8125
2011-07-18 20:52 | 59.896 | 0 |  | 0 | 0 |  |  |  | -653 | 56837.2148
2011-07-18 20:52 | 59.9 | 0 |  | 0 | 0 |  |  |  | -653 | 56837.2148
2011-07-18 20:52 | 59.902 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.5938
2011-07-18 20:52 | 59.904 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.5938
2011-07-18 20:52 | 59.903 | 0 |  | 0 | 0 |  |  |  | -653 | 56841.8438
2011-07-18 20:52 | 59.902 | 0 |  | 0 | 0 |  |  |  | -653 | 56841.8438
2011-07-18 20:52 | 59.903 | 0 |  | 0 | 0 |  |  |  | -653 | 56835.3047
2011-07-18 20:52 | 59.902 | 0 |  | 0 | 0 |  |  |  | -653 | 56835.3047
2011-07-18 20:52 | 59.901 | 0 |  | 0 | 0 |  |  |  | -653 | 56837.2969
2011-07-18 20:52 | 59.9 | 0 |  | 0 | 0 |  |  |  | -653 | 56837.2969
2011-07-18 20:52 | 59.901 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.1523
2011-07-18 20:52 | 59.904 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.1523
2011-07-18 20:52 | 59.907 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.543
2011-07-18 20:52 | 59.91 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.543
2011-07-18 20:52 | 59.913 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.6367
2011-07-18 20:52 | 59.916 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.6367
2011-07-18 20:52 | 59.916 | 0 |  | 0 | 0 |  |  |  | -653 | 56866.1602
2011-07-18 20:52 | 59.919 | 0 |  | 0 | 0 |  |  |  | -653 | 56866.1602
2011-07-18 20:52 | 59.922 | 0 |  | 0 | 0 |  |  |  | -653 | 56869.2109
2011-07-18 20:52 | 59.924 | 0 |  | 0 | 0 |  |  |  | -653 | 56869.2109
2011-07-18 20:52 | 59.924 | 0 |  | 0 | 0 |  |  |  | -653 | 56876.2656
2011-07-18 20:52 | 59.924 | 0 |  | 0 | 0 |  |  |  | -653 | 56876.2656
2011-07-18 20:52 | 59.925 | 0 |  | 0 | 0 |  |  |  | -653 | 56881.3906
2011-07-18 20:52 | 59.928 | 0 |  | 0 | 0 |  |  |  | -653 | 56881.3906
2011-07-18 20:52 | 59.929 | 0 |  | 0 | 0 |  |  |  | -653 | 56889.5859
2011-07-18 20:52 | 59.932 | 0 |  | 0 | 0 |  |  |  | -653 | 56889.5859
2011-07-18 20:53 | 59.934 | 0 |  | 0 | 0 |  |  |  | -653 | 56893.8867
2011-07-18 20:53 | 59.935 | 0 |  | 0 | 0 |  |  |  | -653 | 56900.4414
2011-07-18 20:53 | 59.935 | 0 |  | 0 | 0 |  |  |  | -653 | 56900.4414
2011-07-18 20:53 | 59.935 | 0 |  | 0 | 0 |  |  |  | -653 | 56900.4414
2011-07-18 20:53 | 59.935 | 0 |  | 0 | 0 |  |  |  | -653 | 56887.582
2011-07-18 20:53 | 59.934 | 0 |  | 0 | 0 |  |  |  | -653 | 56887.582
2011-07-18 20:53 | 59.935 | 0 |  | 0 | 0 |  |  |  | -653 | 56901.5859
2011-07-18 20:53 | 59.938 | 0 |  | 0 | 0 |  |  |  | -653 | 56901.5859
2011-07-18 20:53 | 59.941 | 0 |  | 0 | 0 |  |  |  | -653 | 56915.6562
2011-07-18 20:53 | 59.943 | 0 |  | 0 | 0 |  |  |  | -653 | 56915.6562
2011-07-18 20:53 | 59.948 | 0 |  | 0 | 0 |  |  |  | -653 | 56912.2109
2011-07-18 20:53 | 59.951 | 0 |  | 0 | 0 |  |  |  | -653 | 56912.2109
2011-07-18 20:53 | 59.951 | 0 |  | 0 | 0 |  |  |  | -653 | 56914.3086
2011-07-18 20:53 | 59.953 | 0 |  | 0 | 0 |  |  |  | -653 | 56914.3086
2011-07-18 20:53 | 59.956 | 0 |  | 0 | 0 |  |  |  | -653 | 56907.5391
2011-07-18 20:53 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 56907.5391
2011-07-18 20:53 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 56897.043
2011-07-18 20:53 | 59.959 | 0 |  | 0 | 0 |  |  |  | -653 | 56897.043
2011-07-18 20:53 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 56902.0312
2011-07-18 20:53 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 56902.0312
2011-07-18 20:53 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 56903.0273
2011-07-18 20:53 | 59.96 | 0 |  | 0 | 0 |  |  |  | -653 | 56903.0273
2011-07-18 20:53 | 59.962 | 0 |  | 0 | 0 |  |  |  | -653 | 56917.7422
2011-07-18 20:53 | 59.965 | 0 |  | 0 | 0 |  |  |  | -653 | 56917.7422
2011-07-18 20:53 | 59.967 | 0 |  | 0 | 0 |  |  |  | -653 | 56900.8125
2011-07-18 20:53 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56900.8125
2011-07-18 20:53 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56914.8047
2011-07-18 20:53 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56914.8047
2011-07-18 20:53 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56922.5234
2011-07-18 20:54 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56922.5234
2011-07-18 20:54 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56932.4453
2011-07-18 20:54 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56932.4453
2011-07-18 20:54 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 56920.2305
2011-07-18 20:54 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56920.2305
2011-07-18 20:54 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 56912.875
2011-07-18 20:54 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 56912.875
2011-07-18 20:54 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56905.2188
2011-07-18 20:54 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 56905.2188
2011-07-18 20:54 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56915.6172
2011-07-18 20:54 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56915.6172
2011-07-18 20:54 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56923.0312
2011-07-18 20:54 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56923.0312
2011-07-18 20:54 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56932.0273
2011-07-18 20:54 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56932.0273
2011-07-18 20:54 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56926.2188
2011-07-18 20:54 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56926.2188
2011-07-18 20:54 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56930.3281
2011-07-18 20:54 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56930.3281
2011-07-18 20:54 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56935.1094
2011-07-18 20:54 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56935.1094
2011-07-18 20:54 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56938.2383
2011-07-18 20:54 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56938.2383
2011-07-18 20:54 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56947.1367
2011-07-18 20:54 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56947.1367
2011-07-18 20:54 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56946.1875
2011-07-18 20:54 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56946.1875
2011-07-18 20:54 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56937.3008
2011-07-18 20:54 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56937.3008
2011-07-18 20:54 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56931.4141
2011-07-18 20:54 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56931.4141
2011-07-18 20:55 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56924.8359
2011-07-18 20:55 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56924.8359
2011-07-18 20:55 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56933.1562
2011-07-18 20:55 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56933.1562
2011-07-18 20:55 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56935.6211
2011-07-18 20:55 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56935.6211
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56957.3164
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56957.3164
2011-07-18 20:55 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56954.2344
2011-07-18 20:55 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56954.2344
2011-07-18 20:55 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56956.6445
2011-07-18 20:55 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56956.6445
2011-07-18 20:55 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56956.6016
2011-07-18 20:55 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56956.6016
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56938.9023
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56938.9023
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56943.1797
2011-07-18 20:55 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56943.1797
2011-07-18 20:55 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56939.0664
2011-07-18 20:55 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56939.0664
2011-07-18 20:55 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56942.4414
2011-07-18 20:55 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56942.4414
2011-07-18 20:55 | 60.037 | 0 |  | 0 | 0 |  |  |  | -653 | 56924.3672
2011-07-18 20:55 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56924.3672
2011-07-18 20:55 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56907.8984
2011-07-18 20:55 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56907.8984
2011-07-18 20:55 | 60.052 | 0 |  | 0 | 0 |  |  |  | -653 | 56897.7969
2011-07-18 20:55 | 60.051 | 0 |  | 0 | 0 |  |  |  | -653 | 56897.7969
2011-07-18 20:55 | 60.05 | 0 |  | 0 | 0 |  |  |  | -653 | 56864.8906
2011-07-18 20:55 | 60.051 | 0 |  | 0 | 0 |  |  |  | -653 | 56864.8906
2011-07-18 20:56 | 60.049 | 0 |  | 0 | 0 |  |  |  | -653 | 56842.6602
2011-07-18 20:56 | 60.05 | 0 |  | 0 | 0 |  |  |  | -653 | 56842.6602
2011-07-18 20:56 | 60.051 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.2812
2011-07-18 20:56 | 60.049 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.2812
2011-07-18 20:56 | 60.048 | 0 |  | 0 | 0 |  |  |  | -653 | 56850.6172
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56850.6172
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56870.9102
2011-07-18 20:56 | 60.042 | 0 |  | 0 | 0 |  |  |  | -653 | 56870.9102
2011-07-18 20:56 | 60.044 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.5547
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.5547
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56848.6172
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56848.6172
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.1992
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.1992
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.8828
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.8828
2011-07-18 20:56 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56851.7969
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56851.7969
2011-07-18 20:56 | 60.044 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.9805
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56861.9805
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56851.0195
2011-07-18 20:56 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56851.0195
2011-07-18 20:56 | 60.047 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.1289
2011-07-18 20:56 | 60.047 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.1289
2011-07-18 20:56 | 60.048 | 0 |  | 0 | 0 |  |  |  | -653 | 56847.9492
2011-07-18 20:56 | 60.05 | 0 |  | 0 | 0 |  |  |  | -653 | 56847.9492
2011-07-18 20:56 | 60.052 | 0 |  | 0 | 0 |  |  |  | -653 | 56843.6641
2011-07-18 20:56 | 60.052 | 0 |  | 0 | 0 |  |  |  | -653 | 56843.6641
2011-07-18 20:56 | 60.049 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.3945
2011-07-18 20:56 | 60.048 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.3945
2011-07-18 20:57 | 60.049 | 0 |  | 0 | 0 |  |  |  | -653 | 56814.3828
2011-07-18 20:57 | 60.051 | 0 |  | 0 | 0 |  |  |  | -653 | 56814.3828
2011-07-18 20:57 | 60.05 | 0 |  | 0 | 0 |  |  |  | -653 | 56817.1602
2011-07-18 20:57 | 60.049 | 0 |  | 0 | 0 |  |  |  | -653 | 56817.1602
2011-07-18 20:57 | 60.048 | 0 |  | 0 | 0 |  |  |  | -653 | 56805.5156
2011-07-18 20:57 | 60.046 | 0 |  | 0 | 0 |  |  |  | -653 | 56805.5156
2011-07-18 20:57 | 60.044 | 0 |  | 0 | 0 |  |  |  | -653 | 56807.832
2011-07-18 20:57 | 60.043 | 0 |  | 0 | 0 |  |  |  | -653 | 56807.832
2011-07-18 20:57 | 60.045 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.4102
2011-07-18 20:57 | 60.044 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.4102
2011-07-18 20:57 | 60.04 | 0 |  | 0 | 0 |  |  |  | -653 | 56821.6875
2011-07-18 20:57 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56821.6875
2011-07-18 20:57 | 60.036 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.9492
2011-07-18 20:57 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.9492
2011-07-18 20:57 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56860.5078
2011-07-18 20:57 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56860.5078
2011-07-18 20:57 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56877.5938
2011-07-18 20:57 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56877.5938
2011-07-18 20:57 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56918.6641
2011-07-18 20:57 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56918.6641
2011-07-18 20:57 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56891.7109
2011-07-18 20:57 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56891.7109
2011-07-18 20:57 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56894.3477
2011-07-18 20:57 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56894.3477
2011-07-18 20:57 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56895.168
2011-07-18 20:57 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56895.168
2011-07-18 20:57 | 60.04 | 0 |  | 0 | 0 |  |  |  | -653 | 56889.7266
2011-07-18 20:57 | 60.04 | 0 |  | 0 | 0 |  |  |  | -653 | 56889.7266
2011-07-18 20:57 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56892.3945
2011-07-18 20:58 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56892.3945
2011-07-18 20:58 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56875.332
2011-07-18 20:58 | 60.037 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.0078
2011-07-18 20:58 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.0078
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.0078
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56881.0039
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56881.0039
2011-07-18 20:58 | 60.036 | 0 |  | 0 | 0 |  |  |  | -653 | 56887.4492
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56887.4492
2011-07-18 20:58 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56882.082
2011-07-18 20:58 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56882.082
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56879.1133
2011-07-18 20:58 | 60.036 | 0 |  | 0 | 0 |  |  |  | -653 | 56879.1133
2011-07-18 20:58 | 60.038 | 0 |  | 0 | 0 |  |  |  | -653 | 56884.3555
2011-07-18 20:58 | 60.04 | 0 |  | 0 | 0 |  |  |  | -653 | 56884.3555
2011-07-18 20:58 | 60.039 | 0 |  | 0 | 0 |  |  |  | -653 | 56872.6328
2011-07-18 20:58 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56872.6328
2011-07-18 20:58 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56865.5156
2011-07-18 20:58 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56865.5156
2011-07-18 20:58 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.4805
2011-07-18 20:58 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56874.4805
2011-07-18 20:58 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56866.3477
2011-07-18 20:58 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56866.3477
2011-07-18 20:58 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56868.5
2011-07-18 20:58 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56868.5
2011-07-18 20:58 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56865.5781
2011-07-18 20:58 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56865.5781
2011-07-18 20:58 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56862.7578
2011-07-18 20:58 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56862.7578
2011-07-18 20:58 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56871.1289
2011-07-18 20:58 | 60.036 | 0 |  | 0 | 0 |  |  |  | -653 | 56871.1289
2011-07-18 20:59 | 60.037 | 0 |  | 0 | 0 |  |  |  | -653 | 56863.4805
2011-07-18 20:59 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56863.4805
2011-07-18 20:59 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56856.707
2011-07-18 20:59 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56856.707
2011-07-18 20:59 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56859.6719
2011-07-18 20:59 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56859.6719
2011-07-18 20:59 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56860.4062
2011-07-18 20:59 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56860.4062
2011-07-18 20:59 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56867.3125
2011-07-18 20:59 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56867.3125
2011-07-18 20:59 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56852.1367
2011-07-18 20:59 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56852.1367
2011-07-18 20:59 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.8125
2011-07-18 20:59 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56838.8125
2011-07-18 20:59 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56839.6406
2011-07-18 20:59 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56839.6406
2011-07-18 20:59 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56839.9648
2011-07-18 20:59 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56839.9648
2011-07-18 20:59 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56841.0078
2011-07-18 20:59 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56841.0078
2011-07-18 20:59 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.9023
2011-07-18 20:59 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56854.9023
2011-07-18 20:59 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.9961
2011-07-18 20:59 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56845.9961
2011-07-18 20:59 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.0703
2011-07-18 20:59 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.0703
2011-07-18 20:59 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.2773
2011-07-18 20:59 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56827.2773
2011-07-18 20:59 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56829.4219
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56829.4219
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56846.6562
2011-07-18 21:00 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56846.6562
2011-07-18 21:00 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56840.5703
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56840.5703
2011-07-18 21:00 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56831.9141
2011-07-18 21:00 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56831.9141
2011-07-18 21:00 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.3516
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.3516
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.6328
2011-07-18 21:00 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.6328
2011-07-18 21:00 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56828
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56828
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56828
2011-07-18 21:00 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56828
2011-07-18 21:00 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.8008
2011-07-18 21:00 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56833.8008
2011-07-18 21:00 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56806.8594
2011-07-18 21:00 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56806.8594
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56813.1758
2011-07-18 21:00 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56813.1758
2011-07-18 21:00 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56804.2734
2011-07-18 21:00 | 60.035 | 0 |  | 0 | 0 |  |  |  | -653 | 56804.2734
2011-07-18 21:00 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56787.3438
2011-07-18 21:00 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56787.3438
2011-07-18 21:00 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56786.8438
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56786.8438
2011-07-18 21:00 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56773.4883
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56773.4883
2011-07-18 21:00 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56759.3672
2011-07-18 21:00 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56759.3672
2011-07-18 21:01 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56742.3398
2011-07-18 21:01 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56742.3398
2011-07-18 21:01 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56734.9805
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56734.9805
2011-07-18 21:01 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56750.6172
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56750.6172
2011-07-18 21:01 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56746.8867
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56746.8867
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56753.2773
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56753.2773
2011-07-18 21:01 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56749.9648
2011-07-18 21:01 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56749.9648
2011-07-18 21:01 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56728.9453
2011-07-18 21:01 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56728.9453
2011-07-18 21:01 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56723.3242
2011-07-18 21:01 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56723.3242
2011-07-18 21:01 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56715.2227
2011-07-18 21:01 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56715.2227
2011-07-18 21:01 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56724.0977
2011-07-18 21:01 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56724.0977
2011-07-18 21:01 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56718.9062
2011-07-18 21:01 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56718.9062
2011-07-18 21:01 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56704.9922
2011-07-18 21:01 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56704.9922
2011-07-18 21:01 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56708.4766
2011-07-18 21:01 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56708.4766
2011-07-18 21:01 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56730.4492
2011-07-18 21:01 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56730.4492
2011-07-18 21:01 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56720.1562
2011-07-18 21:02 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56720.1562
2011-07-18 21:02 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56711.6289
2011-07-18 21:02 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56711.6289
2011-07-18 21:02 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56708.6641
2011-07-18 21:02 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56708.6641
2011-07-18 21:02 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56706.6133
2011-07-18 21:02 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56706.6133
2011-07-18 21:02 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56716.5508
2011-07-18 21:02 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56716.5508
2011-07-18 21:02 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56705.832
2011-07-18 21:02 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56705.832
2011-07-18 21:02 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56696.3867
2011-07-18 21:02 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56696.3867
2011-07-18 21:02 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56670.6172
2011-07-18 21:02 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56670.6172
2011-07-18 21:02 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56642.6875
2011-07-18 21:02 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56642.6875
2011-07-18 21:02 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56644.3242
2011-07-18 21:02 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56644.3242
2011-07-18 21:02 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56636.4062
2011-07-18 21:02 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56636.4062
2011-07-18 21:02 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56630.7461
2011-07-18 21:02 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56630.7461
2011-07-18 21:02 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56620.9141
2011-07-18 21:02 | 60.037 | 0 |  | 0 | 0 |  |  |  | -653 | 56620.9141
2011-07-18 21:02 | 60.036 | 0 |  | 0 | 0 |  |  |  | -653 | 56619
2011-07-18 21:02 | 60.034 | 0 |  | 0 | 0 |  |  |  | -653 | 56619
2011-07-18 21:02 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56610.4453
2011-07-18 21:02 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56610.4453
2011-07-18 21:02 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56598.0625
2011-07-18 21:02 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56598.0625
2011-07-18 21:03 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56587.0469
2011-07-18 21:03 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56589.8906
2011-07-18 21:03 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56589.8906
2011-07-18 21:03 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56589.8906
2011-07-18 21:03 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56581.125
2011-07-18 21:03 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56581.125
2011-07-18 21:03 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56587.6914
2011-07-18 21:03 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56587.6914
2011-07-18 21:03 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56605.1953
2011-07-18 21:03 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56605.1953
2011-07-18 21:03 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56592.7812
2011-07-18 21:03 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56592.7812
2011-07-18 21:03 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56586.0508
2011-07-18 21:03 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56586.0508
2011-07-18 21:03 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56581.3828
2011-07-18 21:03 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56581.3828
2011-07-18 21:03 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56576.918
2011-07-18 21:03 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56576.918
2011-07-18 21:03 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56570.8984
2011-07-18 21:03 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56570.8984
2011-07-18 21:03 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56585.2969
2011-07-18 21:03 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56585.2969
2011-07-18 21:03 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56579.2891
2011-07-18 21:03 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56579.2891
2011-07-18 21:03 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56575.293
2011-07-18 21:03 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56575.293
2011-07-18 21:03 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56567.6992
2011-07-18 21:03 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56567.6992
2011-07-18 21:03 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56566.8633
2011-07-18 21:04 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56566.8633
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56567.7969
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56567.7969
2011-07-18 21:04 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56565.918
2011-07-18 21:04 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56565.918
2011-07-18 21:04 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56569.9961
2011-07-18 21:04 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56569.9961
2011-07-18 21:04 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56565.5781
2011-07-18 21:04 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56565.5781
2011-07-18 21:04 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56557.957
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56557.957
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56538.8945
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56538.8945
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56537.918
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56537.918
2011-07-18 21:04 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56544.3555
2011-07-18 21:04 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56544.3555
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.6836
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.6836
2011-07-18 21:04 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56554.3086
2011-07-18 21:04 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56554.3086
2011-07-18 21:04 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56543.293
2011-07-18 21:04 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56543.293
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56531.3398
2011-07-18 21:04 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56531.3398
2011-07-18 21:04 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.4492
2011-07-18 21:04 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.4492
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56546.6133
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56546.6133
2011-07-18 21:04 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56538.9219
2011-07-18 21:05 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56538.9219
2011-07-18 21:05 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56548.0664
2011-07-18 21:05 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56548.0664
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.0195
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56542.0195
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56531.9102
2011-07-18 21:05 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56531.9102
2011-07-18 21:05 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56528.668
2011-07-18 21:05 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56528.668
2011-07-18 21:05 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56528.4648
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56528.4648
2011-07-18 21:05 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56519.6055
2011-07-18 21:05 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56519.6055
2011-07-18 21:05 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56512.2031
2011-07-18 21:05 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56512.2031
2011-07-18 21:05 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56514.5234
2011-07-18 21:05 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56514.5234
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56508.4688
2011-07-18 21:05 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56508.4688
2011-07-18 21:05 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56512.1523
2011-07-18 21:05 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56512.1523
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56508.8594
2011-07-18 21:05 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56508.8594
2011-07-18 21:05 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56503.3359
2011-07-18 21:05 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56503.3359
2011-07-18 21:05 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56510.0859
2011-07-18 21:05 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56510.0859
2011-07-18 21:05 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56514.668
2011-07-18 21:05 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56514.668
2011-07-18 21:05 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.8984
2011-07-18 21:06 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.8984
2011-07-18 21:06 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56510.4648
2011-07-18 21:06 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56510.4648
2011-07-18 21:06 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56504.7422
2011-07-18 21:06 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 56504.7422
2011-07-18 21:06 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 56502.2031
2011-07-18 21:06 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 56502.2031
2011-07-18 21:06 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.2461
2011-07-18 21:06 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.2461
2011-07-18 21:06 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 56500.1016
2011-07-18 21:06 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 56500.1016
2011-07-18 21:06 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 56492.3047
2011-07-18 21:06 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56492.3047
2011-07-18 21:06 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 56483.543
2011-07-18 21:06 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 56483.543
2011-07-18 21:06 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 56486.4023
2011-07-18 21:06 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56486.4023
2011-07-18 21:06 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56496.6797
2011-07-18 21:06 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56496.6797
2011-07-18 21:06 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56489.4805
2011-07-18 21:06 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56489.4805
2011-07-18 21:06 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56476.5547
2011-07-18 21:06 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56476.5547
2011-07-18 21:06 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56484.8438
2011-07-18 21:06 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56484.8438
2011-07-18 21:06 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56494.2578
2011-07-18 21:06 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56494.2578
2011-07-18 21:06 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56478.4922
2011-07-18 21:06 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56478.4922
2011-07-18 21:06 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.8672
2011-07-18 21:06 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56501.8672
2011-07-18 21:07 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56491.5078
2011-07-18 21:07 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56491.5078
2011-07-18 21:07 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 56480.0312
2011-07-18 21:07 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56480.0312
2011-07-18 21:07 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56464.7109
2011-07-18 21:07 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56464.7109
2011-07-18 21:07 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56462.3672
2011-07-18 21:07 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56462.3672
2011-07-18 21:07 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56457.7344
2011-07-18 21:07 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56457.7344
2011-07-18 21:07 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.2578
2011-07-18 21:07 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.2578
2011-07-18 21:07 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.1016
2011-07-18 21:07 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.1016
2011-07-18 21:07 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56440.1016
2011-07-18 21:07 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56440.1016
2011-07-18 21:07 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56440.5859
2011-07-18 21:07 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56440.5859
2011-07-18 21:07 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56443.3008
2011-07-18 21:07 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56443.3008
2011-07-18 21:07 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.2695
2011-07-18 21:07 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.2695
2011-07-18 21:07 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56442.7656
2011-07-18 21:07 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56442.7656
2011-07-18 21:07 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56442.0195
2011-07-18 21:07 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56442.0195
2011-07-18 21:07 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56445.7812
2011-07-18 21:07 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56445.7812
2011-07-18 21:07 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.6797
2011-07-18 21:08 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.6797
2011-07-18 21:08 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56446.4805
2011-07-18 21:08 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.8516
2011-07-18 21:08 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.8516
2011-07-18 21:08 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.8516
2011-07-18 21:08 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.1602
2011-07-18 21:08 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.1602
2011-07-18 21:08 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56423.0586
2011-07-18 21:08 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56423.0586
2011-07-18 21:08 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56413.6484
2011-07-18 21:08 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56413.6484
2011-07-18 21:08 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.5273
2011-07-18 21:08 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.5273
2011-07-18 21:08 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56406.3398
2011-07-18 21:08 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56406.3398
2011-07-18 21:08 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.2227
2011-07-18 21:08 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.2227
2011-07-18 21:08 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56415.6875
2011-07-18 21:08 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56415.6875
2011-07-18 21:08 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56420.5977
2011-07-18 21:08 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56420.5977
2011-07-18 21:08 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.1406
2011-07-18 21:08 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.1406
2011-07-18 21:08 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56439.4141
2011-07-18 21:08 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56439.4141
2011-07-18 21:08 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56449.0469
2011-07-18 21:08 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 56449.0469
2011-07-18 21:08 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56441.3242
2011-07-18 21:08 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56441.3242
2011-07-18 21:08 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56451.4141
2011-07-18 21:08 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56451.4141
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56449.0547
2011-07-18 21:09 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56449.0547
2011-07-18 21:09 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56444.2188
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56444.2188
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56448.8047
2011-07-18 21:09 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56448.8047
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56431.2266
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56431.2266
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.9023
2011-07-18 21:09 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.9023
2011-07-18 21:09 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.1602
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.1602
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.3047
2011-07-18 21:09 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.3047
2011-07-18 21:09 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56429.5703
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56429.5703
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.9727
2011-07-18 21:09 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.9727
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.4844
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.4844
2011-07-18 21:09 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.6016
2011-07-18 21:09 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.6016
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56430.3711
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56430.3711
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.0312
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.0312
2011-07-18 21:09 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56419.2266
2011-07-18 21:09 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 56419.2266
2011-07-18 21:09 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.8672
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.8672
2011-07-18 21:10 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.9062
2011-07-18 21:10 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 56428.9062
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.2266
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.2266
2011-07-18 21:10 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 56408.418
2011-07-18 21:10 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56408.418
2011-07-18 21:10 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56418.1133
2011-07-18 21:10 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56418.1133
2011-07-18 21:10 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.9844
2011-07-18 21:10 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.9844
2011-07-18 21:10 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56398.207
2011-07-18 21:10 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56398.207
2011-07-18 21:10 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56398.207
2011-07-18 21:10 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 56398.207
2011-07-18 21:10 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56400.082
2011-07-18 21:10 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56400.082
2011-07-18 21:10 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56416.7812
2011-07-18 21:10 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56416.7812
2011-07-18 21:10 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.8203
2011-07-18 21:10 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.8203
2011-07-18 21:10 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.1094
2011-07-18 21:10 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 56407.1094
2011-07-18 21:10 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.5625
2011-07-18 21:10 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.5625
2011-07-18 21:10 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.4258
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.4258
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.6367
2011-07-18 21:10 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 56424.6367
2011-07-18 21:10 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 56411.082
2011-07-18 21:10 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 56411.082
2011-07-18 21:11 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.0703
2011-07-18 21:11 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.0703
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56415.1836
2011-07-18 21:11 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56415.1836
2011-07-18 21:11 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56434.0078
2011-07-18 21:11 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56434.0078
2011-07-18 21:11 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.7617
2011-07-18 21:11 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.7617
2011-07-18 21:11 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56427.4023
2011-07-18 21:11 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56427.4023
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56430.2734
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56430.2734
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56417.957
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56417.957
2011-07-18 21:11 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.7617
2011-07-18 21:11 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56422.7617
2011-07-18 21:11 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56420.9805
2011-07-18 21:11 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56420.9805
2011-07-18 21:11 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56411.3477
2011-07-18 21:11 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56411.3477
2011-07-18 21:11 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.6836
2011-07-18 21:11 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56412.6836
2011-07-18 21:11 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.7031
2011-07-18 21:11 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56421.7031
2011-07-18 21:11 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56425.1602
2011-07-18 21:11 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56425.1602
2011-07-18 21:11 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.1367
2011-07-18 21:11 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56438.1367
2011-07-18 21:11 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.1562
2011-07-18 21:11 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56433.1562
2011-07-18 21:12 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56425.0703
2011-07-18 21:12 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56425.0703
2011-07-18 21:12 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.6133
2011-07-18 21:12 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56410.6133
2011-07-18 21:12 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56384.75
2011-07-18 21:12 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56384.75
2011-07-18 21:12 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56377.3203
2011-07-18 21:12 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56377.3203
2011-07-18 21:12 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56362.6133
2011-07-18 21:12 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56362.6133
2011-07-18 21:12 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56354.3203
2011-07-18 21:12 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56354.3203
2011-07-18 21:12 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56355.957
2011-07-18 21:12 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56355.957
2011-07-18 21:12 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56348.5078
2011-07-18 21:12 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56348.5078
2011-07-18 21:12 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.2266
2011-07-18 21:12 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.2266
2011-07-18 21:12 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56357.1484
2011-07-18 21:12 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56357.1484
2011-07-18 21:12 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.0664
2011-07-18 21:12 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.0664
2011-07-18 21:12 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56361.332
2011-07-18 21:12 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56361.332
2011-07-18 21:12 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56355.5898
2011-07-18 21:12 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56355.5898
2011-07-18 21:12 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.0664
2011-07-18 21:12 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56349.0664
2011-07-18 21:12 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56354.6992
2011-07-18 21:12 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56354.6992
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56353.6875
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56345.6016
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56345.6016
2011-07-18 21:13 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56345.6016
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56338.0352
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56338.0352
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56325.3203
2011-07-18 21:13 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56325.3203
2011-07-18 21:13 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56325.1172
2011-07-18 21:13 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56325.1172
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56331.5234
2011-07-18 21:13 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56331.5234
2011-07-18 21:13 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56329.4297
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56329.4297
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56318.6328
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56318.6328
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56316.5508
2011-07-18 21:13 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56316.5508
2011-07-18 21:13 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56309.0977
2011-07-18 21:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56309.0977
2011-07-18 21:13 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56298.3477
2011-07-18 21:13 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56298.3477
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56312.5273
2011-07-18 21:13 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56312.5273
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56307.9336
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56307.9336
2011-07-18 21:13 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56288.6719
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56288.6719
2011-07-18 21:13 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.1875
2011-07-18 21:14 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.1875
2011-07-18 21:14 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.8203
2011-07-18 21:14 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.8203
2011-07-18 21:14 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56307.8008
2011-07-18 21:14 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56307.8008
2011-07-18 21:14 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56294.9688
2011-07-18 21:14 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56294.9688
2011-07-18 21:14 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56300.1836
2011-07-18 21:14 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56300.1836
2011-07-18 21:14 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.8359
2011-07-18 21:14 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.8359
2011-07-18 21:14 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.2031
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.2031
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56328.6445
2011-07-18 21:14 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56328.6445
2011-07-18 21:14 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56337.043
2011-07-18 21:14 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56337.043
2011-07-18 21:14 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56326.3516
2011-07-18 21:14 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56326.3516
2011-07-18 21:14 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56318.7891
2011-07-18 21:14 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56318.7891
2011-07-18 21:14 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56303.3789
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56303.3789
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56294.8828
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56294.8828
2011-07-18 21:14 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56303.6445
2011-07-18 21:14 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56303.6445
2011-07-18 21:14 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.3164
2011-07-18 21:14 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.3164
2011-07-18 21:14 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56298.2695
2011-07-18 21:14 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56298.2695
2011-07-18 21:15 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56290.2422
2011-07-18 21:15 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56290.2422
2011-07-18 21:15 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56293.0156
2011-07-18 21:15 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56293.0156
2011-07-18 21:15 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.3164
2011-07-18 21:15 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56295.3164
2011-07-18 21:15 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.6094
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 56283.2109
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.4961
2011-07-18 21:15 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 56262.5078
2011-07-18 21:15 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 56262.5078
2011-07-18 21:15 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56262.5078
2011-07-18 21:15 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56262.5078
2011-07-18 21:16 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56262.5078
2011-07-18 21:16 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.75
2011-07-18 21:16 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.75
2011-07-18 21:16 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.75
2011-07-18 21:16 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.75
2011-07-18 21:16 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56287.75
2011-07-18 21:16 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56271.1875
2011-07-18 21:16 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56271.1875
2011-07-18 21:16 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56271.1875
2011-07-18 21:16 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56271.1875
2011-07-18 21:16 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56271.1875
2011-07-18 21:16 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56261.1172
2011-07-18 21:16 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56261.1172
2011-07-18 21:16 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56261.1172
2011-07-18 21:16 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56261.1172
2011-07-18 21:16 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56261.1172
2011-07-18 21:16 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.9648
2011-07-18 21:16 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.9648
2011-07-18 21:16 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.9648
2011-07-18 21:16 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.9648
2011-07-18 21:16 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.9648
2011-07-18 21:16 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56310.4922
2011-07-18 21:16 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56310.4922
2011-07-18 21:16 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56310.4922
2011-07-18 21:16 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56310.4922
2011-07-18 21:16 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56310.4922
2011-07-18 21:16 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.7891
2011-07-18 21:16 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.7891
2011-07-18 21:16 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.7891
2011-07-18 21:16 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.7891
2011-07-18 21:16 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56278.7891
2011-07-18 21:17 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.1094
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.1094
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.1094
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.1094
2011-07-18 21:17 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.1094
2011-07-18 21:17 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56272.9258
2011-07-18 21:17 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56272.9258
2011-07-18 21:17 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56272.9258
2011-07-18 21:17 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56272.9258
2011-07-18 21:17 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56272.9258
2011-07-18 21:17 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56255.9883
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56255.9883
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56255.9883
2011-07-18 21:17 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56255.9883
2011-07-18 21:17 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56255.9883
2011-07-18 21:17 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56254.0664
2011-07-18 21:17 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56254.0664
2011-07-18 21:17 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56254.0664
2011-07-18 21:17 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56254.0664
2011-07-18 21:17 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56254.0664
2011-07-18 21:17 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56263.5156
2011-07-18 21:17 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56263.5156
2011-07-18 21:17 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56263.5156
2011-07-18 21:17 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56263.5156
2011-07-18 21:17 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56263.5156
2011-07-18 21:17 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.3867
2011-07-18 21:17 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.3867
2011-07-18 21:17 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.3867
2011-07-18 21:17 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.3867
2011-07-18 21:18 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.3867
2011-07-18 21:18 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 56286.6172
2011-07-18 21:18 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56286.6172
2011-07-18 21:18 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 56286.6172
2011-07-18 21:18 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 56286.6172
2011-07-18 21:18 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 56286.6172
2011-07-18 21:18 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.4492
2011-07-18 21:18 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.4492
2011-07-18 21:18 | 59.994 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.4492
2011-07-18 21:18 | 59.993 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.4492
2011-07-18 21:18 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 56275.4492
2011-07-18 21:18 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 56259.8555
2011-07-18 21:18 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 56259.8555
2011-07-18 21:18 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56259.8555
2011-07-18 21:18 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56259.8555
2011-07-18 21:18 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56259.8555
2011-07-18 21:18 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56247.2383
2011-07-18 21:18 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56247.2383
2011-07-18 21:18 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56247.2383
2011-07-18 21:18 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56247.2383
2011-07-18 21:18 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56247.2383
2011-07-18 21:18 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56253.6094
2011-07-18 21:18 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56253.6094
2011-07-18 21:18 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56253.6094
2011-07-18 21:18 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56253.6094
2011-07-18 21:18 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56253.6094
2011-07-18 21:18 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56237.0039
2011-07-18 21:18 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56237.0039
2011-07-18 21:18 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56237.0039
2011-07-18 21:18 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56237.0039
2011-07-18 21:18 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56237.0039
2011-07-18 21:19 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56245.6406
2011-07-18 21:19 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56245.6406
2011-07-18 21:19 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56245.6406
2011-07-18 21:19 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56245.6406
2011-07-18 21:19 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56245.6406
2011-07-18 21:19 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56234.7227
2011-07-18 21:19 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56234.7227
2011-07-18 21:19 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56234.7227
2011-07-18 21:19 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56234.7227
2011-07-18 21:19 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56234.7227
2011-07-18 21:19 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56222.7969
2011-07-18 21:19 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56222.7969
2011-07-18 21:19 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56222.7969
2011-07-18 21:19 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56222.7969
2011-07-18 21:19 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56222.7969
2011-07-18 21:19 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56205.5117
2011-07-18 21:19 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56205.5117
2011-07-18 21:19 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56205.5117
2011-07-18 21:19 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56205.5117
2011-07-18 21:19 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56205.5117
2011-07-18 21:19 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56216.168
2011-07-18 21:19 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56216.168
2011-07-18 21:19 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56216.168
2011-07-18 21:19 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56216.168
2011-07-18 21:19 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56216.168
2011-07-18 21:19 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56203.9336
2011-07-18 21:19 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56203.9336
2011-07-18 21:19 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56203.9336
2011-07-18 21:19 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56203.9336
2011-07-18 21:20 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56203.9336
2011-07-18 21:20 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.125
2011-07-18 21:20 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.125
2011-07-18 21:20 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.125
2011-07-18 21:20 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.125
2011-07-18 21:20 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.125
2011-07-18 21:20 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 56181.918
2011-07-18 21:20 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 56181.918
2011-07-18 21:20 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56181.918
2011-07-18 21:20 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56181.918
2011-07-18 21:20 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56181.918
2011-07-18 21:20 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56187.3359
2011-07-18 21:20 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56187.3359
2011-07-18 21:20 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56187.3359
2011-07-18 21:20 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56187.3359
2011-07-18 21:20 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56187.3359
2011-07-18 21:20 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56197.918
2011-07-18 21:20 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56197.918
2011-07-18 21:20 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56197.918
2011-07-18 21:20 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56197.918
2011-07-18 21:20 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56197.918
2011-07-18 21:20 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.2266
2011-07-18 21:20 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.2266
2011-07-18 21:20 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.2266
2011-07-18 21:20 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.2266
2011-07-18 21:20 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56200.2266
2011-07-18 21:20 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 56147.082
2011-07-18 21:20 | 60.028 | 0 |  | 0 | 0 |  |  |  | -653 | 56147.082
2011-07-18 21:20 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56147.082
2011-07-18 21:20 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56147.082
2011-07-18 21:20 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56147.082
2011-07-18 21:21 | 60.026 | 0 |  | 0 | 0 |  |  |  | -653 | 56110.3555
2011-07-18 21:21 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56110.3555
2011-07-18 21:21 | 60.027 | 0 |  | 0 | 0 |  |  |  | -653 | 56110.3555
2011-07-18 21:21 | 60.029 | 0 |  | 0 | 0 |  |  |  | -653 | 56110.3555
2011-07-18 21:21 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 56110.3555
2011-07-18 21:21 | 60.03 | 0 |  | 0 | 0 |  |  |  | -653 | 56114.0039
2011-07-18 21:21 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56114.0039
2011-07-18 21:21 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56114.0039
2011-07-18 21:21 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56114.0039
2011-07-18 21:21 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56114.0039
2011-07-18 21:21 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56075.3086
2011-07-18 21:21 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56075.3086
2011-07-18 21:21 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 56075.3086
2011-07-18 21:21 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56075.3086
2011-07-18 21:21 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56075.3086
2011-07-18 21:21 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56090.1758
2011-07-18 21:21 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 56090.1758
2011-07-18 21:21 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56090.1758
2011-07-18 21:21 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56090.1758
2011-07-18 21:21 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56090.1758
2011-07-18 21:21 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56087.0469
2011-07-18 21:21 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56087.0469
2011-07-18 21:21 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56087.0469
2011-07-18 21:21 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 56087.0469
2011-07-18 21:21 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56087.0469
2011-07-18 21:21 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.7344
2011-07-18 21:21 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.7344
2011-07-18 21:21 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.7344
2011-07-18 21:21 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.7344
2011-07-18 21:22 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.7344
2011-07-18 21:22 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.3086
2011-07-18 21:22 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.3086
2011-07-18 21:22 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.3086
2011-07-18 21:22 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.3086
2011-07-18 21:22 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 56077.3086
2011-07-18 21:22 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 56076.293
2011-07-18 21:22 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 56076.293
2011-07-18 21:22 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56076.293
2011-07-18 21:22 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 56076.293
2011-07-18 21:22 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 56076.293
2011-07-18 21:22 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56056.7344
2011-07-18 21:22 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 56056.7344
2011-07-18 21:22 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56056.7344
2011-07-18 21:22 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56056.7344
2011-07-18 21:22 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 56056.7344
2011-07-18 21:22 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56049.5547
2011-07-18 21:22 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 56049.5547
2011-07-18 21:22 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56049.5547
2011-07-18 21:22 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56049.5547
2011-07-18 21:22 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56049.5547
2011-07-18 21:22 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 56016.8086
2011-07-18 21:22 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 56016.8086
2011-07-18 21:22 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56016.8086
2011-07-18 21:22 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56016.8086
2011-07-18 21:22 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56016.8086
2011-07-18 21:22 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56044.8438
2011-07-18 21:22 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56044.8438
2011-07-18 21:22 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56044.8438
2011-07-18 21:22 | 60.025 | 0 |  | 0 | 0 |  |  |  | -653 | 56044.8438
2011-07-18 21:22 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 56044.8438
2011-07-18 21:23 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56023.7969
2011-07-18 21:23 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56023.7969
2011-07-18 21:23 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 56023.7969
2011-07-18 21:23 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 56023.7969
2011-07-18 21:23 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 56023.7969
2011-07-18 21:23 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 55979.9375
2011-07-18 21:23 | 60.023 | 0 |  | 0 | 0 |  |  |  | -653 | 55979.9375
2011-07-18 21:23 | 60.024 | 0 |  | 0 | 0 |  |  |  | -653 | 55979.9375
2011-07-18 21:23 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 55979.9375
2011-07-18 21:23 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 55979.9375
2011-07-18 21:23 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 55950.6445
2011-07-18 21:23 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 55950.6445
2011-07-18 21:23 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55950.6445
2011-07-18 21:23 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 55950.6445
2011-07-18 21:23 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 55950.6445
2011-07-18 21:23 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55934.2656
2011-07-18 21:23 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55934.2656
2011-07-18 21:23 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 55934.2656
2011-07-18 21:23 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 55934.2656
2011-07-18 21:23 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55934.2656
2011-07-18 21:23 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55953.2422
2011-07-18 21:23 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55953.2422
2011-07-18 21:23 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55953.2422
2011-07-18 21:23 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 55953.2422
2011-07-18 21:23 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55953.2422
2011-07-18 21:23 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55940.8633
2011-07-18 21:23 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 55940.8633
2011-07-18 21:23 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55940.8633
2011-07-18 21:23 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55940.8633
2011-07-18 21:24 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55940.8633
2011-07-18 21:24 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55935.2539
2011-07-18 21:24 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55935.2539
2011-07-18 21:24 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55935.2539
2011-07-18 21:24 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 55935.2539
2011-07-18 21:24 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 55935.2539
2011-07-18 21:24 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55918.1289
2011-07-18 21:24 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55918.1289
2011-07-18 21:24 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55918.1289
2011-07-18 21:24 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55918.1289
2011-07-18 21:24 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55918.1289
2011-07-18 21:24 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55900.6289
2011-07-18 21:24 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55900.6289
2011-07-18 21:24 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 55900.6289
2011-07-18 21:24 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 55900.6289
2011-07-18 21:24 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 55900.6289
2011-07-18 21:24 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 55903.2969
2011-07-18 21:24 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 55903.2969
2011-07-18 21:24 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 55903.2969
2011-07-18 21:24 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 55903.2969
2011-07-18 21:24 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 55903.2969
2011-07-18 21:24 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4414
2011-07-18 21:24 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4414
2011-07-18 21:24 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4414
2011-07-18 21:24 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4414
2011-07-18 21:24 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4414
2011-07-18 21:24 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55884.4922
2011-07-18 21:24 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55884.4922
2011-07-18 21:24 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 55884.4922
2011-07-18 21:24 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 55884.4922
2011-07-18 21:24 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55884.4922
2011-07-18 21:25 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55860.1328
2011-07-18 21:25 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55860.1328
2011-07-18 21:25 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 55860.1328
2011-07-18 21:25 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 55860.1328
2011-07-18 21:25 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 55860.1328
2011-07-18 21:25 | 59.975 | 0 |  | 0 | 0 |  |  |  | -653 | 55848.3789
2011-07-18 21:25 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 55848.3789
2011-07-18 21:25 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 55848.3789
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55848.3789
2011-07-18 21:25 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 55848.3789
2011-07-18 21:25 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 55872.375
2011-07-18 21:25 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 55872.375
2011-07-18 21:25 | 59.968 | 0 |  | 0 | 0 |  |  |  | -653 | 55872.375
2011-07-18 21:25 | 59.968 | 0 |  | 0 | 0 |  |  |  | -653 | 55872.375
2011-07-18 21:25 | 59.97 | 0 |  | 0 | 0 |  |  |  | -653 | 55872.375
2011-07-18 21:25 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 55877.8555
2011-07-18 21:25 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 55877.8555
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55877.8555
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55877.8555
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55877.8555
2011-07-18 21:25 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4648
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4648
2011-07-18 21:25 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4648
2011-07-18 21:25 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4648
2011-07-18 21:25 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55871.4648
2011-07-18 21:25 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55864.7266
2011-07-18 21:25 | 59.973 | 0 |  | 0 | 0 |  |  |  | -653 | 55864.7266
2011-07-18 21:25 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 55864.7266
2011-07-18 21:25 | 59.971 | 0 |  | 0 | 0 |  |  |  | -653 | 55864.7266
2011-07-18 21:26 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 55864.7266
2011-07-18 21:26 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 55853.1016
2011-07-18 21:26 | 59.972 | 0 |  | 0 | 0 |  |  |  | -653 | 55853.1016
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55853.1016
2011-07-18 21:26 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55853.1016
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55853.1016
2011-07-18 21:26 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 55855.3047
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55855.3047
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55855.3047
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55855.3047
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55855.3047
2011-07-18 21:26 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55868.668
2011-07-18 21:26 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 55868.668
2011-07-18 21:26 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 55868.668
2011-07-18 21:26 | 59.977 | 0 |  | 0 | 0 |  |  |  | -653 | 55868.668
2011-07-18 21:26 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55868.668
2011-07-18 21:26 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 55869.832
2011-07-18 21:26 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 55869.832
2011-07-18 21:26 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 55869.832
2011-07-18 21:26 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 55869.832
2011-07-18 21:26 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 55869.832
2011-07-18 21:26 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.5781
2011-07-18 21:26 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.5781
2011-07-18 21:26 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.5781
2011-07-18 21:26 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.5781
2011-07-18 21:26 | 59.997 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.5781
2011-07-18 21:26 | 59.995 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.918
2011-07-18 21:26 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.918
2011-07-18 21:26 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.918
2011-07-18 21:26 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.918
2011-07-18 21:26 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55854.918
2011-07-18 21:27 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 55820.8906
2011-07-18 21:27 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55820.8906
2011-07-18 21:27 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55820.8906
2011-07-18 21:27 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 55820.8906
2011-07-18 21:27 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55820.8906
2011-07-18 21:27 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55845.9258
2011-07-18 21:27 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55845.9258
2011-07-18 21:27 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55845.9258
2011-07-18 21:27 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55845.9258
2011-07-18 21:27 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55845.9258
2011-07-18 21:27 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55841.3359
2011-07-18 21:27 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55841.3359
2011-07-18 21:27 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 55841.3359
2011-07-18 21:27 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55841.3359
2011-07-18 21:27 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55841.3359
2011-07-18 21:27 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55830.9492
2011-07-18 21:27 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55830.9492
2011-07-18 21:27 | 60.004 | 0 |  | 0 | 0 |  |  |  | -653 | 55830.9492
2011-07-18 21:27 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 55830.9492
2011-07-18 21:27 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55830.9492
2011-07-18 21:27 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 55816.5156
2011-07-18 21:27 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 55816.5156
2011-07-18 21:27 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 55816.5156
2011-07-18 21:27 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 55816.5156
2011-07-18 21:27 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55816.5156
2011-07-18 21:27 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55811.9453
2011-07-18 21:27 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 55811.9453
2011-07-18 21:27 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 55811.9453
2011-07-18 21:27 | 60.019 | 0 |  | 0 | 0 |  |  |  | -653 | 55811.9453
2011-07-18 21:27 | 60.016 | 0 |  | 0 | 0 |  |  |  | -653 | 55811.9453
2011-07-18 21:28 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 55818.7812
2011-07-18 21:28 | 60.014 | 0 |  | 0 | 0 |  |  |  | -653 | 55818.7812
2011-07-18 21:28 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55818.7812
2011-07-18 21:28 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 55818.7812
2011-07-18 21:28 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 55818.7812
2011-07-18 21:28 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 55815.8359
2011-07-18 21:28 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55815.8359
2011-07-18 21:28 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55815.8359
2011-07-18 21:28 | 60.015 | 0 |  | 0 | 0 |  |  |  | -653 | 55815.8359
2011-07-18 21:28 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55815.8359
2011-07-18 21:28 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55787.8438
2011-07-18 21:28 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 55787.8438
2011-07-18 21:28 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 55787.8438
2011-07-18 21:28 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55787.8438
2011-07-18 21:28 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 55787.8438
2011-07-18 21:28 | 60.007 | 0 |  | 0 | 0 |  |  |  | -653 | 55782.082
2011-07-18 21:28 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55782.082
2011-07-18 21:28 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 55782.082
2011-07-18 21:28 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 55782.082
2011-07-18 21:28 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 55782.082
2011-07-18 21:28 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 55755.6719
2011-07-18 21:28 | 60.008 | 0 |  | 0 | 0 |  |  |  | -653 | 55755.6719
2011-07-18 21:28 | 60.006 | 0 |  | 0 | 0 |  |  |  | -653 | 55755.6719
2011-07-18 21:28 | 60.005 | 0 |  | 0 | 0 |  |  |  | -653 | 55755.6719
2011-07-18 21:28 | 60.003 | 0 |  | 0 | 0 |  |  |  | -653 | 55755.6719
2011-07-18 21:28 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 55761.6562
2011-07-18 21:28 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55761.6562
2011-07-18 21:28 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 55761.6562
2011-07-18 21:28 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 55761.6562
2011-07-18 21:28 | 59.996 | 0 |  | 0 | 0 |  |  |  | -653 | 55761.6562
2011-07-18 21:29 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 55733.1094
2011-07-18 21:29 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 55733.1094
2011-07-18 21:29 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 55733.1094
2011-07-18 21:29 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 55733.1094
2011-07-18 21:29 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 55733.1094
2011-07-18 21:29 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 55732.9297
2011-07-18 21:29 | 59.976 | 0 |  | 0 | 0 |  |  |  | -653 | 55732.9297
2011-07-18 21:29 | 59.974 | 0 |  | 0 | 0 |  |  |  | -653 | 55732.9297
2011-07-18 21:29 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55732.9297
2011-07-18 21:29 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 55732.9297
2011-07-18 21:29 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 55742.2227
2011-07-18 21:29 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 55742.2227
2011-07-18 21:29 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 55742.2227
2011-07-18 21:29 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 55742.2227
2011-07-18 21:29 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 55742.2227
2011-07-18 21:29 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55721.2773
2011-07-18 21:29 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 55721.2773
2011-07-18 21:29 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 55721.2773
2011-07-18 21:29 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 55721.2773
2011-07-18 21:29 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 55721.2773
2011-07-18 21:29 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 55691.0859
2011-07-18 21:29 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 55691.0859
2011-07-18 21:29 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 55691.0859
2011-07-18 21:29 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 55691.0859
2011-07-18 21:29 | 59.982 | 0 |  | 0 | 0 |  |  |  | -653 | 55691.0859
2011-07-18 21:29 | 59.981 | 0 |  | 0 | 0 |  |  |  | -653 | 55699.6719
2011-07-18 21:29 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 55699.6719
2011-07-18 21:29 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 55699.6719
2011-07-18 21:29 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 55699.6719
2011-07-18 21:30 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 55699.6719
2011-07-18 21:30 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 55679.7227
2011-07-18 21:30 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 55679.7227
2011-07-18 21:30 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 55679.7227
2011-07-18 21:30 | 59.984 | 0 |  | 0 | 0 |  |  |  | -653 | 55679.7227
2011-07-18 21:30 | 59.983 | 0 |  | 0 | 0 |  |  |  | -653 | 55679.7227
2011-07-18 21:30 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 55654.9805
2011-07-18 21:30 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 55654.9805
2011-07-18 21:30 | 59.988 | 0 |  | 0 | 0 |  |  |  | -653 | 55654.9805
2011-07-18 21:30 | 59.987 | 0 |  | 0 | 0 |  |  |  | -653 | 55654.9805
2011-07-18 21:30 | 59.985 | 0 |  | 0 | 0 |  |  |  | -653 | 55654.9805
2011-07-18 21:30 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 55649.3555
2011-07-18 21:30 | 59.986 | 0 |  | 0 | 0 |  |  |  | -653 | 55649.3555
2011-07-18 21:30 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 55649.3555
2011-07-18 21:30 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 55649.3555
2011-07-18 21:30 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 55649.3555
2011-07-18 21:30 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 55652.0039
2011-07-18 21:30 | 59.992 | 0 |  | 0 | 0 |  |  |  | -653 | 55652.0039
2011-07-18 21:30 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55652.0039
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55652.0039
2011-07-18 21:30 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 55656.6094
2011-07-18 21:30 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 55639.1562
2011-07-18 21:30 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 55639.1562
2011-07-18 21:30 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55639.1562
2011-07-18 21:30 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55639.1562
2011-07-18 21:31 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 55639.1562
2011-07-18 21:31 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55612.9805
2011-07-18 21:31 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55612.9805
2011-07-18 21:31 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 55612.9805
2011-07-18 21:31 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 55612.9805
2011-07-18 21:31 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 55612.9805
2011-07-18 21:31 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 55610.4688
2011-07-18 21:31 | 60.012 | 0 |  | 0 | 0 |  |  |  | -653 | 55610.4688
2011-07-18 21:31 | 60.013 | 0 |  | 0 | 0 |  |  |  | -653 | 55610.4688
2011-07-18 21:31 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 55610.4688
2011-07-18 21:31 | 60.017 | 0 |  | 0 | 0 |  |  |  | -653 | 55610.4688
2011-07-18 21:31 | 60.018 | 0 |  | 0 | 0 |  |  |  | -653 | 55625.6641
2011-07-18 21:31 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 55625.6641
2011-07-18 21:31 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 55625.6641
2011-07-18 21:31 | 60.023 | 0 |  | 0 | 0 |  |  |  |  | 55625.6641
2011-07-18 21:31 | 60.023 | 0 |  | 0 | 0 |  |  |  |  | 55625.6641
2011-07-18 21:31 | 60.023 | 0 |  | 0 | 0 |  |  |  |  | 55610.6523
2011-07-18 21:31 | 60.022 | 0 |  | 0 | 0 |  |  |  |  | 55610.6523
2011-07-18 21:31 | 60.022 | 0 |  | 0 | 0 |  |  |  |  | 55610.6523
2011-07-18 21:31 | 60.019 | 0 |  | 0 | 0 |  |  |  |  | 55610.6523
2011-07-18 21:31 | 60.018 | 0 |  | 0 | 0 |  |  |  |  | 55610.6523
2011-07-18 21:31 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55615.1211
2011-07-18 21:31 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55615.1211
2011-07-18 21:31 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55615.1211
2011-07-18 21:31 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55615.1211
2011-07-18 21:31 | 60.018 | 0 |  | 0 | 0 |  |  |  |  | 55615.1211
2011-07-18 21:31 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55608.6289
2011-07-18 21:31 | 60.021 | 0 |  | 0 | 0 |  |  |  |  | 55608.6289
2011-07-18 21:31 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55608.6289
2011-07-18 21:31 | 60.018 | 0 |  | 0 | 0 |  |  |  |  | 55608.6289
2011-07-18 21:32 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55608.6289
2011-07-18 21:32 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55575.7266
2011-07-18 21:32 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55575.7266
2011-07-18 21:32 | 60.022 | 0 |  | 0 | 0 |  |  |  |  | 55575.7266
2011-07-18 21:32 | 60.021 | 0 |  | 0 | 0 |  |  |  |  | 55575.7266
2011-07-18 21:32 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55575.7266
2011-07-18 21:32 | 60.019 | 0 |  | 0 | 0 |  |  |  |  | 55553.668
2011-07-18 21:32 | 60.019 | 0 |  | 0 | 0 |  |  |  |  | 55553.668
2011-07-18 21:32 | 60.018 | 0 |  | 0 | 0 |  |  |  |  | 55553.668
2011-07-18 21:32 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55553.668
2011-07-18 21:32 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55553.668
2011-07-18 21:32 | 60.02 | 0 |  | 0 | 0 |  |  |  |  | 55547.6289
2011-07-18 21:32 | 60.019 | 0 |  | 0 | 0 |  |  |  |  | 55547.6289
2011-07-18 21:32 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55547.6289
2011-07-18 21:32 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55547.6289
2011-07-18 21:32 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55547.6289
2011-07-18 21:32 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55537.4141
2011-07-18 21:32 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55537.4141
2011-07-18 21:32 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55537.4141
2011-07-18 21:32 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55537.4141
2011-07-18 21:32 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55537.4141
2011-07-18 21:32 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55530.0234
2011-07-18 21:32 | 60.01 | 0 |  | 0 | 0 |  |  |  |  | 55530.0234
2011-07-18 21:32 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55530.0234
2011-07-18 21:32 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55530.0234
2011-07-18 21:32 | 60.007 | 0 |  | 0 | 0 |  |  |  |  | 55530.0234
2011-07-18 21:32 | 60.006 | 0 |  | 0 | 0 |  |  |  |  | 55517.3398
2011-07-18 21:32 | 60.004 | 0 |  | 0 | 0 |  |  |  |  | 55517.3398
2011-07-18 21:32 | 60.005 | 0 |  | 0 | 0 |  |  |  |  | 55517.3398
2011-07-18 21:32 | 60.005 | 0 |  | 0 | 0 |  |  |  |  | 55517.3398
2011-07-18 21:32 | 60.006 | 0 |  | 0 | 0 |  |  |  |  | 55517.3398
2011-07-18 21:33 | 60.007 | 0 |  | 0 | 0 |  |  |  |  | 55523.4062
2011-07-18 21:33 | 60.007 | 0 |  | 0 | 0 |  |  |  |  | 55523.4062
2011-07-18 21:33 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55523.4062
2011-07-18 21:33 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55523.4062
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55523.4062
2011-07-18 21:33 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55494.2461
2011-07-18 21:33 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55494.2461
2011-07-18 21:33 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55494.2461
2011-07-18 21:33 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55494.2461
2011-07-18 21:33 | 60.019 | 0 |  | 0 | 0 |  |  |  |  | 55494.2461
2011-07-18 21:33 | 60.018 | 0 |  | 0 | 0 |  |  |  |  | 55513.8672
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55513.8672
2011-07-18 21:33 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55513.8672
2011-07-18 21:33 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55513.8672
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55513.8672
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55492.5586
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55492.5586
2011-07-18 21:33 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55492.5586
2011-07-18 21:33 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55492.5586
2011-07-18 21:33 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55492.5586
2011-07-18 21:33 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55486.4023
2011-07-18 21:33 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55486.4023
2011-07-18 21:33 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55486.4023
2011-07-18 21:33 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55486.4023
2011-07-18 21:33 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55486.4023
2011-07-18 21:33 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55473.2539
2011-07-18 21:33 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55473.2539
2011-07-18 21:33 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55473.2539
2011-07-18 21:33 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55473.2539
2011-07-18 21:34 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55473.2539
2011-07-18 21:34 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55456.9062
2011-07-18 21:34 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55456.9062
2011-07-18 21:34 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55456.9062
2011-07-18 21:34 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55456.9062
2011-07-18 21:34 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55456.9062
2011-07-18 21:34 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55459.3438
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55459.3438
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55459.3438
2011-07-18 21:34 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55459.3438
2011-07-18 21:34 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55459.3438
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55426.8594
2011-07-18 21:34 | 60.017 | 0 |  | 0 | 0 |  |  |  |  | 55426.8594
2011-07-18 21:34 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55426.8594
2011-07-18 21:34 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55426.8594
2011-07-18 21:34 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55426.8594
2011-07-18 21:34 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55430.1289
2011-07-18 21:34 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55430.1289
2011-07-18 21:34 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55430.1289
2011-07-18 21:34 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55430.1289
2011-07-18 21:34 | 60.01 | 0 |  | 0 | 0 |  |  |  |  | 55430.1289
2011-07-18 21:34 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55394.6445
2011-07-18 21:34 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55394.6445
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55394.6445
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55394.6445
2011-07-18 21:34 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55394.6445
2011-07-18 21:34 | 60.016 | 0 |  | 0 | 0 |  |  |  |  | 55386.9453
2011-07-18 21:34 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55386.9453
2011-07-18 21:34 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55386.9453
2011-07-18 21:34 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55386.9453
2011-07-18 21:34 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55386.9453
2011-07-18 21:35 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55390.6445
2011-07-18 21:35 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55390.6445
2011-07-18 21:35 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 55390.6445
2011-07-18 21:35 | 60.012 | 0 |  | 0 | 0 |  |  |  |  | 55390.6445
2011-07-18 21:35 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55390.6445
2011-07-18 21:35 | 60.015 | 0 |  | 0 | 0 |  |  |  |  | 55376.8828
2011-07-18 21:35 | 60.014 | 0 |  | 0 | 0 |  |  |  |  | 55376.8828
2011-07-18 21:35 | 60.013 | 0 |  | 0 | 0 |  |  |  |  | 55376.8828
2011-07-18 21:35 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 55376.8828
2011-07-18 21:35 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55376.8828
2011-07-18 21:35 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55370.1406
2011-07-18 21:35 | 60.008 | 0 |  | 0 | 0 |  |  |  |  | 55370.1406
2011-07-18 21:35 | 60.005 | 0 |  | 0 | 0 |  |  |  |  | 55370.1406
2011-07-18 21:35 | 60.004 | 0 |  | 0 | 0 |  |  |  |  | 55370.1406
2011-07-18 21:35 | 60.005 | 0 |  | 0 | 0 |  |  |  |  | 55370.1406

## Entry Data
Balancing Authority Name: | ERCOT
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -286
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40742.8685
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708
Step 4. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 5. | Paste data into FRS Form 1 in the appropriate row on the "BA Event Data" worksheet.
Step 6. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2011-07-18 20:51 | Date yymmdd
| 40742.8685 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Copy Data for Pasting into Form 1
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")

## IPFR
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2011-07-18 20:51 |  |  | Balancing Authority | ERCOT | [10 empty] | A Point | 40742.8685 |  |  |  |  | A Point | 40742.8685 | [13 empty] | Non-Conforming Load sign convention | - | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2011-07-18 20:51 | [12 empty] | Date: | 2011-07-18 20:51 | [12 empty] | Date: | 2011-07-18 20:51 | [12 empty] | Date: | 2011-07-18 20:51 | [12 empty] | Date: | 2011-07-18 20:51
[5 empty] | Time of T(0) | 40742.8685 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.007 | 40742.8685 |  |  |  | FPointA | 60.007 | 40742.8685 | [26 empty] | Time of T(0) | 40742.8685 | [12 empty] | Time of T(0) | 40742.8685 | [12 empty] | Time of T(0) | 40742.8685 | [12 empty] | Time of T(0) | 40742.8685 | [12 empty] | Time of T(0) | 40742.8685
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708 |  |  | Capacity @ Droop for Minimum Performance | 8580 | MW | [9 empty] | A Value | 60.0084 |  |  |  |  | A Value | 60.0084 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40742.8708
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.866 | #N/A |  |  |  | C Value | 59.866 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0084 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8807 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.14237 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8751 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8799 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8802 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8804 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8807 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.12767 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -418.7207 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.13323 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.12852 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.12819 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.12793 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.12767 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW |  | Frequency Response Obligation (FRO) | -286 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | #N/A | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 596.1496 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 0 | MW | [13 empty] | C Value Maximum Resource Loss | 596.1496 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 0 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8751 |  | 59.8799 |  | 59.8807 |  | 59.8804 |  | 59.8807 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -596.1496 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | 5.5467 | MW | [19 empty] | Delta FB | -0.13323 | -448.2121 | -0.12852 | -463.9878 | -0.12767 | -465.0911 | -0.12793 | -466.0866 | -0.12767 | -467.0124 | [18 empty] | Net Total Adjustments | 0 | MW | [11 empty] | Net Total Adjustments | 0 | MW | [11 empty] | Net Total Adjustments | 0 | MW | [11 empty] | Net Total Adjustments | 0 | MW | [11 empty] | Net Total Adjustments | 0 | MW
[5 empty] | EPFR Pre-Perturbation Average | -23.953 | MW | [19 empty] | Slope B dF/dT | -0.0066616 |  | -0.0064259 |  | -0.0063835 |  | -0.0063965 |  | -0.0063835 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -23.953 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -23.953 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -23.953 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -23.953 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -23.953 | MW
[5 empty] | EPFR Post-Perturbation Average | 341.1805 | MW | [19 empty] | RatioB-C | 93.5791 |  | 90.2678 |  | 89.6716 |  | 89.8552 |  | 89.6716 | [19 empty] | EPFR for FRO Post-Perturbation Average | 357.0917 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 343.6084 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 342.6792 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 341.9284 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 341.1805 | MW
[5 empty] | EPFR Delta | 365.1335 | MW |  | TC (frequency response filter constant) | 1 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | 0.026158 |  | 0.021443 |  | 0.020594 |  | 0.020856 |  | 0.020594 | [19 empty] | EPFR for FRO Delta | 381.0446 | MW | [11 empty] | EPFR for FRO Delta | 367.5614 | MW | [11 empty] | EPFR for FRO Delta | 366.6322 | MW | [11 empty] | EPFR for FRO Delta | 365.8813 | MW | [11 empty] | EPFR for FRO Delta | 365.1335 | MW
[21 empty] | Tzero | 40742.8685 | [33 empty] | EPFR for FRO Adjusted | 381.0446 | MW | [11 empty] | EPFR for FRO Adjusted | 367.5614 | MW | [11 empty] | EPFR for FRO Adjusted | 366.6322 | MW | [11 empty] | EPFR for FRO Adjusted | 365.8813 | MW | [11 empty] | EPFR for FRO Adjusted | 365.1335 | MW
[21 empty] | FT+4 | 59.918 | [33 empty] | Pre JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.866 | [33 empty] | Pre Non-Conforming Load MW | 0 |  |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 0 |  |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz
[9 empty] | 0 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.878 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -54.6898 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -54.6898 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -54.6898 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -54.6898 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -54.6898 | MW
[9 empty] | 521.7711 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.894 | [33 empty] | Pre Ramping Units MW | 0 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 815.3177 | MW | [6 empty] | Pre Ramping Units MW | 0 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 784.5325 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 782.4109 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 780.6965 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 778.9891 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 370.6802 | MW |  | 312.9908 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | 0 |  |  |  | EPFR for Bias Setting Delta | 870.0075 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 |  |  |  | EPFR for Bias Setting Delta | 839.2223 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 837.1008 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 835.3864 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 833.6789 | MW
[9 empty] | 602.7012 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 0 |  |  |  | Primary Frequency Response Delivery of Bias | -68.52% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 |  |  |  | Primary Frequency Response Delivery of Bias | -71.04% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -71.22% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -71.36% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -71.51%
[9 empty] | -625.5796 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 0 | [12 empty] | Sum of Pre Perturbation Adjustments | 0 | [12 empty] | Sum of Pre Perturbation Adjustments | 0 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 0 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 0 | MW
[9 empty] | 0:03 | Event Duration (h:mm:ss)
[9 empty] | Yes | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 596.1496 | [33 empty] | Post JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation BA Load | 57050.2559 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation BA Load | 57050.2559 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 57050.2559 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 57050.2559 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 57050.2559 | MW
[9 empty] | 544.6495 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | 0 |  |  |  | Post-Perturbation BA Load | 56857.5725 | MW | [6 empty] | Post Non-Conforming Load MW | 0 |  |  |  | Post-Perturbation BA Load | 56872.1323 | MW | [6 empty] | Post Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation BA Load | 56878.6644 | MW | [6 empty] | Post Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation BA Load | 56882.8589 | MW | [6 empty] | Post Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation BA Load | 56884.0016 | MW
[9 empty] | 22.8783 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 596.1496 | [33 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -192.6833 | MW | [6 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -178.1236 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -171.5914 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -167.3969 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -166.2543 | MW
[9 empty] | Yes | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 0 |  |  |  | Load Dampening Frequency Response | -144.622 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 |  |  |  | Load Dampening Frequency Response | -138.5982 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -133.8539 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -130.8499 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -130.2228 | MW/0.1 Hz
[9 empty] | No | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 0 |  |  |  | Load Dampening % of Total BA Frequency Response | -32.32% | [7 empty] | Post Transferred Frequency Response MW | 0 |  |  |  | Load Dampening % of Total BA Frequency Response | -29.88% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -28.78% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -28.08% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -27.89%
[9 empty] | No | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | -80.9301 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 0 | [12 empty] | Sum of Post Perturbation Adjustments | 0 | [12 empty] | Sum of Post Perturbation Adjustments | 0 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 0 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 0 | MW
[9 empty] | -602.7012 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | 0 | [12 empty] | Net Total Adjustments MW | 0 | [12 empty] | Net Total Adjustments MW | 0 | MW | [11 empty] | Net Total Adjustments MW | 0 | MW | [11 empty] | Net Total Adjustments MW | 0 | MW
[9 empty] | Down | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 1.6506 | P.U. |  | No Evaluation | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 1.5645 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.6219 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.626 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.6294 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 1.6327 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 1.5645 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.6219 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.626 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.6294 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 1.6327 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  | FRO |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual
|  |  | Total | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  | Generation | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Lost | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 596.1496 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40742.8677 | 60.012 | 593.3 |  |  |  | -34.323 | -34.323 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40742.8677 | 60.012 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57058.0938 | -34.323 | T-72 sec | 40742.8677 | [12 empty] | T-72 sec | 40742.8677 | [12 empty] | T-72 sec | 40742.8677 | [12 empty] | T-72 sec | 40742.8677 | [12 empty] | T-72 sec | 40742.8677
T-70 sec | 40742.8677 | 60.01 | 593.3 |  |  |  | -28.5952 | -28.5952 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40742.8677 | 60.01 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57058.0938 | -28.5952 | T-70 sec | 40742.8677 | [12 empty] | T-70 sec | 40742.8677 | [12 empty] | T-70 sec | 40742.8677 | [12 empty] | T-70 sec | 40742.8677 | [12 empty] | T-70 sec | 40742.8677
T-68 sec | 40742.8677 | 60.01 | 593.3 |  |  |  | -28.5952 | -28.5952 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40742.8677 | 60.01 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.5 | -28.5952 | T-68 sec | 40742.8677 | [12 empty] | T-68 sec | 40742.8677 | [12 empty] | T-68 sec | 40742.8677 | [12 empty] | T-68 sec | 40742.8677 | [12 empty] | T-68 sec | 40742.8677
T-66 sec | 40742.8678 | 60.011 | 593.3 |  |  |  | -31.4645 | -31.4645 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40742.8678 | 60.011 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.5 | -31.4645 | T-66 sec | 40742.8678 | [12 empty] | T-66 sec | 40742.8678 | [12 empty] | T-66 sec | 40742.8678 | [12 empty] | T-66 sec | 40742.8678 | [12 empty] | T-66 sec | 40742.8678
T-64 sec | 40742.8678 | 60.011 | 593.3 |  |  |  | -31.4645 | -31.4645 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40742.8678 | 60.011 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.5 | -31.4645 | T-64 sec | 40742.8678 | [12 empty] | T-64 sec | 40742.8678 | [12 empty] | T-64 sec | 40742.8678 | [12 empty] | T-64 sec | 40742.8678 | [12 empty] | T-64 sec | 40742.8678
T-62 sec | 40742.8678 | 60.01 | 593.3 |  |  |  | -28.5952 | -28.5952 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40742.8678 | 60.01 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.5 | -28.5952 | T-62 sec | 40742.8678 | [12 empty] | T-62 sec | 40742.8678 | [12 empty] | T-62 sec | 40742.8678 | [12 empty] | T-62 sec | 40742.8678 | [12 empty] | T-62 sec | 40742.8678
T-60 sec | 40742.8678 | 60.011 | 593.3 |  |  |  | -31.4645 | -31.4645 |  | -0.070462 | 593.3 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40742.8678 | 60.011 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.5 | -31.4645 | T-60 sec | 40742.8678 | [12 empty] | T-60 sec | 40742.8678 | [12 empty] | T-60 sec | 40742.8678 | [12 empty] | T-60 sec | 40742.8678 | [12 empty] | T-60 sec | 40742.8678
T-58 sec | 40742.8678 | 60.011 | 593.3 |  |  |  | -31.4645 | -31.4645 |  | -0.070462 | 593.2295 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40742.8678 | 60.011 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.1172 | -31.4645 | T-58 sec | 40742.8678 | [12 empty] | T-58 sec | 40742.8678 | [12 empty] | T-58 sec | 40742.8678 | [12 empty] | T-58 sec | 40742.8678 | [12 empty] | T-58 sec | 40742.8678
T-56 sec | 40742.8679 | 60.012 | 593.3 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 590.3006 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40742.8679 | 60.012 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.1172 | -34.323 | T-56 sec | 40742.8679 | [12 empty] | T-56 sec | 40742.8679 | [12 empty] | T-56 sec | 40742.8679 | [12 empty] | T-56 sec | 40742.8679 | [12 empty] | T-56 sec | 40742.8679
T-54 sec | 40742.8679 | 60.012 | 593.3 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 590.2302 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40742.8679 | 60.012 | 593.3 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.1172 | -34.323 | T-54 sec | 40742.8679 | [12 empty] | T-54 sec | 40742.8679 | [12 empty] | T-54 sec | 40742.8679 | [12 empty] | T-54 sec | 40742.8679 | [12 empty] | T-54 sec | 40742.8679
T-52 sec | 40742.8679 | 60.011 | 585.6284 |  |  |  | -31.4645 | -31.4645 |  | -0.070462 | 593.0182 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40742.8679 | 60.011 | 585.6284 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57057.2109 | -31.4645 | T-52 sec | 40742.8679 | [12 empty] | T-52 sec | 40742.8679 | [12 empty] | T-52 sec | 40742.8679 | [12 empty] | T-52 sec | 40742.8679 | [12 empty] | T-52 sec | 40742.8679
T-50 sec | 40742.8679 | 60.012 | 585.6284 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 590.0893 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40742.8679 | 60.012 | 585.6284 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57057.2109 | -34.323 | T-50 sec | 40742.8679 | [12 empty] | T-50 sec | 40742.8679 | [12 empty] | T-50 sec | 40742.8679 | [12 empty] | T-50 sec | 40742.8679 | [12 empty] | T-50 sec | 40742.8679
T-48 sec | 40742.868 | 60.013 | 586.143 |  |  |  | -37.1814 | -37.1814 |  | -0.070462 | 587.1604 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40742.868 | 60.013 | 586.143 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57051.7422 | -37.1814 | T-48 sec | 40742.868 | [12 empty] | T-48 sec | 40742.868 | [12 empty] | T-48 sec | 40742.868 | [12 empty] | T-48 sec | 40742.868 | [12 empty] | T-48 sec | 40742.868
T-46 sec | 40742.868 | 60.015 | 586.143 |  |  |  | -42.8983 | -42.8983 |  | -0.070462 | 581.3731 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40742.868 | 60.015 | 586.143 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57051.7422 | -42.8983 | T-46 sec | 40742.868 | [12 empty] | T-46 sec | 40742.868 | [12 empty] | T-46 sec | 40742.868 | [12 empty] | T-46 sec | 40742.868 | [12 empty] | T-46 sec | 40742.868
T-44 sec | 40742.868 | 60.016 | 586.7954 |  |  |  | -45.7567 | -45.7567 |  | -0.070462 | 578.4442 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40742.868 | 60.016 | 586.7954 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57051.7422 | -45.7567 | T-44 sec | 40742.868 | [12 empty] | T-44 sec | 40742.868 | [12 empty] | T-44 sec | 40742.868 | [12 empty] | T-44 sec | 40742.868 | [12 empty] | T-44 sec | 40742.868
T-42 sec | 40742.868 | 60.015 | 586.7954 |  |  |  | -42.8983 | -42.8983 |  | -0.070462 | 581.2321 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40742.868 | 60.015 | 586.7954 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57051.7422 | -42.8983 | T-42 sec | 40742.868 | [12 empty] | T-42 sec | 40742.868 | [12 empty] | T-42 sec | 40742.868 | [12 empty] | T-42 sec | 40742.868 | [12 empty] | T-42 sec | 40742.868
T-40 sec | 40742.8681 | 60.014 | 585.9467 |  |  |  | -40.0398 | -40.0398 |  | -0.070462 | 584.0201 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40742.8681 | 60.014 | 585.9467 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57037.8789 | -40.0398 | T-40 sec | 40742.8681 | [12 empty] | T-40 sec | 40742.8681 | [12 empty] | T-40 sec | 40742.8681 | [12 empty] | T-40 sec | 40742.8681 | [12 empty] | T-40 sec | 40742.8681
T-38 sec | 40742.8681 | 60.013 | 585.9467 |  |  |  | -37.1814 | -37.1814 |  | -0.070462 | 586.8081 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40742.8681 | 60.013 | 585.9467 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57037.8789 | -37.1814 | T-38 sec | 40742.8681 | [12 empty] | T-38 sec | 40742.8681 | [12 empty] | T-38 sec | 40742.8681 | [12 empty] | T-38 sec | 40742.8681 | [12 empty] | T-38 sec | 40742.8681
T-36 sec | 40742.8681 | 60.012 | 585.6723 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 589.596 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40742.8681 | 60.012 | 585.6723 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.4336 | -34.323 | T-36 sec | 40742.8681 | [12 empty] | T-36 sec | 40742.8681 | [12 empty] | T-36 sec | 40742.8681 | [12 empty] | T-36 sec | 40742.8681 | [12 empty] | T-36 sec | 40742.8681
T-34 sec | 40742.8681 | 60.012 | 585.6723 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 589.5256 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40742.8681 | 60.012 | 585.6723 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.4336 | -34.323 | T-34 sec | 40742.8681 | [12 empty] | T-34 sec | 40742.8681 | [12 empty] | T-34 sec | 40742.8681 | [12 empty] | T-34 sec | 40742.8681 | [12 empty] | T-34 sec | 40742.8681
T-32 sec | 40742.8681 | 60.012 | 585.1163 |  |  |  | -34.323 | -34.323 |  | -0.070462 | 589.4551 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40742.8681 | 60.012 | 585.1163 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57029.9219 | -34.323 | T-32 sec | 40742.8681 | [12 empty] | T-32 sec | 40742.8681 | [12 empty] | T-32 sec | 40742.8681 | [12 empty] | T-32 sec | 40742.8681 | [12 empty] | T-32 sec | 40742.8681
T-30 sec | 40742.8682 | 60.013 | 585.1163 |  |  |  | -37.1814 | -37.1814 |  | -0.070462 | 586.5262 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40742.8682 | 60.013 | 585.1163 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57029.9219 | -37.1814 | T-30 sec | 40742.8682 | [12 empty] | T-30 sec | 40742.8682 | [12 empty] | T-30 sec | 40742.8682 | [12 empty] | T-30 sec | 40742.8682 | [12 empty] | T-30 sec | 40742.8682
T-28 sec | 40742.8682 | 60.015 | 584.655 |  |  |  | -42.8983 | -42.8983 |  | -0.070462 | 580.7389 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40742.8682 | 60.015 | 584.655 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57033.7109 | -42.8983 | T-28 sec | 40742.8682 | [12 empty] | T-28 sec | 40742.8682 | [12 empty] | T-28 sec | 40742.8682 | [12 empty] | T-28 sec | 40742.8682 | [12 empty] | T-28 sec | 40742.8682
T-26 sec | 40742.8682 | 60.017 | 584.655 |  |  |  | -48.6151 | -48.6151 |  | -0.070462 | 574.9516 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40742.8682 | 60.017 | 584.655 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57033.7109 | -48.6151 | T-26 sec | 40742.8682 | [12 empty] | T-26 sec | 40742.8682 | [12 empty] | T-26 sec | 40742.8682 | [12 empty] | T-26 sec | 40742.8682 | [12 empty] | T-26 sec | 40742.8682
T-24 sec | 40742.8682 | 60.017 | 585.3073 |  |  |  | -48.6151 | -48.6151 |  | -0.070462 | 574.8811 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40742.8682 | 60.017 | 585.3073 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57035.5586 | -48.6151 | T-24 sec | 40742.8682 | [12 empty] | T-24 sec | 40742.8682 | [12 empty] | T-24 sec | 40742.8682 | [12 empty] | T-24 sec | 40742.8682 | [12 empty] | T-24 sec | 40742.8682
T-22 sec | 40742.8683 | 60.014 | 585.3073 |  |  |  | -40.0398 | -40.0398 |  | -0.070462 | 583.3859 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40742.8683 | 60.014 | 585.3073 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57035.5586 | -40.0398 | T-22 sec | 40742.8683 | [12 empty] | T-22 sec | 40742.8683 | [12 empty] | T-22 sec | 40742.8683 | [12 empty] | T-22 sec | 40742.8683 | [12 empty] | T-22 sec | 40742.8683
T-20 sec | 40742.8683 | 60.015 | 585.2109 |  |  |  | -42.8983 | -42.8983 |  | -0.070462 | 580.457 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40742.8683 | 60.015 | 585.2109 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57020.6016 | -42.8983 | T-20 sec | 40742.8683 | [12 empty] | T-20 sec | 40742.8683 | [12 empty] | T-20 sec | 40742.8683 | [12 empty] | T-20 sec | 40742.8683 | [12 empty] | T-20 sec | 40742.8683
T-18 sec | 40742.8683 | 60.013 | 585.2109 |  |  |  | -37.1814 | -37.1814 |  | -0.070462 | 586.1034 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40742.8683 | 60.013 | 585.2109 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57020.6016 | -37.1814 | T-18 sec | 40742.8683 | [12 empty] | T-18 sec | 40742.8683 | [12 empty] | T-18 sec | 40742.8683 | [12 empty] | T-18 sec | 40742.8683 | [12 empty] | T-18 sec | 40742.8683
T-16 sec | 40742.8683 | 60.012 | 585.9184 | 60.0084 | 596.1496 |  | -34.323 | -34.323 |  | -0.070462 | 588.8914 | [12 empty] | 0 |  |  | T-16 sec | 60.0084 | [9 empty] | T-16 sec | 40742.8683 | 60.012 | 585.9184 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57030.3711 | -34.323 | T-16 sec | 40742.8683 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-16 sec | 40742.8683 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-16 sec | 40742.8683 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-16 sec | 40742.8683 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-16 sec | 40742.8683 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-14 sec | 40742.8684 | 60.011 | 585.9184 | 60.0084 | 596.1496 |  | -31.4645 | -31.4645 |  | -0.070462 | 591.6794 | [12 empty] | 0 |  |  | T-14 sec | 60.0084 | [9 empty] | T-14 sec | 40742.8684 | 60.011 | 585.9184 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57030.3711 | -31.4645 | T-14 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-14 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-14 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-14 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-14 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-12 sec | 40742.8684 | 60.008 | 593.2776 | 60.0084 | 596.1496 |  | -22.8783 | -22.8783 |  | -0.070462 | 600.1951 | [12 empty] | 0 |  |  | T-12 sec | 60.0084 | [9 empty] | T-12 sec | 40742.8684 | 60.008 | 593.2776 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57039.1484 | -22.8783 | T-12 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-12 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-12 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-12 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-12 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-10 sec | 40742.8684 | 60.008 | 593.2776 | 60.0084 | 596.1496 |  | -22.8783 | -22.8783 |  | -0.070462 | 600.1247 | [12 empty] | 0 |  |  | T-10 sec | 60.0084 | [9 empty] | T-10 sec | 40742.8684 | 60.008 | 593.2776 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57039.1484 | -22.8783 | T-10 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-10 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-10 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-10 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-10 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-08 sec | 40742.8684 | 60.007 | 602.7012 | 60.0084 | 596.1496 |  | -20.0199 | -20.0199 |  | -0.070462 | 602.9126 | [12 empty] | 0 |  |  | T-08 sec | 60.0084 | [9 empty] | T-08 sec | 40742.8684 | 60.007 | 602.7012 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.2031 | -20.0199 | T-08 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-08 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-08 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-08 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-08 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-06 sec | 40742.8684 | 60.007 | 602.7012 | 60.0084 | 596.1496 |  | -20.0199 | -20.0199 |  | -0.070462 | 602.8422 | [12 empty] | 0 |  |  | T-06 sec | 60.0084 | [9 empty] | T-06 sec | 40742.8684 | 60.007 | 602.7012 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57042.2031 | -20.0199 | T-06 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-06 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-06 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-06 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-06 sec | 40742.8684 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-04 sec | 40742.8685 | 60.007 | 602.7012 | 60.0084 | 596.1496 |  | -20.0199 | -20.0199 |  | -0.070462 | 602.7717 | [12 empty] | 0 |  |  | T-04 sec | 60.0084 | [9 empty] | T-04 sec | 40742.8685 | 60.007 | 602.7012 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57089.3008 | -20.0199 | T-04 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-04 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-04 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-04 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-04 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T-02 sec | 40742.8685 | 60.007 | 602.7012 | 60.0084 | 596.1496 |  | -20.0199 | -20.0199 |  | -0.070462 | 602.7012 | [12 empty] | 0 |  |  | T-02 sec | 60.0084 | [9 empty] | T-02 sec | 40742.8685 | 60.007 | 602.7012 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57089.3008 | -20.0199 | T-02 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-02 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-02 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-02 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953 |  | T-02 sec | 40742.8685 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -23.953
T+0 sec | 40742.8685 | 59.989 | 0 |  |  |  | 31.4645 | 31.4645 |  | 0 | 654.1857 |  |  |  |  | 596.1496 | [7 empty] | 596.1496 | -3076.6227 |  | T+0 sec | [10 empty] | T+0 sec | 40742.8685 | 59.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56704.1289 | 31.4645 | T+0 sec | 40742.8685 | [12 empty] | T+0 sec | 40742.8685 | [12 empty] | T+0 sec | 40742.8685 | [12 empty] | T+0 sec | 40742.8685 | [12 empty] | T+0 sec | 40742.8685
T+02 sec | 40742.8685 | 59.918 | 0 |  |  |  | 234.5221 | 234.5221 |  | -6.2558 | 850.9875 | 0 | 752.5866 | 622.6507 | 622.6507 | 596.1496 | [7 empty] | 596.1496 | -659.6334 |  | T+02 sec | [10 empty] | T+02 sec | 40742.8685 | 59.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56704.1289 | 234.5221 | T+02 sec | 40742.8685 | [12 empty] | T+02 sec | 40742.8685 | [12 empty] | T+02 sec | 40742.8685 | [12 empty] | T+02 sec | 40742.8685 | [12 empty] | T+02 sec | 40742.8685
T+04 sec | 40742.8686 | 59.918 | 0 |  |  |  | 234.5221 | 234.5221 |  | -6.2558 | 844.7317 | 0 | 783.3016 | 616.3949 | 619.5228 | 596.1496 | [7 empty] | 596.1496 | -659.6334 |  | T+04 sec | [10 empty] | T+04 sec | 40742.8686 | 59.918 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56704.1289 | 234.5221 | T+04 sec | 40742.8686 | [12 empty] | T+04 sec | 40742.8686 | [12 empty] | T+04 sec | 40742.8686 | [12 empty] | T+04 sec | 40742.8686 | [12 empty] | T+04 sec | 40742.8686
T+06 sec | 40742.8686 | 59.88 | 0 |  |  |  | 343.1969 | 343.1969 |  | -6.2558 | 947.1508 | 0 | 824.2639 | 610.1392 | 616.3949 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 |  | T+06 sec | [10 empty] | T+06 sec | 40742.8686 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56763.9688 | 343.1969 | T+06 sec | 40742.8686 | [12 empty] | T+06 sec | 40742.8686 | [12 empty] | T+06 sec | 40742.8686 | [12 empty] | T+06 sec | 40742.8686 | [12 empty] | T+06 sec | 40742.8686
T+08 sec | 40742.8686 | 59.872 | 0 |  |  |  | 366.0753 | 366.0753 |  | -6.2558 | 963.7734 | 0 | 852.1658 | 603.8834 | 613.2671 | 596.1496 | [6 empty] | 0 | 596.1496 | -437.1447 |  | T+08 sec | [10 empty] | T+08 sec | 40742.8686 | 59.872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56763.9688 | 366.0753 | T+08 sec | 40742.8686 | [12 empty] | T+08 sec | 40742.8686 | [12 empty] | T+08 sec | 40742.8686 | [12 empty] | T+08 sec | 40742.8686 | [12 empty] | T+08 sec | 40742.8686
T+10 sec | 40742.8686 | 59.866 | 0 |  |  |  | 383.2368 | 383.2368 |  | -6.2558 | 974.6791 | 0 | 872.5847 | 597.6277 | 610.1392 | 596.1496 | [6 empty] | 0 | 596.1496 | -418.7207 |  | T+10 sec | [10 empty] | T+10 sec | 40742.8686 | 59.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56811.1953 | 383.2368 | T+10 sec | 40742.8686 | [12 empty] | T+10 sec | 40742.8686 | [12 empty] | T+10 sec | 40742.8686 | [12 empty] | T+10 sec | 40742.8686 | [12 empty] | T+10 sec | 40742.8686
T+12 sec | 40742.8687 | 59.867 | 0 |  |  |  | 380.3783 | 380.3783 |  | -6.2558 | 965.565 | 0 | 885.8676 | 591.3719 | 607.0113 | 596.1496 | [6 empty] | 0 | 596.1496 | -421.6809 |  | T+12 sec | 59.8751 | -448.2121 | [8 empty] | T+12 sec | 40742.8687 | 59.867 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56811.1953 | 380.3783 | T+12 sec | 40742.8687 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+12 sec | 40742.8687 | [12 empty] | T+12 sec | 40742.8687 | [12 empty] | T+12 sec | 40742.8687 | [12 empty] | T+12 sec | 40742.8687
T+14 sec | 40742.8687 | 59.868 | 0 |  |  |  | 377.5199 | 377.5199 |  | -6.2558 | 956.4508 | 0 | 894.6905 | 585.1161 | 603.8834 | 596.1496 | [6 empty] | 0 | 596.1496 | -424.6832 |  | T+14 sec | 59.8751 | -448.2121 | [8 empty] | T+14 sec | 40742.8687 | 59.868 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56864.9648 | 377.5199 | T+14 sec | 40742.8687 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+14 sec | 40742.8687 | [12 empty] | T+14 sec | 40742.8687 | [12 empty] | T+14 sec | 40742.8687 | [12 empty] | T+14 sec | 40742.8687
T+16 sec | 40742.8687 | 59.874 | 0 |  |  |  | 360.3584 | 360.3584 |  | -6.2558 | 933.0335 | 0 | 898.9508 | 578.8604 | 600.7555 | 596.1496 | [6 empty] | 0 | 596.1496 | -443.6475 |  | T+16 sec | 59.8751 | -448.2121 | [8 empty] | T+16 sec | 40742.8687 | 59.874 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56864.9648 | 360.3584 | T+16 sec | 40742.8687 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+16 sec | 40742.8687 | [12 empty] | T+16 sec | 40742.8687 | [12 empty] | T+16 sec | 40742.8687 | [12 empty] | T+16 sec | 40742.8687
T+18 sec | 40742.8687 | 59.876 | 0 |  |  |  | 354.6416 | 354.6416 |  | -6.2558 | 921.0609 | 0 | 901.1618 | 572.6046 | 597.6277 | 596.1496 | [6 empty] | 0 | 596.1496 | -450.3467 |  | T+18 sec | 59.8751 | -448.2121 | 59.8799 | -463.9878 |  |  | 59.8804 | -466.0866 |  |  | T+18 sec | 40742.8687 | 59.876 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56863.4336 | 354.6416 | T+18 sec | 40742.8687 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+18 sec | 40742.8687 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+18 sec | 40742.8687 | [12 empty] | T+18 sec | 40742.8687 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+18 sec | 40742.8687
T+20 sec | 40742.8687 | 59.878 | 0 | 59.8807 | 0 |  | 348.9247 | 348.9247 | 966.8298 | -6.2558 | 909.0883 | 0 | 901.8824 | 566.3489 | 594.4998 | 596.1496 | [6 empty] | 0 | 596.1496 | -457.2513 | -467.0124 | T+20 sec | 59.8751 | -448.2121 | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+20 sec | 40742.8687 | 59.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56863.4336 | 348.9247 | T+20 sec | 40742.8687 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+20 sec | 40742.8687 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+20 sec | 40742.8687 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+20 sec | 40742.8687 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+20 sec | 40742.8687 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+22 sec | 40742.8688 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 897.1048 | 0 | 901.4843 | 560.0931 | 591.3719 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+22 sec | 59.8751 | -448.2121 | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+22 sec | 40742.8688 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56867.5078 | 343.1969 | T+22 sec | 40742.8688 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+22 sec | 40742.8688 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+22 sec | 40742.8688 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+22 sec | 40742.8688 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+22 sec | 40742.8688 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+24 sec | 40742.8688 | 59.883 | 0 | 59.8807 | 0 |  | 334.6217 | 334.6217 | 966.8298 | -6.2558 | 882.2737 | 0 | 900.0066 | 553.8374 | 588.244 | 596.1496 | [6 empty] | 0 | 596.1496 | -475.4904 | -467.0124 | T+24 sec | 59.8751 | -448.2121 | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+24 sec | 40742.8688 | 59.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56867.5078 | 334.6217 | T+24 sec | 40742.8688 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56857.5725 | 357.0917 | 977.1943 | T+24 sec | 40742.8688 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+24 sec | 40742.8688 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+24 sec | 40742.8688 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+24 sec | 40742.8688 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+26 sec | 40742.8688 | 59.881 | 0 | 59.8807 | 0 |  | 340.3385 | 340.3385 | 966.8298 | -6.2558 | 881.7348 | 0 | 898.7014 | 547.5816 | 585.1161 | 596.1496 | [6 empty] | 0 | 596.1496 | -468.0285 | -467.0124 | T+26 sec |  |  | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+26 sec | 40742.8688 | 59.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.3594 | 340.3385 | T+26 sec | 40742.8688 | [12 empty] | T+26 sec | 40742.8688 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+26 sec | 40742.8688 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+26 sec | 40742.8688 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+26 sec | 40742.8688 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+28 sec | 40742.8688 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 878.3375 | 0 | 897.3438 | 541.3259 | 581.9883 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+28 sec |  |  | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+28 sec | 40742.8688 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.3594 | 343.1969 | T+28 sec | 40742.8688 | [12 empty] | T+28 sec | 40742.8688 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+28 sec | 40742.8688 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+28 sec | 40742.8688 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+28 sec | 40742.8688 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+30 sec | 40742.8689 | 59.881 | 0 | 59.8807 | 0 |  | 340.3385 | 340.3385 | 966.8298 | -6.2558 | 869.2233 | 0 | 895.5863 | 535.0701 | 578.8604 | 596.1496 | [6 empty] | 0 | 596.1496 | -468.0285 | -467.0124 | T+30 sec |  |  | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+30 sec | 40742.8689 | 59.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56886.3242 | 340.3385 | T+30 sec | 40742.8689 | [12 empty] | T+30 sec | 40742.8689 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.1323 | 343.6084 | 963.711 | T+30 sec | 40742.8689 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+30 sec | 40742.8689 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+30 sec | 40742.8689 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+32 sec | 40742.8689 | 59.881 | 0 | 59.8807 | 0 |  | 340.3385 | 340.3385 | 966.8298 | -6.2558 | 862.9676 | 0 | 893.6676 | 528.8143 | 575.7325 | 596.1496 | [6 empty] | 0 | 596.1496 | -468.0285 | -467.0124 | T+32 sec |  |  |  |  | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+32 sec | 40742.8689 | 59.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56886.3242 | 340.3385 | T+32 sec | 40742.8689 | [12 empty] | T+32 sec | 40742.8689 | [12 empty] | T+32 sec | 40742.8689 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+32 sec | 40742.8689 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+32 sec | 40742.8689 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+34 sec | 40742.8689 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 859.5702 | 0 | 891.7733 | 522.5586 | 572.6046 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+34 sec |  |  |  |  | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+34 sec | 40742.8689 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56893.1289 | 343.1969 | T+34 sec | 40742.8689 | [12 empty] | T+34 sec | 40742.8689 | [12 empty] | T+34 sec | 40742.8689 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+34 sec | 40742.8689 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+34 sec | 40742.8689 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+36 sec | 40742.8689 | 59.878 | 0 | 59.8807 | 0 |  | 348.9247 | 348.9247 | 966.8298 | -6.2558 | 859.0423 | 0 | 890.0506 | 516.3028 | 569.4768 | 596.1496 | [6 empty] | 0 | 596.1496 | -457.2513 | -467.0124 | T+36 sec |  |  |  |  | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+36 sec | 40742.8689 | 59.878 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56893.1289 | 348.9247 | T+36 sec | 40742.8689 | [12 empty] | T+36 sec | 40742.8689 | [12 empty] | T+36 sec | 40742.8689 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+36 sec | 40742.8689 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+36 sec | 40742.8689 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+38 sec | 40742.869 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 847.0587 | 0 | 887.901 | 510.0471 | 566.3489 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+38 sec |  |  |  |  | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+38 sec | 40742.869 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56875.6172 | 343.1969 | T+38 sec | 40742.869 | [12 empty] | T+38 sec | 40742.869 | [12 empty] | T+38 sec | 40742.869 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+38 sec | 40742.869 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+38 sec | 40742.869 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+40 sec | 40742.869 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 840.803 | 0 | 885.6582 | 503.7913 | 563.221 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+40 sec |  |  |  |  | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+40 sec | 40742.869 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56875.6172 | 343.1969 | T+40 sec | 40742.869 | [12 empty] | T+40 sec | 40742.869 | [12 empty] | T+40 sec | 40742.869 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56878.6644 | 342.6792 | 962.7818 | T+40 sec | 40742.869 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+40 sec | 40742.869 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+42 sec | 40742.869 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 834.5472 | 0 | 883.335 | 497.5356 | 560.0931 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+42 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+42 sec | 40742.869 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56890.8242 | 343.1969 | T+42 sec | 40742.869 | [12 empty] | T+42 sec | 40742.869 | [12 empty] | T+42 sec | 40742.869 | [12 empty] | T+42 sec | 40742.869 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+42 sec | 40742.869 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+44 sec | 40742.869 | 59.882 | 0 | 59.8807 | 0 |  | 337.4801 | 337.4801 | 966.8298 | -6.2558 | 822.5746 | 0 | 880.6932 | 491.2798 | 556.9652 | 596.1496 | [6 empty] | 0 | 596.1496 | -471.7299 | -467.0124 | T+44 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+44 sec | 40742.869 | 59.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56890.8242 | 337.4801 | T+44 sec | 40742.869 | [12 empty] | T+44 sec | 40742.869 | [12 empty] | T+44 sec | 40742.869 | [12 empty] | T+44 sec | 40742.869 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+44 sec | 40742.869 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+46 sec | 40742.8691 | 59.883 | 0 | 59.8807 | 0 |  | 334.6217 | 334.6217 | 966.8298 | -6.2558 | 813.4604 | 0 | 877.8919 | 485.0241 | 553.8374 | 596.1496 | [6 empty] | 0 | 596.1496 | -475.4904 | -467.0124 | T+46 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+46 sec | 40742.8691 | 59.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56891.0664 | 334.6217 | T+46 sec | 40742.8691 | [12 empty] | T+46 sec | 40742.8691 | [12 empty] | T+46 sec | 40742.8691 | [12 empty] | T+46 sec | 40742.8691 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+46 sec | 40742.8691 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+48 sec | 40742.8691 | 59.882 | 0 | 59.8807 | 0 |  | 337.4801 | 337.4801 | 966.8298 | -6.2558 | 810.0631 | 0 | 875.1787 | 478.7683 | 550.7095 | 596.1496 | [6 empty] | 0 | 596.1496 | -471.7299 | -467.0124 | T+48 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+48 sec | 40742.8691 | 59.882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56891.0664 | 337.4801 | T+48 sec | 40742.8691 | [12 empty] | T+48 sec | 40742.8691 | [12 empty] | T+48 sec | 40742.8691 | [12 empty] | T+48 sec | 40742.8691 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+48 sec | 40742.8691 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+50 sec | 40742.8691 | 59.883 | 0 | 59.8807 | 0 |  | 334.6217 | 334.6217 | 966.8298 | -6.2558 | 800.9489 | 0 | 872.3237 | 472.5125 | 547.5816 | 596.1496 | [6 empty] | 0 | 596.1496 | -475.4904 | -467.0124 | T+50 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+50 sec | 40742.8691 | 59.883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56899.4688 | 334.6217 | T+50 sec | 40742.8691 | [12 empty] | T+50 sec | 40742.8691 | [12 empty] | T+50 sec | 40742.8691 | [12 empty] | T+50 sec | 40742.8691 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+50 sec | 40742.8691 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+52 sec | 40742.8691 | 59.88 | 0 | 59.8807 | 0 |  | 343.1969 | 343.1969 | 966.8298 | -6.2558 | 803.2684 | 0 | 869.7661 | 466.2568 | 544.4537 | 596.1496 | [6 empty] | 0 | 596.1496 | -464.3847 | -467.0124 | T+52 sec | [6 empty] | 59.8804 | -466.0866 | 59.8807 | -467.0124 | T+52 sec | 40742.8691 | 59.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56899.4688 | 343.1969 | T+52 sec | 40742.8691 | [12 empty] | T+52 sec | 40742.8691 | [12 empty] | T+52 sec | 40742.8691 | [12 empty] | T+52 sec | 40742.8691 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.8589 | 341.9284 | 962.031 | T+52 sec | 40742.8691 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.0016 | 341.1805 | 961.2831
T+54 sec | 40742.8691 | 59.881 | 0 |  |  |  | 340.3385 | 340.3385 |  | -6.2558 | 794.1543 | 0 | 867.0657 | 460.001 | 541.3259 | 596.1496 | [6 empty] | 0 | 596.1496 | -468.0285 |  | T+54 sec | [10 empty] | T+54 sec | 40742.8691 | 59.881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.9023 | 340.3385 | T+54 sec | 40742.8691 | [12 empty] | T+54 sec | 40742.8691 | [12 empty] | T+54 sec | 40742.8691 | [12 empty] | T+54 sec | 40742.8691 | [12 empty] | T+54 sec | 40742.8691
T+56 sec | 40742.8692 | 59.884 | 0 |  |  |  | 331.7632 | 331.7632 |  | -6.2558 | 779.3232 | 0 | 864.0401 | 453.7453 | 538.198 | 596.1496 | [6 empty] | 0 | 596.1496 | -479.3113 |  | T+56 sec | [10 empty] | T+56 sec | 40742.8692 | 59.884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.9023 | 331.7632 | T+56 sec | 40742.8692 | [12 empty] | T+56 sec | 40742.8692 | [12 empty] | T+56 sec | 40742.8692 | [12 empty] | T+56 sec | 40742.8692 | [12 empty] | T+56 sec | 40742.8692
T+58 sec | 40742.8692 | 59.892 | 0 |  |  |  | 308.8849 | 308.8849 |  | -6.2558 | 750.1891 | 0 | 860.2451 | 447.4895 | 535.0701 | 596.1496 | [6 empty] | 0 | 596.1496 | -512.2578 |  | T+58 sec | [10 empty] | T+58 sec | 40742.8692 | 59.892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.8125 | 308.8849 | T+58 sec | 40742.8692 | [12 empty] | T+58 sec | 40742.8692 | [12 empty] | T+58 sec | 40742.8692 | [12 empty] | T+58 sec | 40742.8692 | [12 empty] | T+58 sec | 40742.8692
T+60 sec | 40742.8692 | 59.894 | 0 |  |  |  | 303.1571 | 303.1571 |  | -6.2558 | 738.2056 | 0 | 856.3083 | 441.2338 | 531.9422 | 596.1496 | [6 empty] | 0 | 596.1496 | -521.2275 |  | T+60 sec | [10 empty] | T+60 sec | 40742.8692 | 59.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.8125 | 303.1571 | T+60 sec | 40742.8692 | [12 empty] | T+60 sec | 40742.8692 | [12 empty] | T+60 sec | 40742.8692 | [12 empty] | T+60 sec | 40742.8692 | [12 empty] | T+60 sec | 40742.8692
T+62 sec | 40742.8692 | 59.896 | 0 |  |  |  | 297.4403 | 297.4403 |  | -6.2558 | 726.233 | 0 | 852.2435 | 434.978 | 528.8143 | 596.1496 | [6 empty] | 0 | 596.1496 | -530.499 |  | T+62 sec | [10 empty] | T+62 sec | 40742.8692 | 59.896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56837.2148 | 297.4403 | T+62 sec | 40742.8692 | [12 empty] | T+62 sec | 40742.8692 | [12 empty] | T+62 sec | 40742.8692 | [12 empty] | T+62 sec | 40742.8692 | [12 empty] | T+62 sec | 40742.8692
T+64 sec | 40742.8693 | 59.9 | 0 |  |  |  | 285.9956 | 285.9956 |  | -6.2558 | 708.5326 | 0 | 847.8886 | 428.7223 | 525.6865 | 596.1496 | [6 empty] | 0 | 596.1496 | -550.0873 |  | T+64 sec | [10 empty] | T+64 sec | 40742.8693 | 59.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56837.2148 | 285.9956 | T+64 sec | 40742.8693 | [12 empty] | T+64 sec | 40742.8693 | [12 empty] | T+64 sec | 40742.8693 | [12 empty] | T+64 sec | 40742.8693 | [12 empty] | T+64 sec | 40742.8693
T+66 sec | 40742.8693 | 59.902 | 0 |  |  |  | 280.2788 | 280.2788 |  | -6.2558 | 696.56 | 0 | 843.4377 | 422.4665 | 522.5586 | 596.1496 | [6 empty] | 0 | 596.1496 | -560.424 |  | T+66 sec | [10 empty] | T+66 sec | 40742.8693 | 59.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.5938 | 280.2788 | T+66 sec | 40742.8693 | [12 empty] | T+66 sec | 40742.8693 | [12 empty] | T+66 sec | 40742.8693 | [12 empty] | T+66 sec | 40742.8693 | [12 empty] | T+66 sec | 40742.8693
T+68 sec | 40742.8693 | 59.904 | 0 |  |  |  | 274.5619 | 274.5619 |  | -6.2558 | 684.5874 | 0 | 838.8992 | 416.2107 | 519.4307 | 596.1496 | [6 empty] | 0 | 596.1496 | -571.1567 |  | T+68 sec | [10 empty] | T+68 sec | 40742.8693 | 59.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.5938 | 274.5619 | T+68 sec | 40742.8693 | [12 empty] | T+68 sec | 40742.8693 | [12 empty] | T+68 sec | 40742.8693 | [12 empty] | T+68 sec | 40742.8693 | [12 empty] | T+68 sec | 40742.8693
T+70 sec | 40742.8693 | 59.903 | 0 |  |  |  | 277.4203 | 277.4203 |  | -6.2558 | 681.19 | 0 | 834.5183 | 409.955 | 516.3028 | 596.1496 | [6 empty] | 0 | 596.1496 | -565.7395 |  | T+70 sec | [10 empty] | T+70 sec | 40742.8693 | 59.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56841.8438 | 277.4203 | T+70 sec | 40742.8693 | [12 empty] | T+70 sec | 40742.8693 | [12 empty] | T+70 sec | 40742.8693 | [12 empty] | T+70 sec | 40742.8693 | [12 empty] | T+70 sec | 40742.8693
T+72 sec | 40742.8694 | 59.902 | 0 |  |  |  | 280.2788 | 280.2788 |  | -6.2558 | 677.7927 | 0 | 830.2825 | 403.6992 | 513.175 | 596.1496 | [6 empty] | 0 | 596.1496 | -560.424 |  | T+72 sec | [10 empty] | T+72 sec | 40742.8694 | 59.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56841.8438 | 280.2788 | T+72 sec | 40742.8694 | [12 empty] | T+72 sec | 40742.8694 | [12 empty] | T+72 sec | 40742.8694 | [12 empty] | T+72 sec | 40742.8694 | [12 empty] | T+72 sec | 40742.8694
T+74 sec | 40742.8694 | 59.903 | 0 |  |  |  | 277.4203 | 277.4203 |  | -6.2558 | 668.6785 | 0 | 826.0298 | 397.4435 | 510.0471 | 596.1496 | [6 empty] | 0 | 596.1496 | -565.7395 |  | T+74 sec | [10 empty] | T+74 sec | 40742.8694 | 59.903 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56835.3047 | 277.4203 | T+74 sec | 40742.8694 | [12 empty] | T+74 sec | 40742.8694 | [12 empty] | T+74 sec | 40742.8694 | [12 empty] | T+74 sec | 40742.8694 | [12 empty] | T+74 sec | 40742.8694
T+76 sec | 40742.8694 | 59.902 | 0 |  |  |  | 280.2788 | 280.2788 |  | -6.2558 | 665.2812 | 0 | 821.908 | 391.1877 | 506.9192 | 596.1496 | [6 empty] | 0 | 596.1496 | -560.424 |  | T+76 sec | [10 empty] | T+76 sec | 40742.8694 | 59.902 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56835.3047 | 280.2788 | T+76 sec | 40742.8694 | [12 empty] | T+76 sec | 40742.8694 | [12 empty] | T+76 sec | 40742.8694 | [12 empty] | T+76 sec | 40742.8694 | [12 empty] | T+76 sec | 40742.8694
T+78 sec | 40742.8694 | 59.901 | 0 |  |  |  | 283.1372 | 283.1372 |  | -6.2558 | 661.8839 | 0 | 817.9074 | 384.932 | 503.7913 | 596.1496 | [6 empty] | 0 | 596.1496 | -555.2076 |  | T+78 sec | [10 empty] | T+78 sec | 40742.8694 | 59.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56837.2969 | 283.1372 | T+78 sec | 40742.8694 | [12 empty] | T+78 sec | 40742.8694 | [12 empty] | T+78 sec | 40742.8694 | [12 empty] | T+78 sec | 40742.8694 | [12 empty] | T+78 sec | 40742.8694
T+80 sec | 40742.8694 | 59.9 | 0 |  |  |  | 285.9956 | 285.9956 |  | -6.2558 | 658.4866 | 0 | 814.0191 | 378.6762 | 500.6634 | 596.1496 | [6 empty] | 0 | 596.1496 | -550.0873 |  | T+80 sec | [10 empty] | T+80 sec | 40742.8694 | 59.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56837.2969 | 285.9956 | T+80 sec | 40742.8694 | [12 empty] | T+80 sec | 40742.8694 | [12 empty] | T+80 sec | 40742.8694 | [12 empty] | T+80 sec | 40742.8694 | [12 empty] | T+80 sec | 40742.8694
| 40742.8695 | 59.901 | 0 |  |  |  | 283.1372 | 283.1372 |  | -6.2558 | 649.3724 | 0 | 810.0989 | 372.4205 | 497.5356 | 596.1496 | [6 empty] | 0 | 596.1496 | -555.2076 | [13 empty] | 40742.8695 | 59.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.1523 | 283.1372
| 40742.8695 | 59.904 | 0 |  |  |  | 274.5619 | 274.5619 |  | -6.2558 | 634.5413 | 0 | 806.0162 | 366.1647 | 494.4077 | 596.1496 | [6 empty] | 0 | 596.1496 | -571.1567 | [13 empty] | 40742.8695 | 59.904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.1523 | 274.5619
| 40742.8695 | 59.907 | 0 |  |  |  | 265.9757 | 265.9757 |  | -6.2558 | 619.6994 | 0 | 801.7817 | 359.9089 | 491.2798 | 596.1496 | [6 empty] | 0 | 596.1496 | -588.0715 | [13 empty] | 40742.8695 | 59.907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.543 | 265.9757
| 40742.8695 | 59.91 | 0 |  |  |  | 257.4004 | 257.4004 |  | -6.2558 | 604.8683 | 0 | 797.4059 | 353.6532 | 488.1519 | 596.1496 | [6 empty] | 0 | 596.1496 | -605.9951 | [13 empty] | 40742.8695 | 59.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.543 | 257.4004
| 40742.8696 | 59.913 | 0 |  |  |  | 248.8251 | 248.8251 |  | -6.2558 | 590.0373 | 0 | 792.8979 | 347.3974 | 485.0241 | 596.1496 | [6 empty] | 0 | 596.1496 | -625.0457 | [13 empty] | 40742.8696 | 59.913 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.6367 | 248.8251
| 40742.8696 | 59.916 | 0 |  |  |  | 240.239 | 240.239 |  | -6.2558 | 575.1953 | 0 | 788.2659 | 341.1417 | 481.8962 | 596.1496 | [6 empty] | 0 | 596.1496 | -645.3596 | [13 empty] | 40742.8696 | 59.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.6367 | 240.239
| 40742.8696 | 59.916 | 0 |  |  |  | 240.239 | 240.239 |  | -6.2558 | 568.9396 | 0 | 783.6966 | 334.8859 | 478.7683 | 596.1496 | [6 empty] | 0 | 596.1496 | -645.3596 | [13 empty] | 40742.8696 | 59.916 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56866.1602 | 240.239
| 40742.8696 | 59.919 | 0 |  |  |  | 231.6637 | 231.6637 |  | -6.2558 | 554.1085 | 0 | 779.0111 | 328.6302 | 475.6404 | 596.1496 | [6 empty] | 0 | 596.1496 | -667.0097 | [13 empty] | 40742.8696 | 59.919 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56866.1602 | 231.6637
| 40742.8697 | 59.922 | 0 |  |  |  | 223.0775 | 223.0775 |  | -6.2558 | 539.2666 | 0 | 774.2162 | 322.3744 | 472.5125 | 596.1496 | [6 empty] | 0 | 596.1496 | -690.1934 | [13 empty] | 40742.8697 | 59.922 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56869.2109 | 223.0775
| 40742.8697 | 59.924 | 0 |  |  |  | 217.3606 | 217.3606 |  | -6.2558 | 527.294 | 0 | 769.3746 | 316.1187 | 469.3847 | 596.1496 | [6 empty] | 0 | 596.1496 | -706.5445 | [13 empty] | 40742.8697 | 59.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56869.2109 | 217.3606
| 40742.8697 | 59.924 | 0 |  |  |  | 217.3606 | 217.3606 |  | -6.2558 | 521.0382 | 0 | 764.5989 | 309.8629 | 466.2568 | 596.1496 | [6 empty] | 0 | 596.1496 | -706.5445 | [13 empty] | 40742.8697 | 59.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56876.2656 | 217.3606
| 40742.8697 | 59.924 | 0 |  |  |  | 217.3606 | 217.3606 |  | -6.2558 | 514.7825 | 0 | 759.8854 | 303.6071 | 463.1289 | 596.1496 | [6 empty] | 0 | 596.1496 | -706.5445 | [13 empty] | 40742.8697 | 59.924 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56876.2656 | 217.3606
| 40742.8697 | 59.925 | 0 |  |  |  | 214.5022 | 214.5022 |  | -6.2558 | 505.6683 | 0 | 755.1777 | 297.3514 | 460.001 | 596.1496 | [6 empty] | 0 | 596.1496 | -715.0141 | [13 empty] | 40742.8697 | 59.925 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56881.3906 | 214.5022
| 40742.8698 | 59.928 | 0 |  |  |  | 205.916 | 205.916 |  | -6.2558 | 490.8263 | 0 | 750.3713 | 291.0956 | 456.8732 | 596.1496 | [6 empty] | 0 | 596.1496 | -741.7217 | [13 empty] | 40742.8698 | 59.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56881.3906 | 205.916
| 40742.8698 | 59.929 | 0 |  |  |  | 203.0576 | 203.0576 |  | -6.2558 | 481.7121 | 0 | 745.5738 | 284.8399 | 453.7453 | 596.1496 | [6 empty] | 0 | 596.1496 | -751.0611 | [13 empty] | 40742.8698 | 59.929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56889.5859 | 203.0576
| 40742.8698 | 59.932 | 0 |  |  |  | 194.4823 | 194.4823 |  | -6.2558 | 466.8811 | 0 | 740.6845 | 278.5841 | 450.6174 | 596.1496 | [6 empty] | 0 | 596.1496 | -780.5462 | [13 empty] | 40742.8698 | 59.932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56889.5859 | 194.4823
| 40742.8698 | 59.934 | 0 |  |  |  | 188.7654 | 188.7654 |  | -6.2558 | 454.9085 | 0 | 735.7573 | 272.3284 | 447.4895 | 596.1496 | [6 empty] | 0 | 596.1496 | -801.5235 | [13 empty] | 40742.8698 | 59.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56893.8867 | 188.7654
| 40742.8699 | 59.935 | 0 |  |  |  | 185.8961 | 185.8961 |  | -6.2558 | 445.7834 | 0 | 730.8425 | 266.0726 | 444.3616 | 596.1496 | [6 empty] | 0 | 596.1496 | -812.483 | [13 empty] | 40742.8699 | 59.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56900.4414 | 185.8961
| 40742.8699 | 59.935 | 0 |  |  |  | 185.8961 | 185.8961 |  | -6.2558 | 439.5276 | 0 | 725.9872 | 259.8169 | 441.2338 | 596.1496 | [6 empty] | 0 | 596.1496 | -812.483 | [13 empty] | 40742.8699 | 59.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56900.4414 | 185.8961
| 40742.8699 | 59.935 | 0 |  |  |  | 185.8961 | 185.8961 |  | -6.2558 | 433.2719 | 0 | 721.1886 | 253.5611 | 438.1059 | 596.1496 | [6 empty] | 0 | 596.1496 | -812.483 | [13 empty] | 40742.8699 | 59.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56900.4414 | 185.8961
| 40742.8699 | 59.935 | 0 |  |  |  | 185.8961 | 185.8961 |  | -6.2558 | 427.0161 | 0 | 716.4439 | 247.3053 | 434.978 | 596.1496 | [6 empty] | 0 | 596.1496 | -812.483 | [13 empty] | 40742.8699 | 59.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56887.582 | 185.8961
| 40742.87 | 59.934 | 0 |  |  |  | 188.7654 | 188.7654 |  | -6.2558 | 423.6297 | 0 | 711.7961 | 241.0496 | 431.8501 | 596.1496 | [6 empty] | 0 | 596.1496 | -801.5235 | [13 empty] | 40742.87 | 59.934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56887.582 | 188.7654
| 40742.87 | 59.935 | 0 |  |  |  | 185.8961 | 185.8961 |  | -6.2558 | 414.5046 | 0 | 707.1509 | 234.7938 | 428.7223 | 596.1496 | [6 empty] | 0 | 596.1496 | -812.483 | [13 empty] | 40742.87 | 59.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56901.5859 | 185.8961
| 40742.87 | 59.938 | 0 |  |  |  | 177.3208 | 177.3208 |  | -6.2558 | 399.6736 | 0 | 702.4205 | 228.5381 | 425.5944 | 596.1496 | [6 empty] | 0 | 596.1496 | -847.0989 | [13 empty] | 40742.87 | 59.938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56901.5859 | 177.3208
| 40742.87 | 59.941 | 0 |  |  |  | 168.7346 | 168.7346 |  | -6.2558 | 384.8316 | 0 | 697.6085 | 222.2823 | 422.4665 | 596.1496 | [6 empty] | 0 | 596.1496 | -884.8458 | [13 empty] | 40742.87 | 59.941 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56915.6562 | 168.7346
| 40742.87 | 59.943 | 0 |  |  |  | 163.0177 | 163.0177 |  | -6.2558 | 372.859 | 0 | 692.7615 | 216.0266 | 419.3386 | 596.1496 | [6 empty] | 0 | 596.1496 | -911.9011 | [13 empty] | 40742.87 | 59.943 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56915.6562 | 163.0177
| 40742.8701 | 59.948 | 0 |  |  |  | 148.7147 | 148.7147 |  | -6.2558 | 352.3002 | 0 | 687.7547 | 209.7708 | 416.2107 | 596.1496 | [6 empty] | 0 | 596.1496 | -987.4391 | [13 empty] | 40742.8701 | 59.948 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56912.2109 | 148.7147
| 40742.8701 | 59.951 | 0 |  |  |  | 140.1394 | 140.1394 |  | -6.2558 | 337.4691 | 0 | 682.6781 | 203.5151 | 413.0829 | 596.1496 | [6 empty] | 0 | 596.1496 | -1039.0416 | [13 empty] | 40742.8701 | 59.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56912.2109 | 140.1394
| 40742.8701 | 59.951 | 0 |  |  |  | 140.1394 | 140.1394 |  | -6.2558 | 331.2134 | 0 | 677.6572 | 197.2593 | 409.955 | 596.1496 | [6 empty] | 0 | 596.1496 | -1039.0416 | [13 empty] | 40742.8701 | 59.951 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56914.3086 | 140.1394
| 40742.8701 | 59.953 | 0 |  |  |  | 134.4225 | 134.4225 |  | -6.2558 | 319.2408 | 0 | 672.6091 | 191.0035 | 406.8271 | 596.1496 | [6 empty] | 0 | 596.1496 | -1076.5477 | [13 empty] | 40742.8701 | 59.953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56914.3086 | 134.4225
| 40742.8702 | 59.956 | 0 |  |  |  | 125.8363 | 125.8363 |  | -6.2558 | 304.3988 | 0 | 667.495 | 184.7478 | 403.6992 | 596.1496 | [6 empty] | 0 | 596.1496 | -1138.2574 | [13 empty] | 40742.8702 | 59.956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56907.5391 | 125.8363
| 40742.8702 | 59.958 | 0 |  |  |  | 120.1195 | 120.1195 |  | -6.2558 | 292.4262 | 0 | 662.3571 | 178.492 | 400.5714 | 596.1496 | [6 empty] | 0 | 596.1496 | -1183.4239 | [13 empty] | 40742.8702 | 59.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56907.5391 | 120.1195
| 40742.8702 | 59.958 | 0 |  |  |  | 120.1195 | 120.1195 |  | -6.2558 | 286.1705 | 0 | 657.2735 | 172.2363 | 397.4435 | 596.1496 | [6 empty] | 0 | 596.1496 | -1183.4239 | [13 empty] | 40742.8702 | 59.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56897.043 | 120.1195
| 40742.8702 | 59.959 | 0 |  |  |  | 117.261 | 117.261 |  | -6.2558 | 277.0563 | 0 | 652.2039 | 165.9805 | 394.3156 | 596.1496 | [6 empty] | 0 | 596.1496 | -1207.3786 | [13 empty] | 40742.8702 | 59.959 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56897.043 | 117.261
| 40742.8703 | 59.958 | 0 |  |  |  | 120.1195 | 120.1195 |  | -6.2558 | 273.6589 | 0 | 647.2231 | 159.7248 | 391.1877 | 596.1496 | [6 empty] | 0 | 596.1496 | -1183.4239 | [13 empty] | 40742.8703 | 59.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56902.0312 | 120.1195
| 40742.8703 | 59.958 | 0 |  |  |  | 120.1195 | 120.1195 |  | -6.2558 | 267.4032 | 0 | 642.2904 | 153.469 | 388.0598 | 596.1496 | [6 empty] | 0 | 596.1496 | -1183.4239 | [13 empty] | 40742.8703 | 59.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56902.0312 | 120.1195
| 40742.8703 | 59.958 | 0 |  |  |  | 120.1195 | 120.1195 |  | -6.2558 | 261.1474 | 0 | 637.4039 | 147.2133 | 384.932 | 596.1496 | [6 empty] | 0 | 596.1496 | -1183.4239 | [13 empty] | 40742.8703 | 59.958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56903.0273 | 120.1195
| 40742.8703 | 59.96 | 0 |  |  |  | 114.4026 | 114.4026 |  | -6.2558 | 249.1748 | 0 | 632.4896 | 140.9575 | 381.8041 | 596.1496 | [6 empty] | 0 | 596.1496 | -1232.3231 | [13 empty] | 40742.8703 | 59.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56903.0273 | 114.4026
| 40742.8703 | 59.962 | 0 |  |  |  | 108.6749 | 108.6749 |  | -6.2558 | 237.1913 | 0 | 627.5484 | 134.7017 | 378.6762 | 596.1496 | [6 empty] | 0 | 596.1496 | -1285.5431 | [13 empty] | 40742.8703 | 59.962 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56917.7422 | 108.6749
| 40742.8704 | 59.965 | 0 |  |  |  | 100.0996 | 100.0996 |  | -6.2558 | 222.3603 | 0 | 622.5461 | 128.446 | 375.5483 | 596.1496 | [6 empty] | 0 | 596.1496 | -1374.4079 | [13 empty] | 40742.8704 | 59.965 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56917.7422 | 100.0996
| 40742.8704 | 59.967 | 0 |  |  |  | 94.3827 | 94.3827 |  | -6.2558 | 210.3876 | 0 | 617.5198 | 122.1902 | 372.4205 | 596.1496 | [6 empty] | 0 | 596.1496 | -1440.8062 | [13 empty] | 40742.8704 | 59.967 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56900.8125 | 94.3827
| 40742.8704 | 59.97 | 0 |  |  |  | 85.7965 | 85.7965 |  | -6.2558 | 195.5457 | 0 | 612.4357 | 115.9345 | 369.2926 | 596.1496 | [6 empty] | 0 | 596.1496 | -1553.527 | [13 empty] | 40742.8704 | 59.97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56900.8125 | 85.7965
| 40742.8704 | 59.971 | 0 |  |  |  | 82.9381 | 82.9381 |  | -6.2558 | 186.4315 | 0 | 607.3642 | 109.6787 | 366.1647 | 596.1496 | [6 empty] | 0 | 596.1496 | -1595.0707 | [13 empty] | 40742.8704 | 59.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56914.8047 | 82.9381
| 40742.8705 | 59.973 | 0 |  |  |  | 77.2212 | 77.2212 |  | -6.2558 | 174.4589 | 0 | 602.2712 | 103.423 | 363.0368 | 596.1496 | [6 empty] | 0 | 596.1496 | -1685.2003 | [13 empty] | 40742.8705 | 59.973 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56914.8047 | 77.2212
| 40742.8705 | 59.971 | 0 |  |  |  | 82.9381 | 82.9381 |  | -6.2558 | 173.92 | 0 | 597.2904 | 97.1672 | 359.9089 | 596.1496 | [6 empty] | 0 | 596.1496 | -1595.0707 | [13 empty] | 40742.8705 | 59.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56922.5234 | 82.9381
| 40742.8705 | 59.971 | 0 |  |  |  | 82.9381 | 82.9381 |  | -6.2558 | 167.6642 | 0 | 592.3522 | 90.9114 | 356.7811 | 596.1496 | [6 empty] | 0 | 596.1496 | -1595.0707 | [13 empty] | 40742.8705 | 59.971 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56922.5234 | 82.9381
| 40742.8705 | 59.972 | 0 |  |  |  | 80.0797 | 80.0797 |  | -6.2558 | 158.5501 | 0 | 587.4226 | 84.6557 | 353.6532 | 596.1496 | [6 empty] | 0 | 596.1496 | -1638.8973 | [13 empty] | 40742.8705 | 59.972 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56932.4453 | 80.0797
| 40742.8706 | 59.974 | 0 |  |  |  | 74.3628 | 74.3628 |  | -6.2558 | 146.5774 | 0 | 582.4693 | 78.3999 | 350.5253 | 596.1496 | [6 empty] | 0 | 596.1496 | -1734.1957 | [13 empty] | 40742.8706 | 59.974 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56932.4453 | 74.3628
| 40742.8706 | 59.975 | 0 |  |  |  | 71.5044 | 71.5044 |  | -6.2558 | 137.4633 | 0 | 577.5248 | 72.1442 | 347.3974 | 596.1496 | [6 empty] | 0 | 596.1496 | -1786.1255 | [13 empty] | 40742.8706 | 59.975 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56920.2305 | 71.5044
| 40742.8706 | 59.977 | 0 |  |  |  | 65.7766 | 65.7766 |  | -6.2558 | 125.4797 | 0 | 572.5573 | 65.8884 | 344.2696 | 596.1496 | [6 empty] | 0 | 596.1496 | -1900.1404 | [13 empty] | 40742.8706 | 59.977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56920.2305 | 65.7766
| 40742.8706 | 59.979 | 0 |  |  |  | 60.0597 | 60.0597 |  | -6.2558 | 113.5071 | 0 | 567.5676 | 59.6327 | 341.1417 | 596.1496 | [6 empty] | 0 | 596.1496 | -2029.4403 | [13 empty] | 40742.8706 | 59.979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56912.875 | 60.0597
| 40742.8706 | 59.981 | 0 |  |  |  | 54.3429 | 54.3429 |  | -6.2558 | 101.5345 | 0 | 562.5565 | 53.3769 | 338.0138 | 596.1496 | [6 empty] | 0 | 596.1496 | -2177.6221 | [13 empty] | 40742.8706 | 59.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56912.875 | 54.3429
| 40742.8707 | 59.982 | 0 |  |  |  | 51.4845 | 51.4845 |  | -6.2558 | 92.4203 | 0 | 557.555 | 47.1212 | 334.8859 | 596.1496 | [6 empty] | 0 | 596.1496 | -2260.1352 | [13 empty] | 40742.8707 | 59.982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56905.2188 | 51.4845
| 40742.8707 | 59.984 | 0 |  |  |  | 45.7567 | 45.7567 |  | -6.2558 | 80.4368 | 0 | 552.5327 | 40.8654 | 331.758 | 596.1496 | [6 empty] | 0 | 596.1496 | -2445.8416 | [13 empty] | 40742.8707 | 59.984 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56905.2188 | 45.7567
| 40742.8707 | 59.986 | 0 |  |  |  | 40.0398 | 40.0398 |  | -6.2558 | 68.4642 | 0 | 547.4903 | 34.6096 | 328.6302 | 596.1496 | [6 empty] | 0 | 596.1496 | -2664.3432 | [13 empty] | 40742.8707 | 59.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56915.6172 | 40.0398
| 40742.8707 | 59.989 | 0 |  |  |  | 31.4645 | 31.4645 |  | -6.2558 | 53.6331 | 0 | 542.399 | 28.3539 | 325.5023 | 596.1496 | [6 empty] | 0 | 596.1496 | -3076.6227 | [13 empty] | 40742.8707 | 59.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56915.6172 | 31.4645
| 40742.8708 | 59.991 | 0 |  |  |  | 25.7368 | 25.7368 |  | -6.2558 | 41.6496 | 0 | 537.2893 | 22.0981 | 322.3744 | 596.1496 | [6 empty] | 0 | 596.1496 | -3431.2668 | [13 empty] | 40742.8708 | 59.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56923.0312 | 25.7368
| 40742.8708 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | -6.2558 | 29.677 | 0 | 532.1619 | 15.8424 | 319.2465 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8708 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56923.0312 | 20.0199
| 40742.8708 | 59.996 | 0 |  |  |  | 11.4446 | 11.4446 |  | -6.2558 | 14.846 | 0 | 526.9888 | 9.5866 | 316.1187 | 596.1496 | [6 empty] | 0 | 596.1496 | -4816.6759 | [13 empty] | 40742.8708 | 59.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56932.0273 | 11.4446
| 40742.8708 | 59.999 | 0 |  |  |  | 2.8584 | 2.8584 |  | -6.2558 | 0.0040044 | 0 | 521.7711 | 3.3309 | 312.9908 | 596.1496 | [6 empty] | 0 | 596.1496 | -6359.1881 | [13 empty] | 40742.8708 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56932.0273 | 2.8584
| 40742.8709 | 60.002 | 0 |  |  |  | -5.7169 | -5.7169 |  | 0 | -8.5713 | 0 | 516.5717 | 3.3309 | 309.9248 | 596.1496 | [6 empty] | 0 | 596.1496 | -9349.5093 | [13 empty] | 40742.8709 | 60.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56926.2188 | -5.7169
| 40742.8709 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 511.3898 | 3.3309 | 306.919 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8709 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56926.2188 | -14.3031
| 40742.8709 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 506.3077 | 3.3309 | 303.9716 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8709 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56930.3281 | -14.3031
| 40742.8709 | 60.009 | 0 |  |  |  | -25.7368 | -25.7368 |  | 0 | -28.5912 | 0 | 501.2134 | 3.3309 | 301.0808 | 596.1496 | [6 empty] | 0 | 596.1496 | 95582.2924 | [13 empty] | 40742.8709 | 60.009 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56930.3281 | -25.7368
| 40742.8709 | 60.01 | 0 |  |  |  | -28.5952 | -28.5952 |  | 0 | -31.4496 | 0 | 496.1883 | 3.3309 | 298.2451 | 596.1496 | [6 empty] | 0 | 596.1496 | 36727.8609 | [13 empty] | 40742.8709 | 60.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56935.1094 | -28.5952
| 40742.871 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 491.2303 | 3.3309 | 295.4629 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.871 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56935.1094 | -31.4645
| 40742.871 | 60.012 | 0 |  |  |  | -34.323 | -34.323 |  | 0 | -37.1774 | 0 | 486.3376 | 3.3309 | 292.7327 | 596.1496 | [6 empty] | 0 | 596.1496 | 16441.5621 | [13 empty] | 40742.871 | 60.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56938.2383 | -34.323
| 40742.871 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 481.5609 | 3.3309 | 290.053 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.871 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56938.2383 | -31.4645
| 40742.871 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 476.8191 | 3.3309 | 287.4225 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.871 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56947.1367 | -37.1814
| 40742.8711 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 472.137 | 3.3309 | 284.8399 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.8711 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56947.1367 | -40.0398
| 40742.8711 | 60.017 | 0 |  |  |  | -48.6151 | -48.6151 |  | 0 | -51.4695 | 0 | 467.462 | 3.3309 | 282.3038 | 596.1496 | [6 empty] | 0 | 596.1496 | 6913.3841 | [13 empty] | 40742.8711 | 60.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56946.1875 | -48.6151
| 40742.8711 | 60.021 | 0 |  |  |  | -60.0597 | -60.0597 |  | 0 | -62.9142 | 0 | 462.7684 | 3.3309 | 279.8129 | 596.1496 | [6 empty] | 0 | 596.1496 | 4722.0743 | [13 empty] | 40742.8711 | 60.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56946.1875 | -60.0597
| 40742.8711 | 60.023 | 0 |  |  |  | -65.7766 | -65.7766 |  | 0 | -68.631 | 0 | 458.107 | 3.3309 | 277.3662 | 596.1496 | [6 empty] | 0 | 596.1496 | 4076.6153 | [13 empty] | 40742.8711 | 60.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56937.3008 | -65.7766
| 40742.8712 | 60.024 | 0 |  |  |  | -68.635 | -68.635 |  | 0 | -71.4894 | 0 | 453.5018 | 3.3309 | 274.9624 | 596.1496 | [6 empty] | 0 | 596.1496 | 3815.8234 | [13 empty] | 40742.8712 | 60.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56937.3008 | -68.635
| 40742.8712 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 448.9513 | 3.3309 | 272.6004 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8712 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56931.4141 | -71.5044
| 40742.8712 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 444.4541 | 3.3309 | 270.2791 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8712 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56931.4141 | -74.3628
| 40742.8712 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 440.0332 | 3.3309 | 267.9975 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8712 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56924.8359 | -74.3628
| 40742.8712 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 435.6385 | 3.3309 | 265.7545 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8712 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56924.8359 | -80.0797
| 40742.8713 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 431.2932 | 3.3309 | 263.5493 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8713 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56933.1562 | -82.9381
| 40742.8713 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 427.0198 | 3.3309 | 261.3808 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8713 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56933.1562 | -82.9381
| 40742.8713 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 422.793 | 3.3309 | 259.2481 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8713 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56935.6211 | -85.7965
| 40742.8713 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 418.5883 | 3.3309 | 257.1505 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8713 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56935.6211 | -91.5243
| 40742.8714 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 414.4284 | 3.3309 | 255.0869 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8714 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56957.3164 | -94.3827
| 40742.8714 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 410.3351 | 3.3309 | 253.0566 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8714 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56957.3164 | -94.3827
| 40742.8714 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 406.3522 | 3.3309 | 251.0588 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8714 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56954.2344 | -88.6549
| 40742.8714 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 402.4771 | 3.3309 | 249.0927 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8714 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56954.2344 | -82.9381
| 40742.8715 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 398.6401 | 3.3309 | 247.1576 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8715 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56956.6445 | -85.7965
| 40742.8715 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 394.8405 | 3.3309 | 245.2527 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8715 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56956.6445 | -88.6549
| 40742.8715 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 391.0994 | 3.3309 | 243.3773 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8715 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56956.6016 | -88.6549
| 40742.8715 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 387.3934 | 3.3309 | 241.5308 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8715 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56956.6016 | -91.5243
| 40742.8716 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 383.722 | 3.3309 | 239.7125 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8716 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56938.9023 | -94.3827
| 40742.8716 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 380.1058 | 3.3309 | 237.9217 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8716 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56938.9023 | -94.3827
| 40742.8716 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 376.5435 | 3.3309 | 236.1579 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8716 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56943.1797 | -94.3827
| 40742.8716 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 373.0552 | 3.3309 | 234.4204 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8716 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56943.1797 | -91.5243
| 40742.8716 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 369.6603 | 3.3309 | 232.7086 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8716 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56939.0664 | -85.7965
| 40742.8717 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 366.2523 | 3.3309 | 231.022 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8717 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56939.0664 | -94.3827
| 40742.8717 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 362.8729 | 3.3309 | 229.36 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8717 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56942.4414 | -97.2411
| 40742.8717 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 359.5217 | 3.3309 | 227.7221 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8717 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56942.4414 | -100.0996
| 40742.8717 | 60.037 | 0 |  |  |  | -105.8164 | -105.8164 |  | 0 | -108.6708 | 0 | 356.1774 | 3.3309 | 226.1078 | 596.1496 | [6 empty] | 0 | 596.1496 | 2082.722 | [13 empty] | 40742.8717 | 60.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56924.3672 | -105.8164
| 40742.8718 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 352.84 | 3.3309 | 224.5165 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8718 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56924.3672 | -111.5442
| 40742.8718 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 349.5698 | 3.3309 | 222.9478 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8718 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56907.8984 | -108.6749
| 40742.8718 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 346.1853 | 3.3309 | 221.4012 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8718 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56907.8984 | -131.5641
| 40742.8718 | 60.052 | 0 |  |  |  | -148.7147 | -148.7147 |  | 0 | -151.5691 | 0 | 342.7287 | 3.3309 | 219.8763 | 596.1496 | [6 empty] | 0 | 596.1496 | 1366.5957 | [13 empty] | 40742.8718 | 60.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56897.7969 | -148.7147
| 40742.8719 | 60.051 | 0 |  |  |  | -145.8562 | -145.8562 |  | 0 | -148.7107 | 0 | 339.3394 | 3.3309 | 218.3725 | 596.1496 | [6 empty] | 0 | 596.1496 | 1398.6401 | [13 empty] | 40742.8719 | 60.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56897.7969 | -145.8562
| 40742.8719 | 60.05 | 0 |  |  |  | -142.9978 | -142.9978 |  | 0 | -145.8522 | 0 | 336.0162 | 3.3309 | 216.8894 | 596.1496 | [6 empty] | 0 | 596.1496 | 1432.2233 | [13 empty] | 40742.8719 | 60.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56864.8906 | -142.9978
| 40742.8719 | 60.051 | 0 |  |  |  | -145.8562 | -145.8562 |  | 0 | -148.7107 | 0 | 332.7187 | 3.3309 | 215.4267 | 596.1496 | [6 empty] | 0 | 596.1496 | 1398.6401 | [13 empty] | 40742.8719 | 60.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56864.8906 | -145.8562
| 40742.8719 | 60.049 | 0 |  |  |  | -140.1394 | -140.1394 |  | 0 | -142.9938 | 0 | 329.5044 | 3.3309 | 213.9839 | 596.1496 | [6 empty] | 0 | 596.1496 | 1467.459 | [13 empty] | 40742.8719 | 60.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56842.6602 | -140.1394
| 40742.8719 | 60.05 | 0 |  |  |  | -142.9978 | -142.9978 |  | 0 | -145.8522 | 0 | 326.3141 | 3.3309 | 212.5605 | 596.1496 | [6 empty] | 0 | 596.1496 | 1432.2233 | [13 empty] | 40742.8719 | 60.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56842.6602 | -142.9978
| 40742.872 | 60.051 | 0 |  |  |  | -145.8562 | -145.8562 |  | 0 | -148.7107 | 0 | 323.1473 | 3.3309 | 211.1563 | 596.1496 | [6 empty] | 0 | 596.1496 | 1398.6401 | [13 empty] | 40742.872 | 60.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.2812 | -145.8562
| 40742.872 | 60.049 | 0 |  |  |  | -140.1394 | -140.1394 |  | 0 | -142.9938 | 0 | 320.0603 | 3.3309 | 209.7708 | 596.1496 | [6 empty] | 0 | 596.1496 | 1467.459 | [13 empty] | 40742.872 | 60.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.2812 | -140.1394
| 40742.872 | 60.048 | 0 |  |  |  | -137.281 | -137.281 |  | 0 | -140.1354 | 0 | 317.0327 | 3.3309 | 208.4037 | 596.1496 | [6 empty] | 0 | 596.1496 | 1504.4722 | [13 empty] | 40742.872 | 60.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56850.6172 | -137.281
| 40742.872 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 314.082 | 3.3309 | 207.0545 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.872 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56850.6172 | -131.5641
| 40742.8721 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 311.1697 | 3.3309 | 205.723 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8721 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56870.9102 | -131.5641
| 40742.8721 | 60.042 | 0 |  |  |  | -120.1195 | -120.1195 |  | 0 | -122.9739 | 0 | 308.3687 | 3.3309 | 204.4087 | 596.1496 | [6 empty] | 0 | 596.1496 | 1772.9542 | [13 empty] | 40742.8721 | 60.042 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56870.9102 | -120.1195
| 40742.8721 | 60.044 | 0 |  |  |  | -125.8363 | -125.8363 |  | 0 | -128.6908 | 0 | 305.5671 | 3.3309 | 203.1115 | 596.1496 | [6 empty] | 0 | 596.1496 | 1673.4706 | [13 empty] | 40742.8721 | 60.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.5547 | -125.8363
| 40742.8721 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 302.7829 | 3.3309 | 201.8308 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8721 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.5547 | -128.6948
| 40742.8722 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 300.034 | 3.3309 | 200.5665 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8722 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56848.6172 | -128.6948
| 40742.8722 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 297.3196 | 3.3309 | 199.3182 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8722 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56848.6172 | -128.6948
| 40742.8722 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 294.6392 | 3.3309 | 198.0855 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8722 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.1992 | -128.6948
| 40742.8722 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 291.992 | 3.3309 | 196.8683 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8722 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.1992 | -128.6948
| 40742.8722 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 289.3599 | 3.3309 | 195.6662 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8722 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.8828 | -131.5641
| 40742.8723 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 286.76 | 3.3309 | 194.479 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8723 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.8828 | -131.5641
| 40742.8723 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 284.2093 | 3.3309 | 193.3063 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8723 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56851.7969 | -128.6948
| 40742.8723 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 281.6722 | 3.3309 | 192.1479 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8723 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56851.7969 | -131.5641
| 40742.8723 | 60.044 | 0 |  |  |  | -125.8363 | -125.8363 |  | 0 | -128.6908 | 0 | 279.2001 | 3.3309 | 191.0035 | 596.1496 | [6 empty] | 0 | 596.1496 | 1673.4706 | [13 empty] | 40742.8723 | 60.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.9805 | -125.8363
| 40742.8724 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 276.7234 | 3.3309 | 189.873 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8724 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56861.9805 | -131.5641
| 40742.8724 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 274.2761 | 3.3309 | 188.756 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8724 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56851.0195 | -131.5641
| 40742.8724 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 271.8578 | 3.3309 | 187.6522 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8724 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56851.0195 | -131.5641
| 40742.8724 | 60.047 | 0 |  |  |  | -134.4225 | -134.4225 |  | 0 | -137.277 | 0 | 269.4511 | 3.3309 | 186.5616 | 596.1496 | [6 empty] | 0 | 596.1496 | 1543.4008 | [13 empty] | 40742.8724 | 60.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.1289 | -134.4225
| 40742.8725 | 60.047 | 0 |  |  |  | -134.4225 | -134.4225 |  | 0 | -137.277 | 0 | 267.0726 | 3.3309 | 185.4838 | 596.1496 | [6 empty] | 0 | 596.1496 | 1543.4008 | [13 empty] | 40742.8725 | 60.047 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.1289 | -134.4225
| 40742.8725 | 60.048 | 0 |  |  |  | -137.281 | -137.281 |  | 0 | -140.1354 | 0 | 264.7051 | 3.3309 | 184.4185 | 596.1496 | [6 empty] | 0 | 596.1496 | 1504.4722 | [13 empty] | 40742.8725 | 60.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56847.9492 | -137.281
| 40742.8725 | 60.05 | 0 |  |  |  | -142.9978 | -142.9978 |  | 0 | -145.8522 | 0 | 262.3319 | 3.3309 | 183.3657 | 596.1496 | [6 empty] | 0 | 596.1496 | 1432.2233 | [13 empty] | 40742.8725 | 60.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56847.9492 | -142.9978
| 40742.8725 | 60.052 | 0 |  |  |  | -148.7147 | -148.7147 |  | 0 | -151.5691 | 0 | 259.9532 | 3.3309 | 182.325 | 596.1496 | [6 empty] | 0 | 596.1496 | 1366.5957 | [13 empty] | 40742.8725 | 60.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56843.6641 | -148.7147
| 40742.8725 | 60.052 | 0 |  |  |  | -148.7147 | -148.7147 |  | 0 | -151.5691 | 0 | 257.6016 | 3.3309 | 181.2963 | 596.1496 | [6 empty] | 0 | 596.1496 | 1366.5957 | [13 empty] | 40742.8725 | 60.052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56843.6641 | -148.7147
| 40742.8726 | 60.049 | 0 |  |  |  | -140.1394 | -140.1394 |  | 0 | -142.9938 | 0 | 255.3255 | 3.3309 | 180.2794 | 596.1496 | [6 empty] | 0 | 596.1496 | 1467.459 | [13 empty] | 40742.8726 | 60.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.3945 | -140.1394
| 40742.8726 | 60.048 | 0 |  |  |  | -137.281 | -137.281 |  | 0 | -140.1354 | 0 | 253.0913 | 3.3309 | 179.274 | 596.1496 | [6 empty] | 0 | 596.1496 | 1504.4722 | [13 empty] | 40742.8726 | 60.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.3945 | -137.281
| 40742.8726 | 60.049 | 0 |  |  |  | -140.1394 | -140.1394 |  | 0 | -142.9938 | 0 | 250.8661 | 3.3309 | 178.28 | 596.1496 | [6 empty] | 0 | 596.1496 | 1467.459 | [13 empty] | 40742.8726 | 60.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56814.3828 | -140.1394
| 40742.8726 | 60.051 | 0 |  |  |  | -145.8562 | -145.8562 |  | 0 | -148.7107 | 0 | 248.6338 | 3.3309 | 177.2971 | 596.1496 | [6 empty] | 0 | 596.1496 | 1398.6401 | [13 empty] | 40742.8726 | 60.051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56814.3828 | -145.8562
| 40742.8727 | 60.05 | 0 |  |  |  | -142.9978 | -142.9978 |  | 0 | -145.8522 | 0 | 246.4422 | 3.3309 | 176.3252 | 596.1496 | [6 empty] | 0 | 596.1496 | 1432.2233 | [13 empty] | 40742.8727 | 60.05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56817.1602 | -142.9978
| 40742.8727 | 60.049 | 0 |  |  |  | -140.1394 | -140.1394 |  | 0 | -142.9938 | 0 | 244.2907 | 3.3309 | 175.3642 | 596.1496 | [6 empty] | 0 | 596.1496 | 1467.459 | [13 empty] | 40742.8727 | 60.049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56817.1602 | -140.1394
| 40742.8727 | 60.048 | 0 |  |  |  | -137.281 | -137.281 |  | 0 | -140.1354 | 0 | 242.1784 | 3.3309 | 174.4137 | 596.1496 | [6 empty] | 0 | 596.1496 | 1504.4722 | [13 empty] | 40742.8727 | 60.048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56805.5156 | -137.281
| 40742.8727 | 60.046 | 0 |  |  |  | -131.5641 | -131.5641 |  | 0 | -134.4185 | 0 | 240.1205 | 3.3309 | 173.4737 | 596.1496 | [6 empty] | 0 | 596.1496 | 1584.3975 | [13 empty] | 40742.8727 | 60.046 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56805.5156 | -131.5641
| 40742.8728 | 60.044 | 0 |  |  |  | -125.8363 | -125.8363 |  | 0 | -128.6908 | 0 | 238.1161 | 3.3309 | 172.5439 | 596.1496 | [6 empty] | 0 | 596.1496 | 1673.4706 | [13 empty] | 40742.8728 | 60.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56807.832 | -125.8363
| 40742.8728 | 60.043 | 0 |  |  |  | -122.9779 | -122.9779 |  | 0 | -125.8323 | 0 | 236.1488 | 3.3309 | 171.6243 | 596.1496 | [6 empty] | 0 | 596.1496 | 1721.7765 | [13 empty] | 40742.8728 | 60.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56807.832 | -122.9779
| 40742.8728 | 60.045 | 0 |  |  |  | -128.6948 | -128.6948 |  | 0 | -131.5492 | 0 | 234.1719 | 3.3309 | 170.7146 | 596.1496 | [6 empty] | 0 | 596.1496 | 1627.8011 | [13 empty] | 40742.8728 | 60.045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.4102 | -128.6948
| 40742.8728 | 60.044 | 0 |  |  |  | -125.8363 | -125.8363 |  | 0 | -128.6908 | 0 | 232.2315 | 3.3309 | 169.8147 | 596.1496 | [6 empty] | 0 | 596.1496 | 1673.4706 | [13 empty] | 40742.8728 | 60.044 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.4102 | -125.8363
| 40742.8728 | 60.04 | 0 |  |  |  | -114.4026 | -114.4026 |  | 0 | -117.257 | 0 | 230.3725 | 3.3309 | 168.9244 | 596.1496 | [6 empty] | 0 | 596.1496 | 1885.0135 | [13 empty] | 40742.8728 | 60.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56821.6875 | -114.4026
| 40742.8729 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 228.5635 | 3.3309 | 168.0436 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8729 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56821.6875 | -108.6749
| 40742.8729 | 60.036 | 0 |  |  |  | -102.958 | -102.958 |  | 0 | -105.8124 | 0 | 226.8036 | 3.3309 | 167.1721 | 596.1496 | [6 empty] | 0 | 596.1496 | 2158.0756 | [13 empty] | 40742.8729 | 60.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.9492 | -102.958
| 40742.8729 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 225.0772 | 3.3309 | 166.3098 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8729 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.9492 | -100.0996
| 40742.8729 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 223.4283 | 3.3309 | 165.4565 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8729 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56860.5078 | -88.6549
| 40742.873 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 221.8113 | 3.3309 | 164.6121 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.873 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56860.5078 | -85.7965
| 40742.873 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 220.211 | 3.3309 | 163.7764 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.873 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56877.5938 | -85.7965
| 40742.873 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 218.5977 | 3.3309 | 162.9494 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.873 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56877.5938 | -91.5243
| 40742.873 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 216.9863 | 3.3309 | 162.1308 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.873 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56918.6641 | -94.3827
| 40742.8731 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 215.3912 | 3.3309 | 161.3206 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8731 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56918.6641 | -94.3827
| 40742.8731 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 213.8267 | 3.3309 | 160.5186 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8731 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56891.7109 | -91.5243
| 40742.8731 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 212.2349 | 3.3309 | 159.7248 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8731 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56891.7109 | -100.0996
| 40742.8731 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 210.6161 | 3.3309 | 158.9389 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8731 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56894.3477 | -108.6749
| 40742.8731 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 208.9991 | 3.3309 | 158.1608 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8731 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56894.3477 | -111.5442
| 40742.8732 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 207.4123 | 3.3309 | 157.3905 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8732 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56895.168 | -108.6749
| 40742.8732 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 205.827 | 3.3309 | 156.6279 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8732 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56895.168 | -111.5442
| 40742.8732 | 60.04 | 0 |  |  |  | -114.4026 | -114.4026 |  | 0 | -117.257 | 0 | 204.2433 | 3.3309 | 155.8727 | 596.1496 | [6 empty] | 0 | 596.1496 | 1885.0135 | [13 empty] | 40742.8732 | 60.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56889.7266 | -114.4026
| 40742.8732 | 60.04 | 0 |  |  |  | -114.4026 | -114.4026 |  | 0 | -117.257 | 0 | 202.675 | 3.3309 | 155.1249 | 596.1496 | [6 empty] | 0 | 596.1496 | 1885.0135 | [13 empty] | 40742.8732 | 60.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56889.7266 | -114.4026
| 40742.8733 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 201.1358 | 3.3309 | 154.3845 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8733 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56892.3945 | -111.5442
| 40742.8733 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 199.6115 | 3.3309 | 153.6512 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8733 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56892.3945 | -111.5442
| 40742.8733 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 198.1156 | 3.3309 | 152.925 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8733 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56875.332 | -108.6749
| 40742.8733 | 60.037 | 0 |  |  |  | -105.8164 | -105.8164 |  | 0 | -108.6708 | 0 | 196.6477 | 3.3309 | 152.2058 | 596.1496 | [6 empty] | 0 | 596.1496 | 2082.722 | [13 empty] | 40742.8733 | 60.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.0078 | -105.8164
| 40742.8734 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 195.221 | 3.3309 | 151.4935 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8734 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.0078 | -100.0996
| 40742.8734 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 193.8214 | 3.3309 | 150.788 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8734 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.0078 | -97.2411
| 40742.8734 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 192.435 | 3.3309 | 150.0891 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8734 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56881.0039 | -97.2411
| 40742.8734 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 191.0617 | 3.3309 | 149.3969 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8734 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56881.0039 | -97.2411
| 40742.8734 | 60.036 | 0 |  |  |  | -102.958 | -102.958 |  | 0 | -105.8124 | 0 | 189.6744 | 3.3309 | 148.7111 | 596.1496 | [6 empty] | 0 | 596.1496 | 2158.0756 | [13 empty] | 40742.8734 | 60.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56887.4492 | -102.958
| 40742.8735 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 188.3266 | 3.3309 | 148.0318 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8735 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56887.4492 | -97.2411
| 40742.8735 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 187.0178 | 3.3309 | 147.3587 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8735 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.082 | -91.5243
| 40742.8735 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 185.7079 | 3.3309 | 146.6919 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8735 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56882.082 | -94.3827
| 40742.8735 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 184.3969 | 3.3309 | 146.0313 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8735 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56879.1133 | -97.2411
| 40742.8736 | 60.036 | 0 |  |  |  | -102.958 | -102.958 |  | 0 | -105.8124 | 0 | 183.0717 | 3.3309 | 145.3767 | 596.1496 | [6 empty] | 0 | 596.1496 | 2158.0756 | [13 empty] | 40742.8736 | 60.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56879.1133 | -102.958
| 40742.8736 | 60.038 | 0 |  |  |  | -108.6749 | -108.6749 |  | 0 | -111.5293 | 0 | 181.7326 | 3.3309 | 144.7281 | 596.1496 | [6 empty] | 0 | 596.1496 | 2012.4531 | [13 empty] | 40742.8736 | 60.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.3555 | -108.6749
| 40742.8736 | 60.04 | 0 |  |  |  | -114.4026 | -114.4026 |  | 0 | -117.257 | 0 | 180.3797 | 3.3309 | 144.0854 | 596.1496 | [6 empty] | 0 | 596.1496 | 1885.0135 | [13 empty] | 40742.8736 | 60.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56884.3555 | -114.4026
| 40742.8736 | 60.039 | 0 |  |  |  | -111.5442 | -111.5442 |  | 0 | -114.3986 | 0 | 179.0519 | 3.3309 | 143.4485 | 596.1496 | [6 empty] | 0 | 596.1496 | 1946.5286 | [13 empty] | 40742.8736 | 60.039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.6328 | -111.5442
| 40742.8737 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 177.7873 | 3.3309 | 142.8173 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8737 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56872.6328 | -100.0996
| 40742.8737 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 176.534 | 3.3309 | 142.1918 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8737 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56865.5156 | -100.0996
| 40742.8737 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 175.3045 | 3.3309 | 141.5719 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8737 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56865.5156 | -97.2411
| 40742.8737 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 174.0986 | 3.3309 | 140.9575 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8737 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.4805 | -94.3827
| 40742.8737 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 172.9537 | 3.3309 | 140.3485 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8737 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56874.4805 | -82.9381
| 40742.8738 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 171.8063 | 3.3309 | 139.7449 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8738 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56866.3477 | -85.7965
| 40742.8738 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 170.6814 | 3.3309 | 139.1466 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8738 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56866.3477 | -82.9381
| 40742.8738 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 169.5787 | 3.3309 | 138.5535 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8738 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56868.5 | -80.0797
| 40742.8738 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 168.5103 | 3.3309 | 137.9656 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8738 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56868.5 | -74.3628
| 40742.8739 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 167.4265 | 3.3309 | 137.3828 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8739 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56865.5781 | -80.0797
| 40742.8739 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 166.3275 | 3.3309 | 136.805 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8739 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56865.5781 | -85.7965
| 40742.8739 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 165.2134 | 3.3309 | 136.2321 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8739 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56862.7578 | -91.5243
| 40742.8739 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 164.0965 | 3.3309 | 135.6642 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8739 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56862.7578 | -94.3827
| 40742.874 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 162.965 | 3.3309 | 135.101 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.874 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56871.1289 | -100.0996
| 40742.874 | 60.036 | 0 |  |  |  | -102.958 | -102.958 |  | 0 | -105.8124 | 0 | 161.8309 | 3.3309 | 134.5427 | 596.1496 | [6 empty] | 0 | 596.1496 | 2158.0756 | [13 empty] | 40742.874 | 60.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56871.1289 | -102.958
| 40742.874 | 60.037 | 0 |  |  |  | -105.8164 | -105.8164 |  | 0 | -108.6708 | 0 | 160.6943 | 3.3309 | 133.9891 | 596.1496 | [6 empty] | 0 | 596.1496 | 2082.722 | [13 empty] | 40742.874 | 60.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56863.4805 | -105.8164
| 40742.874 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 159.6032 | 3.3309 | 133.4401 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.874 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56863.4805 | -97.2411
| 40742.8741 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 158.5449 | 3.3309 | 132.8957 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8741 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56856.707 | -91.5243
| 40742.8741 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 157.5192 | 3.3309 | 132.3558 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8741 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56856.707 | -85.7965
| 40742.8741 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 156.5256 | 3.3309 | 131.8205 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8741 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56859.6719 | -80.0797
| 40742.8741 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 155.5402 | 3.3309 | 131.2895 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8741 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56859.6719 | -80.0797
| 40742.8741 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 154.5628 | 3.3309 | 130.7629 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8741 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56860.4062 | -80.0797
| 40742.8742 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 153.5934 | 3.3309 | 130.2407 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8742 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56860.4062 | -80.0797
| 40742.8742 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 152.6087 | 3.3309 | 129.7227 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8742 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56867.3125 | -85.7965
| 40742.8742 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 151.6435 | 3.3309 | 129.2089 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8742 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56867.3125 | -82.9381
| 40742.8742 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 150.6746 | 3.3309 | 128.6993 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8742 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56852.1367 | -85.7965
| 40742.8743 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 149.6904 | 3.3309 | 128.1937 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8743 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56852.1367 | -91.5243
| 40742.8743 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 148.6798 | 3.3309 | 127.6923 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8743 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.8125 | -100.0996
| 40742.8743 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 147.6773 | 3.3309 | 127.1948 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8743 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56838.8125 | -100.0996
| 40742.8743 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 146.6828 | 3.3309 | 126.7014 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8743 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56839.6406 | -100.0996
| 40742.8744 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 145.7073 | 3.3309 | 126.2118 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8744 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56839.6406 | -97.2411
| 40742.8744 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 144.7509 | 3.3309 | 125.7261 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8744 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56839.9648 | -94.3827
| 40742.8744 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 143.7907 | 3.3309 | 125.2442 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8744 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56839.9648 | -97.2411
| 40742.8744 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 142.838 | 3.3309 | 124.7661 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8744 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56841.0078 | -97.2411
| 40742.8744 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 141.8927 | 3.3309 | 124.2918 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8744 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56841.0078 | -97.2411
| 40742.8745 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 140.9659 | 3.3309 | 123.8211 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8745 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.9023 | -94.3827
| 40742.8745 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 140.0904 | 3.3309 | 123.3541 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8745 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56854.9023 | -82.9381
| 40742.8745 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 139.2436 | 3.3309 | 122.8907 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8745 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.9961 | -77.2212
| 40742.8745 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 138.4252 | 3.3309 | 122.4308 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8745 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56845.9961 | -71.5044
| 40742.8746 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 137.613 | 3.3309 | 121.9745 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8746 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.0703 | -71.5044
| 40742.8746 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 136.7962 | 3.3309 | 121.5217 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8746 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.0703 | -74.3628
| 40742.8746 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 135.9855 | 3.3309 | 121.0723 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8746 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.2773 | -74.3628
| 40742.8746 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 135.1918 | 3.3309 | 120.6263 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8746 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56827.2773 | -71.5044
| 40742.8747 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 134.3932 | 3.3309 | 120.1837 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8747 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56829.4219 | -74.3628
| 40742.8747 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 133.59 | 3.3309 | 119.7444 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8747 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56829.4219 | -77.2212
| 40742.8747 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 132.7927 | 3.3309 | 119.3084 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8747 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56846.6562 | -77.2212
| 40742.8747 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 131.9908 | 3.3309 | 118.8756 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8747 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56846.6562 | -80.0797
| 40742.8747 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 131.1736 | 3.3309 | 118.4461 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8747 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56840.5703 | -85.7965
| 40742.8748 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 130.373 | 3.3309 | 118.0197 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8748 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56840.5703 | -82.9381
| 40742.8748 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 129.5677 | 3.3309 | 117.5965 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8748 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56831.9141 | -85.7965
| 40742.8748 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 128.7893 | 3.3309 | 117.1764 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8748 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56831.9141 | -80.0797
| 40742.8748 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 128.0375 | 3.3309 | 116.7594 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8748 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.3516 | -74.3628
| 40742.8749 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 127.2807 | 3.3309 | 116.3454 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8749 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.3516 | -77.2212
| 40742.8749 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 126.5087 | 3.3309 | 115.9345 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8749 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.6328 | -82.9381
| 40742.8749 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 125.732 | 3.3309 | 115.5265 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8749 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.6328 | -85.7965
| 40742.8749 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 124.9402 | 3.3309 | 115.1214 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8749 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56828 | -91.5243
| 40742.875 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 124.1849 | 3.3309 | 114.7193 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.875 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56828 | -82.9381
| 40742.875 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 123.435 | 3.3309 | 114.3201 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.875 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56828 | -82.9381
| 40742.875 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 122.6598 | 3.3309 | 113.9237 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.875 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56828 | -91.5243
| 40742.875 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 121.88 | 3.3309 | 113.5301 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.875 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.8008 | -94.3827
| 40742.875 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 121.1058 | 3.3309 | 113.1393 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.875 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56833.8008 | -94.3827
| 40742.8751 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 120.347 | 3.3309 | 112.7513 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8751 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56806.8594 | -91.5243
| 40742.8751 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 119.6137 | 3.3309 | 112.366 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8751 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56806.8594 | -85.7965
| 40742.8751 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 118.8955 | 3.3309 | 111.9835 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8751 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56813.1758 | -82.9381
| 40742.8751 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 118.1424 | 3.3309 | 111.6036 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8751 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56813.1758 | -94.3827
| 40742.8752 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 117.3747 | 3.3309 | 111.2263 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8752 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56804.2734 | -100.0996
| 40742.8752 | 60.035 | 0 |  |  |  | -100.0996 | -100.0996 |  | 0 | -102.954 | 0 | 116.6123 | 3.3309 | 110.8517 | 596.1496 | [6 empty] | 0 | 596.1496 | 2239.0866 | [13 empty] | 40742.8752 | 60.035 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56804.2734 | -100.0996
| 40742.8752 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 115.8947 | 3.3309 | 110.4796 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8752 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56787.3438 | -88.6549
| 40742.8752 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 115.1721 | 3.3309 | 110.1101 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8752 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56787.3438 | -91.5243
| 40742.8753 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 114.4839 | 3.3309 | 109.7432 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8753 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56786.8438 | -82.9381
| 40742.8753 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 113.8198 | 3.3309 | 109.3788 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8753 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56786.8438 | -77.2212
| 40742.8753 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 113.17 | 3.3309 | 109.0168 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8753 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56773.4883 | -74.3628
| 40742.8753 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 112.515 | 3.3309 | 108.6574 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8753 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56773.4883 | -77.2212
| 40742.8753 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 111.8643 | 3.3309 | 108.3003 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8753 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56759.3672 | -77.2212
| 40742.8754 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 111.2277 | 3.3309 | 107.9457 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8754 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56759.3672 | -74.3628
| 40742.8754 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 110.5953 | 3.3309 | 107.5935 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8754 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56742.3398 | -74.3628
| 40742.8754 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 109.9481 | 3.3309 | 107.2436 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8754 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56742.3398 | -80.0797
| 40742.8754 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 109.3051 | 3.3309 | 106.8961 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8754 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56734.9805 | -80.0797
| 40742.8755 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 108.676 | 3.3309 | 106.5508 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8755 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56734.9805 | -77.2212
| 40742.8755 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 108.0604 | 3.3309 | 106.2079 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8755 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56750.6172 | -74.3628
| 40742.8755 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 107.4395 | 3.3309 | 105.8673 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8755 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56750.6172 | -77.2212
| 40742.8755 | 60.028 | 0 |  |  |  | -80.0797 | -80.0797 |  | 0 | -82.9341 | 0 | 106.8133 | 3.3309 | 105.5289 | 596.1496 | [6 empty] | 0 | 596.1496 | 3037.75 | [13 empty] | 40742.8755 | 60.028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56746.8867 | -80.0797
| 40742.8756 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 106.2005 | 3.3309 | 105.1927 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8756 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56746.8867 | -77.2212
| 40742.8756 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 105.5918 | 3.3309 | 104.8587 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8756 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56753.2773 | -77.2212
| 40742.8756 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 104.987 | 3.3309 | 104.5269 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8756 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56753.2773 | -77.2212
| 40742.8756 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 104.3862 | 3.3309 | 104.1973 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8756 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56749.9648 | -77.2212
| 40742.8756 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 103.8077 | 3.3309 | 103.8698 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8756 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56749.9648 | -71.5044
| 40742.8757 | 60.024 | 0 |  |  |  | -68.635 | -68.635 |  | 0 | -71.4894 | 0 | 103.2422 | 3.3309 | 103.5444 | 596.1496 | [6 empty] | 0 | 596.1496 | 3815.8234 | [13 empty] | 40742.8757 | 60.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56728.9453 | -68.635
| 40742.8757 | 60.024 | 0 |  |  |  | -68.635 | -68.635 |  | 0 | -71.4894 | 0 | 102.6804 | 3.3309 | 103.2212 | 596.1496 | [6 empty] | 0 | 596.1496 | 3815.8234 | [13 empty] | 40742.8757 | 60.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56728.9453 | -68.635
| 40742.8757 | 60.024 | 0 |  |  |  | -68.635 | -68.635 |  | 0 | -71.4894 | 0 | 102.1221 | 3.3309 | 102.9 | 596.1496 | [6 empty] | 0 | 596.1496 | 3815.8234 | [13 empty] | 40742.8757 | 60.024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56723.3242 | -68.635
| 40742.8757 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 101.5583 | 3.3309 | 102.5808 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8757 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56723.3242 | -71.5044
| 40742.8758 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 100.9981 | 3.3309 | 102.2637 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8758 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56715.2227 | -71.5044
| 40742.8758 | 60.026 | 0 |  |  |  | -74.3628 | -74.3628 |  | 0 | -77.2172 | 0 | 100.4323 | 3.3309 | 101.9487 | 596.1496 | [6 empty] | 0 | 596.1496 | 3382.254 | [13 empty] | 40742.8758 | 60.026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56715.2227 | -74.3628
| 40742.8758 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 99.8792 | 3.3309 | 101.6356 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8758 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56724.0977 | -71.5044
| 40742.8758 | 60.023 | 0 |  |  |  | -65.7766 | -65.7766 |  | 0 | -68.631 | 0 | 99.3476 | 3.3309 | 101.3245 | 596.1496 | [6 empty] | 0 | 596.1496 | 4076.6153 | [13 empty] | 40742.8758 | 60.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56724.0977 | -65.7766
| 40742.8759 | 60.022 | 0 |  |  |  | -62.9182 | -62.9182 |  | 0 | -65.7726 | 0 | 98.8283 | 3.3309 | 101.0154 | 596.1496 | [6 empty] | 0 | 596.1496 | 4375.6698 | [13 empty] | 40742.8759 | 60.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56718.9062 | -62.9182
| 40742.8759 | 60.021 | 0 |  |  |  | -60.0597 | -60.0597 |  | 0 | -62.9142 | 0 | 98.3213 | 3.3309 | 100.7082 | 596.1496 | [6 empty] | 0 | 596.1496 | 4722.0743 | [13 empty] | 40742.8759 | 60.021 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56718.9062 | -60.0597
| 40742.8759 | 60.02 | 0 |  |  |  | -57.2013 | -57.2013 |  | 0 | -60.0557 | 0 | 97.8264 | 3.3309 | 100.4029 | 596.1496 | [6 empty] | 0 | 596.1496 | 5128.041 | [13 empty] | 40742.8759 | 60.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56704.9922 | -57.2013
| 40742.8759 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 97.3523 | 3.3309 | 100.0996 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.8759 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56704.9922 | -51.4845
| 40742.8759 | 60.015 | 0 |  |  |  | -42.8983 | -42.8983 |  | 0 | -45.7527 | 0 | 96.9079 | 3.3309 | 99.7981 | 596.1496 | [6 empty] | 0 | 596.1496 | 8999.5421 | [13 empty] | 40742.8759 | 60.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56708.4766 | -42.8983
| 40742.876 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 96.4839 | 3.3309 | 99.4985 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.876 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56708.4766 | -37.1814
| 40742.876 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 96.0626 | 3.3309 | 99.2008 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.876 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56730.4492 | -37.1814
| 40742.876 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 95.6438 | 3.3309 | 98.9049 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.876 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56730.4492 | -37.1814
| 40742.876 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 95.2189 | 3.3309 | 98.6108 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.876 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56720.1562 | -40.0398
| 40742.8761 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 94.7965 | 3.3309 | 98.3186 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.8761 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56720.1562 | -40.0398
| 40742.8761 | 60.015 | 0 |  |  |  | -42.8983 | -42.8983 |  | 0 | -45.7527 | 0 | 94.368 | 3.3309 | 98.0281 | 596.1496 | [6 empty] | 0 | 596.1496 | 8999.5421 | [13 empty] | 40742.8761 | 60.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56711.6289 | -42.8983
| 40742.8761 | 60.017 | 0 |  |  |  | -48.6151 | -48.6151 |  | 0 | -51.4695 | 0 | 93.9247 | 3.3309 | 97.7394 | 596.1496 | [6 empty] | 0 | 596.1496 | 6913.3841 | [13 empty] | 40742.8761 | 60.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56711.6289 | -48.6151
| 40742.8761 | 60.016 | 0 |  |  |  | -45.7567 | -45.7567 |  | 0 | -48.6111 | 0 | 93.4928 | 3.3309 | 97.4524 | 596.1496 | [6 empty] | 0 | 596.1496 | 7819.7172 | [13 empty] | 40742.8761 | 60.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56708.6641 | -45.7567
| 40742.8762 | 60.016 | 0 |  |  |  | -45.7567 | -45.7567 |  | 0 | -48.6111 | 0 | 93.0635 | 3.3309 | 97.1672 | 596.1496 | [6 empty] | 0 | 596.1496 | 7819.7172 | [13 empty] | 40742.8762 | 60.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56708.6641 | -45.7567
| 40742.8762 | 60.016 | 0 |  |  |  | -45.7567 | -45.7567 |  | 0 | -48.6111 | 0 | 92.6367 | 3.3309 | 96.8837 | 596.1496 | [6 empty] | 0 | 596.1496 | 7819.7172 | [13 empty] | 40742.8762 | 60.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56706.6133 | -45.7567
| 40742.8762 | 60.015 | 0 |  |  |  | -42.8983 | -42.8983 |  | 0 | -45.7527 | 0 | 92.2212 | 3.3309 | 96.6019 | 596.1496 | [6 empty] | 0 | 596.1496 | 8999.5421 | [13 empty] | 40742.8762 | 60.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56706.6133 | -42.8983
| 40742.8762 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 91.8166 | 3.3309 | 96.3218 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.8762 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56716.5508 | -40.0398
| 40742.8762 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 91.423 | 3.3309 | 96.0434 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.8762 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56716.5508 | -37.1814
| 40742.8763 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 91.0233 | 3.3309 | 95.7667 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.8763 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56705.832 | -40.0398
| 40742.8763 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 90.5919 | 3.3309 | 95.4916 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.8763 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56705.832 | -51.4845
| 40742.8763 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 90.1631 | 3.3309 | 95.2181 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.8763 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56696.3867 | -51.4845
| 40742.8763 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 89.7369 | 3.3309 | 94.9462 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.8763 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56696.3867 | -51.4845
| 40742.8764 | 60.016 | 0 |  |  |  | -45.7567 | -45.7567 |  | 0 | -48.6111 | 0 | 89.33 | 3.3309 | 94.676 | 596.1496 | [6 empty] | 0 | 596.1496 | 7819.7172 | [13 empty] | 40742.8764 | 60.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56670.6172 | -45.7567
| 40742.8764 | 60.017 | 0 |  |  |  | -48.6151 | -48.6151 |  | 0 | -51.4695 | 0 | 88.9171 | 3.3309 | 94.4073 | 596.1496 | [6 empty] | 0 | 596.1496 | 6913.3841 | [13 empty] | 40742.8764 | 60.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56670.6172 | -48.6151
| 40742.8764 | 60.025 | 0 |  |  |  | -71.5044 | -71.5044 |  | 0 | -74.3588 | 0 | 88.4397 | 3.3309 | 94.1402 | 596.1496 | [6 empty] | 0 | 596.1496 | 3585.5695 | [13 empty] | 40742.8764 | 60.025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56642.6875 | -71.5044
| 40742.8764 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 87.9234 | 3.3309 | 93.8747 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8764 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56642.6875 | -85.7965
| 40742.8765 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 87.3934 | 3.3309 | 93.6107 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8765 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56644.3242 | -91.5243
| 40742.8765 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 86.85 | 3.3309 | 93.3483 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8765 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56644.3242 | -97.2411
| 40742.8765 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 86.3179 | 3.3309 | 93.0874 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8765 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56636.4062 | -94.3827
| 40742.8765 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 85.7889 | 3.3309 | 92.828 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8765 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56636.4062 | -94.3827
| 40742.8766 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 85.263 | 3.3309 | 92.57 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8766 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56630.7461 | -94.3827
| 40742.8766 | 60.033 | 0 |  |  |  | -94.3827 | -94.3827 |  | 0 | -97.2371 | 0 | 84.7401 | 3.3309 | 92.3136 | 596.1496 | [6 empty] | 0 | 596.1496 | 2420.8357 | [13 empty] | 40742.8766 | 60.033 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56630.7461 | -94.3827
| 40742.8766 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 84.212 | 3.3309 | 92.0586 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8766 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56620.9141 | -97.2411
| 40742.8766 | 60.037 | 0 |  |  |  | -105.8164 | -105.8164 |  | 0 | -108.6708 | 0 | 83.6625 | 3.3309 | 91.8051 | 596.1496 | [6 empty] | 0 | 596.1496 | 2082.722 | [13 empty] | 40742.8766 | 60.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56620.9141 | -105.8164
| 40742.8766 | 60.036 | 0 |  |  |  | -102.958 | -102.958 |  | 0 | -105.8124 | 0 | 83.1242 | 3.3309 | 91.5531 | 596.1496 | [6 empty] | 0 | 596.1496 | 2158.0756 | [13 empty] | 40742.8766 | 60.036 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56619 | -102.958
| 40742.8767 | 60.034 | 0 |  |  |  | -97.2411 | -97.2411 |  | 0 | -100.0956 | 0 | 82.6051 | 3.3309 | 91.3024 | 596.1496 | [6 empty] | 0 | 596.1496 | 2326.4168 | [13 empty] | 40742.8767 | 60.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56619 | -97.2411
| 40742.8767 | 60.03 | 0 |  |  |  | -85.7965 | -85.7965 |  | 0 | -88.6509 | 0 | 82.1214 | 3.3309 | 91.0532 | 596.1496 | [6 empty] | 0 | 596.1496 | 2756.9383 | [13 empty] | 40742.8767 | 60.03 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56610.4453 | -85.7965
| 40742.8767 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 81.6242 | 3.3309 | 90.8054 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8767 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56610.4453 | -91.5243
| 40742.8767 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 81.1379 | 3.3309 | 90.559 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8767 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56598.0625 | -88.6549
| 40742.8768 | 60.032 | 0 |  |  |  | -91.5243 | -91.5243 |  | 0 | -94.3787 | 0 | 80.6462 | 3.3309 | 90.314 | 596.1496 | [6 empty] | 0 | 596.1496 | 2523.2429 | [13 empty] | 40742.8768 | 60.032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56598.0625 | -91.5243
| 40742.8768 | 60.031 | 0 |  |  |  | -88.6549 | -88.6549 |  | 0 | -91.5094 | 0 | 80.1653 | 3.3309 | 90.0703 | 596.1496 | [6 empty] | 0 | 596.1496 | 2635.1412 | [13 empty] | 40742.8768 | 60.031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56587.0469 | -88.6549
| 40742.8768 | 60.029 | 0 |  |  |  | -82.9381 | -82.9381 |  | 0 | -85.7925 | 0 | 79.7031 | 3.3309 | 89.8281 | 596.1496 | [6 empty] | 0 | 596.1496 | 2890.5401 | [13 empty] | 40742.8768 | 60.029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56589.8906 | -82.9381
| 40742.8768 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 79.2592 | 3.3309 | 89.5871 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8768 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56589.8906 | -77.2212
| 40742.8769 | 60.027 | 0 |  |  |  | -77.2212 | -77.2212 |  | 0 | -80.0756 | 0 | 78.8179 | 3.3309 | 89.3475 | 596.1496 | [6 empty] | 0 | 596.1496 | 3200.7588 | [13 empty] | 40742.8769 | 60.027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56589.8906 | -77.2212
| 40742.8769 | 60.023 | 0 |  |  |  | -65.7766 | -65.7766 |  | 0 | -68.631 | 0 | 78.4105 | 3.3309 | 89.1092 | 596.1496 | [6 empty] | 0 | 596.1496 | 4076.6153 | [13 empty] | 40742.8769 | 60.023 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56581.125 | -65.7766
| 40742.8769 | 60.022 | 0 |  |  |  | -62.9182 | -62.9182 |  | 0 | -65.7726 | 0 | 78.0133 | 3.3309 | 88.8723 | 596.1496 | [6 empty] | 0 | 596.1496 | 4375.6698 | [13 empty] | 40742.8769 | 60.022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56581.125 | -62.9182
| 40742.8769 | 60.02 | 0 |  |  |  | -57.2013 | -57.2013 |  | 0 | -60.0557 | 0 | 77.634 | 3.3309 | 88.6366 | 596.1496 | [6 empty] | 0 | 596.1496 | 5128.041 | [13 empty] | 40742.8769 | 60.02 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56587.6914 | -57.2013
| 40742.8769 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 77.2725 | 3.3309 | 88.4023 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.8769 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56587.6914 | -51.4845
| 40742.877 | 60.019 | 0 |  |  |  | -54.3429 | -54.3429 |  | 0 | -57.1973 | 0 | 76.9051 | 3.3309 | 88.1692 | 596.1496 | [6 empty] | 0 | 596.1496 | 5610.3769 | [13 empty] | 40742.877 | 60.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56605.1953 | -54.3429
| 40742.877 | 60.018 | 0 |  |  |  | -51.4845 | -51.4845 |  | 0 | -54.3389 | 0 | 76.5474 | 3.3309 | 87.9374 | 596.1496 | [6 empty] | 0 | 596.1496 | 6192.869 | [13 empty] | 40742.877 | 60.018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56605.1953 | -51.4845
| 40742.877 | 60.019 | 0 |  |  |  | -54.3429 | -54.3429 |  | 0 | -57.1973 | 0 | 76.184 | 3.3309 | 87.7069 | 596.1496 | [6 empty] | 0 | 596.1496 | 5610.3769 | [13 empty] | 40742.877 | 60.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56592.7812 | -54.3429
| 40742.877 | 60.019 | 0 |  |  |  | -54.3429 | -54.3429 |  | 0 | -57.1973 | 0 | 75.8225 | 3.3309 | 87.4776 | 596.1496 | [6 empty] | 0 | 596.1496 | 5610.3769 | [13 empty] | 40742.877 | 60.019 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56592.7812 | -54.3429
| 40742.8771 | 60.017 | 0 |  |  |  | -48.6151 | -48.6151 |  | 0 | -51.4695 | 0 | 75.4785 | 3.3309 | 87.2495 | 596.1496 | [6 empty] | 0 | 596.1496 | 6913.3841 | [13 empty] | 40742.8771 | 60.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56586.0508 | -48.6151
| 40742.8771 | 60.016 | 0 |  |  |  | -45.7567 | -45.7567 |  | 0 | -48.6111 | 0 | 75.144 | 3.3309 | 87.0227 | 596.1496 | [6 empty] | 0 | 596.1496 | 7819.7172 | [13 empty] | 40742.8771 | 60.016 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56586.0508 | -45.7567
| 40742.8771 | 60.017 | 0 |  |  |  | -48.6151 | -48.6151 |  | 0 | -51.4695 | 0 | 74.8037 | 3.3309 | 86.7972 | 596.1496 | [6 empty] | 0 | 596.1496 | 6913.3841 | [13 empty] | 40742.8771 | 60.017 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56581.3828 | -48.6151
| 40742.8771 | 60.015 | 0 |  |  |  | -42.8983 | -42.8983 |  | 0 | -45.7527 | 0 | 74.4805 | 3.3309 | 86.5728 | 596.1496 | [6 empty] | 0 | 596.1496 | 8999.5421 | [13 empty] | 40742.8771 | 60.015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56581.3828 | -42.8983
| 40742.8772 | 60.014 | 0 |  |  |  | -40.0398 | -40.0398 |  | 0 | -42.8942 | 0 | 74.1666 | 3.3309 | 86.3496 | 596.1496 | [6 empty] | 0 | 596.1496 | 10598.6469 | [13 empty] | 40742.8772 | 60.014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56576.918 | -40.0398
| 40742.8772 | 60.012 | 0 |  |  |  | -34.323 | -34.323 |  | 0 | -37.1774 | 0 | 73.8697 | 3.3309 | 86.1276 | 596.1496 | [6 empty] | 0 | 596.1496 | 16441.5621 | [13 empty] | 40742.8772 | 60.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56576.918 | -34.323
| 40742.8772 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 73.582 | 3.3309 | 85.9068 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.8772 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56570.8984 | -31.4645
| 40742.8772 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 73.2958 | 3.3309 | 85.6872 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.8772 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56570.8984 | -31.4645
| 40742.8772 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 73.0111 | 3.3309 | 85.4688 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.8772 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56585.2969 | -31.4645
| 40742.8773 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 72.7128 | 3.3309 | 85.2515 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.8773 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56585.2969 | -37.1814
| 40742.8773 | 60.013 | 0 |  |  |  | -37.1814 | -37.1814 |  | 0 | -40.0358 | 0 | 72.4161 | 3.3309 | 85.0353 | 596.1496 | [6 empty] | 0 | 596.1496 | 12888.8287 | [13 empty] | 40742.8773 | 60.013 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56579.2891 | -37.1814
| 40742.8773 | 60.012 | 0 |  |  |  | -34.323 | -34.323 |  | 0 | -37.1774 | 0 | 72.1284 | 3.3309 | 84.8203 | 596.1496 | [6 empty] | 0 | 596.1496 | 16441.5621 | [13 empty] | 40742.8773 | 60.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56579.2891 | -34.323
| 40742.8773 | 60.012 | 0 |  |  |  | -34.323 | -34.323 |  | 0 | -37.1774 | 0 | 71.8423 | 3.3309 | 84.6064 | 596.1496 | [6 empty] | 0 | 596.1496 | 16441.5621 | [13 empty] | 40742.8773 | 60.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56575.293 | -34.323
| 40742.8774 | 60.012 | 0 |  |  |  | -34.323 | -34.323 |  | 0 | -37.1774 | 0 | 71.5577 | 3.3309 | 84.3937 | 596.1496 | [6 empty] | 0 | 596.1496 | 16441.5621 | [13 empty] | 40742.8774 | 60.012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56575.293 | -34.323
| 40742.8774 | 60.011 | 0 |  |  |  | -31.4645 | -31.4645 |  | 0 | -34.319 | 0 | 71.2819 | 3.3309 | 84.182 | 596.1496 | [6 empty] | 0 | 596.1496 | 22698.1914 | [13 empty] | 40742.8774 | 60.011 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56567.6992 | -31.4645
| 40742.8774 | 60.007 | 0 |  |  |  | -20.0199 | -20.0199 |  | 0 | -22.8743 | 0 | 71.0374 | 3.3309 | 83.9715 | 596.1496 | [6 empty] | 0 | 596.1496 | -43350.0827 | [13 empty] | 40742.8774 | 60.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56567.6992 | -20.0199
| 40742.8774 | 60.004 | 0 |  |  |  | -11.4446 | -11.4446 |  | 0 | -14.2991 | 0 | 70.8163 | 3.3309 | 83.762 | 596.1496 | [6 empty] | 0 | 596.1496 | -13630.7935 | [13 empty] | 40742.8774 | 60.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56566.8633 | -11.4446
| 40742.8775 | 60.001 | 0 |  |  |  | -2.8584 | -2.8584 |  | 0 | -5.7129 | 0 | 70.6185 | 3.3309 | 83.5536 | 596.1496 | [6 empty] | 0 | 596.1496 | -8082.5988 | [13 empty] | 40742.8775 | 60.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56566.8633 | -2.8584
| 40742.8775 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 70.4439 | 3.3309 | 83.3463 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.8775 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56567.7969 | 5.7169
| 40742.8775 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 70.2702 | 3.3309 | 83.1401 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.8775 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56567.7969 | 5.7169
| 40742.8775 | 59.999 | 0 |  |  |  | 2.8584 | 2.8584 |  | 0 | 0.0040044 | 0 | 70.09 | 3.3309 | 82.935 | 596.1496 | [6 empty] | 0 | 596.1496 | -6359.1881 | [13 empty] | 40742.8775 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56565.918 | 2.8584
| 40742.8775 | 60.001 | 0 |  |  |  | -2.8584 | -2.8584 |  | 0 | -5.7129 | 0 | 69.8961 | 3.3309 | 82.7308 | 596.1496 | [6 empty] | 0 | 596.1496 | -8082.5988 | [13 empty] | 40742.8775 | 60.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56565.918 | -2.8584
| 40742.8776 | 60.002 | 0 |  |  |  | -5.7169 | -5.7169 |  | 0 | -8.5713 | 0 | 69.696 | 3.3309 | 82.5278 | 596.1496 | [6 empty] | 0 | 596.1496 | -9349.5093 | [13 empty] | 40742.8776 | 60.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56569.9961 | -5.7169
| 40742.8776 | 60.004 | 0 |  |  |  | -11.4446 | -11.4446 |  | 0 | -14.2991 | 0 | 69.4822 | 3.3309 | 82.3257 | 596.1496 | [6 empty] | 0 | 596.1496 | -13630.7935 | [13 empty] | 40742.8776 | 60.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56569.9961 | -11.4446
| 40742.8776 | 60.006 | 0 |  |  |  | -17.1615 | -17.1615 |  | 0 | -20.0159 | 0 | 69.2551 | 3.3309 | 82.1247 | 596.1496 | [6 empty] | 0 | 596.1496 | -25104.7467 | [13 empty] | 40742.8776 | 60.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56565.5781 | -17.1615
| 40742.8776 | 60.006 | 0 |  |  |  | -17.1615 | -17.1615 |  | 0 | -20.0159 | 0 | 69.0291 | 3.3309 | 81.9248 | 596.1496 | [6 empty] | 0 | 596.1496 | -25104.7467 | [13 empty] | 40742.8776 | 60.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56565.5781 | -17.1615
| 40742.8777 | 60.006 | 0 |  |  |  | -17.1615 | -17.1615 |  | 0 | -20.0159 | 0 | 68.8042 | 3.3309 | 81.7258 | 596.1496 | [6 empty] | 0 | 596.1496 | -25104.7467 | [13 empty] | 40742.8777 | 60.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56557.957 | -17.1615
| 40742.8777 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 68.5877 | 3.3309 | 81.5278 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8777 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56557.957 | -14.3031
| 40742.8777 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 68.3723 | 3.3309 | 81.3308 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8777 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56538.8945 | -14.3031
| 40742.8777 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 68.1579 | 3.3309 | 81.1349 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8777 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56538.8945 | -14.3031
| 40742.8778 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 67.9446 | 3.3309 | 80.9399 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8778 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56537.918 | -14.3031
| 40742.8778 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 67.7324 | 3.3309 | 80.7458 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8778 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56537.918 | -14.3031
| 40742.8778 | 60.004 | 0 |  |  |  | -11.4446 | -11.4446 |  | 0 | -14.2991 | 0 | 67.5283 | 3.3309 | 80.5528 | 596.1496 | [6 empty] | 0 | 596.1496 | -13630.7935 | [13 empty] | 40742.8778 | 60.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56544.3555 | -11.4446
| 40742.8778 | 60.004 | 0 |  |  |  | -11.4446 | -11.4446 |  | 0 | -14.2991 | 0 | 67.3253 | 3.3309 | 80.3607 | 596.1496 | [6 empty] | 0 | 596.1496 | -13630.7935 | [13 empty] | 40742.8778 | 60.004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56544.3555 | -11.4446
| 40742.8778 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 67.1162 | 3.3309 | 80.1696 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8778 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.6836 | -14.3031
| 40742.8779 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 66.9081 | 3.3309 | 79.9794 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8779 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.6836 | -14.3031
| 40742.8779 | 60.005 | 0 |  |  |  | -14.3031 | -14.3031 |  | 0 | -17.1575 | 0 | 66.701 | 3.3309 | 79.7901 | 596.1496 | [6 empty] | 0 | 596.1496 | -17668.4057 | [13 empty] | 40742.8779 | 60.005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56554.3086 | -14.3031
| 40742.8779 | 60.002 | 0 |  |  |  | -5.7169 | -5.7169 |  | 0 | -8.5713 | 0 | 66.5161 | 3.3309 | 79.6018 | 596.1496 | [6 empty] | 0 | 596.1496 | -9349.5093 | [13 empty] | 40742.8779 | 60.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56554.3086 | -5.7169
| 40742.8779 | 59.999 | 0 |  |  |  | 2.8584 | 2.8584 |  | 0 | 0.0040044 | 0 | 66.3531 | 3.3309 | 79.4144 | 596.1496 | [6 empty] | 0 | 596.1496 | -6359.1881 | [13 empty] | 40742.8779 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56543.293 | 2.8584
| 40742.878 | 59.996 | 0 |  |  |  | 11.4446 | 11.4446 |  | 0 | 8.5902 | 0 | 66.2118 | 3.3309 | 79.2279 | 596.1496 | [6 empty] | 0 | 596.1496 | -4816.6759 | [13 empty] | 40742.878 | 59.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56543.293 | 11.4446
| 40742.878 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 66.0573 | 3.3309 | 79.0423 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.878 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56531.3398 | 5.7169
| 40742.878 | 59.999 | 0 |  |  |  | 2.8584 | 2.8584 |  | 0 | 0.0040044 | 0 | 65.8966 | 3.3309 | 78.8577 | 596.1496 | [6 empty] | 0 | 596.1496 | -6359.1881 | [13 empty] | 40742.878 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56531.3398 | 2.8584
| 40742.878 | 60.001 | 0 |  |  |  | -2.8584 | -2.8584 |  | 0 | -5.7129 | 0 | 65.7228 | 3.3309 | 78.6739 | 596.1496 | [6 empty] | 0 | 596.1496 | -8082.5988 | [13 empty] | 40742.878 | 60.001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.4492 | -2.8584
| 40742.8781 | 59.999 | 0 |  |  |  | 2.8584 | 2.8584 |  | 0 | 0.0040044 | 0 | 65.5637 | 3.3309 | 78.491 | 596.1496 | [6 empty] | 0 | 596.1496 | -6359.1881 | [13 empty] | 40742.8781 | 59.999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.4492 | 2.8584
| 40742.8781 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 65.4122 | 3.3309 | 78.3091 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.8781 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56546.6133 | 5.7169
| 40742.8781 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 65.2615 | 3.3309 | 78.1279 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.8781 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56546.6133 | 5.7169
| 40742.8781 | 59.998 | 0 |  |  |  | 5.7169 | 5.7169 |  | 0 | 2.8624 | 0 | 65.1115 | 3.3309 | 77.9477 | 596.1496 | [6 empty] | 0 | 596.1496 | -5746.5361 | [13 empty] | 40742.8781 | 59.998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56538.9219 | 5.7169
| 40742.8781 | 59.997 | 0 |  |  |  | 8.5753 | 8.5753 |  | 0 | 5.7209 | 0 | 64.9691 | 3.3309 | 77.7683 | 596.1496 | [6 empty] | 0 | 596.1496 | -5241.5579 | [13 empty] | 40742.8781 | 59.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56538.9219 | 8.5753
| 40742.8782 | 59.996 | 0 |  |  |  | 11.4446 | 11.4446 |  | 0 | 8.5902 | 0 | 64.8342 | 3.3309 | 77.5898 | 596.1496 | [6 empty] | 0 | 596.1496 | -4816.6759 | [13 empty] | 40742.8782 | 59.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56548.0664 | 11.4446
| 40742.8782 | 59.995 | 0 |  |  |  | 14.3031 | 14.3031 |  | 0 | 11.4486 | 0 | 64.7068 | 3.3309 | 77.4122 | 596.1496 | [6 empty] | 0 | 596.1496 | -4456.7816 | [13 empty] | 40742.8782 | 59.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56548.0664 | 14.3031
| 40742.8782 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 64.5936 | 3.3309 | 77.2354 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8782 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.0195 | 20.0199
| 40742.8782 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 64.4809 | 3.3309 | 77.0594 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8782 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56542.0195 | 20.0199
| 40742.8783 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 64.3688 | 3.3309 | 76.8843 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8783 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56531.9102 | 20.0199
| 40742.8783 | 59.995 | 0 |  |  |  | 14.3031 | 14.3031 |  | 0 | 11.4486 | 0 | 64.2437 | 3.3309 | 76.71 | 596.1496 | [6 empty] | 0 | 596.1496 | -4456.7816 | [13 empty] | 40742.8783 | 59.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56531.9102 | 14.3031
| 40742.8783 | 59.995 | 0 |  |  |  | 14.3031 | 14.3031 |  | 0 | 11.4486 | 0 | 64.1192 | 3.3309 | 76.5365 | 596.1496 | [6 empty] | 0 | 596.1496 | -4456.7816 | [13 empty] | 40742.8783 | 59.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56528.668 | 14.3031
| 40742.8783 | 59.996 | 0 |  |  |  | 11.4446 | 11.4446 |  | 0 | 8.5902 | 0 | 63.9885 | 3.3309 | 76.3639 | 596.1496 | [6 empty] | 0 | 596.1496 | -4816.6759 | [13 empty] | 40742.8783 | 59.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56528.668 | 11.4446
| 40742.8784 | 59.995 | 0 |  |  |  | 14.3031 | 14.3031 |  | 0 | 11.4486 | 0 | 63.8652 | 3.3309 | 76.192 | 596.1496 | [6 empty] | 0 | 596.1496 | -4456.7816 | [13 empty] | 40742.8784 | 59.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56528.4648 | 14.3031
| 40742.8784 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 63.7558 | 3.3309 | 76.021 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8784 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56528.4648 | 20.0199
| 40742.8784 | 59.99 | 0 |  |  |  | 28.5952 | 28.5952 |  | 0 | 25.7408 | 0 | 63.667 | 3.3309 | 75.8508 | 596.1496 | [6 empty] | 0 | 596.1496 | -3244.6185 | [13 empty] | 40742.8784 | 59.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56519.6055 | 28.5952
| 40742.8784 | 59.988 | 0 |  |  |  | 34.323 | 34.323 |  | 0 | 31.4685 | 0 | 63.592 | 3.3309 | 75.6813 | 596.1496 | [6 empty] | 0 | 596.1496 | -2925.7146 | [13 empty] | 40742.8784 | 59.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56519.6055 | 34.323
| 40742.8784 | 59.987 | 0 |  |  |  | 37.1814 | 37.1814 |  | 0 | 34.327 | 0 | 63.5239 | 3.3309 | 75.5127 | 596.1496 | [6 empty] | 0 | 596.1496 | -2788.9185 | [13 empty] | 40742.8784 | 59.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56512.2031 | 37.1814
| 40742.8785 | 59.987 | 0 |  |  |  | 37.1814 | 37.1814 |  | 0 | 34.327 | 0 | 63.4562 | 3.3309 | 75.3448 | 596.1496 | [6 empty] | 0 | 596.1496 | -2788.9185 | [13 empty] | 40742.8785 | 59.987 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56512.2031 | 37.1814
| 40742.8785 | 59.989 | 0 |  |  |  | 31.4645 | 31.4645 |  | 0 | 28.6101 | 0 | 63.3755 | 3.3309 | 75.1777 | 596.1496 | [6 empty] | 0 | 596.1496 | -3076.6227 | [13 empty] | 40742.8785 | 59.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56514.5234 | 31.4645
| 40742.8785 | 59.991 | 0 |  |  |  | 25.7368 | 25.7368 |  | 0 | 22.8823 | 0 | 63.282 | 3.3309 | 75.0114 | 596.1496 | [6 empty] | 0 | 596.1496 | -3431.2668 | [13 empty] | 40742.8785 | 59.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56514.5234 | 25.7368
| 40742.8785 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 63.1757 | 3.3309 | 74.8459 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8785 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56508.4688 | 20.0199
| 40742.8786 | 59.996 | 0 |  |  |  | 11.4446 | 11.4446 |  | 0 | 8.5902 | 0 | 63.0502 | 3.3309 | 74.6811 | 596.1496 | [6 empty] | 0 | 596.1496 | -4816.6759 | [13 empty] | 40742.8786 | 59.996 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56508.4688 | 11.4446
| 40742.8786 | 59.997 | 0 |  |  |  | 8.5753 | 8.5753 |  | 0 | 5.7209 | 0 | 62.9187 | 3.3309 | 74.5171 | 596.1496 | [6 empty] | 0 | 596.1496 | -5241.5579 | [13 empty] | 40742.8786 | 59.997 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56512.1523 | 8.5753
| 40742.8786 | 59.995 | 0 |  |  |  | 14.3031 | 14.3031 |  | 0 | 11.4486 | 0 | 62.801 | 3.3309 | 74.3538 | 596.1496 | [6 empty] | 0 | 596.1496 | -4456.7816 | [13 empty] | 40742.8786 | 59.995 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56512.1523 | 14.3031
| 40742.8786 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 62.6968 | 3.3309 | 74.1913 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8786 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56508.8594 | 20.0199
| 40742.8787 | 59.993 | 0 |  |  |  | 20.0199 | 20.0199 |  | 0 | 17.1655 | 0 | 62.5931 | 3.3309 | 74.0295 | 596.1496 | [6 empty] | 0 | 596.1496 | -3877.3613 | [13 empty] | 40742.8787 | 59.993 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56508.8594 | 20.0199
| 40742.8787 | 59.992 | 0 |  |  |  | 22.8783 | 22.8783 |  | 0 | 20.0239 | 0 | 62.4963 | 3.3309 | 73.8684 | 596.1496 | [6 empty] | 0 | 596.1496 | -3640.7 | [13 empty] | 40742.8787 | 59.992 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56503.3359 | 22.8783
| 40742.8787 | 59.99 | 0 |  |  |  | 28.5952 | 28.5952 |  | 0 | 25.7408 | 0 | 62.413 | 3.3309 | 73.7081 | 596.1496 | [6 empty] | 0 | 596.1496 | -3244.6185 | [13 empty] | 40742.8787 | 59.99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56503.3359 | 28.5952
| 40742.8787 | 59.989 | 0 |  |  |  | 31.4645 | 31.4645 |  | 0 | 28.6101 | 0 | 62.3365 | 3.3309 | 73.5485 | 596.1496 | [6 empty] | 0 | 596.1496 | -3076.6227 | [13 empty] | 40742.8787 | 59.989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56510.0859 | 31.4645
| 40742.8787 | 59.988 | 0 |  |  |  | 34.323 | 34.323 |  | 0 | 31.4685 | 0 | 62.2668 | 3.3309 | 73.3897 | 596.1496 | [6 empty] | 0 | 596.1496 | -2925.7146 | [13 empty] | 40742.8787 | 59.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56510.0859 | 34.323
| 40742.8788 | 59.986 | 0 |  |  |  | 40.0398 | 40.0398 |  | 0 | 37.1854 | 0 | 62.2103 | 3.3309 | 73.2315 | 596.1496 | [6 empty] | 0 | 596.1496 | -2664.3432 | [13 empty] | 40742.8788 | 59.986 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56514.668 | 40.0398
| 40742.8788 | 59.985 | 0 |  |  |  | 42.8983 | 42.8983 |  | 0 | 40.0438 | 0 | 62.1605 | 3.3309 | 73.0741 | 596.1496 | [6 empty] | 0 | 596.1496 | -2550.421 | [13 empty] | 40742.8788 | 59.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56514.668 | 42.8983
| 40742.8788 | 59.985 | 0 |  |  |  | 42.8983 | 42.8983 |  | 0 | 40.0438 | 0 | 62.1109 | 3.3309 | 72.9174 | 596.1496 | [6 empty] | 0 | 596.1496 | -2550.421 | [13 empty] | 40742.8788 | 59.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56501.8984 | 42.8983
| 40742.8788 | 59.985 | 0 |  |  |  | 42.8983 | 42.8983 |  | 0 | 40.0438 | 0 | 62.0616 | 3.3309 | 72.7613 | 596.1496 | [6 empty] | 0 | 596.1496 | -2550.421 | [13 empty] | 40742.8788 | 59.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56501.8984 | 42.8983
| 40742.8789 | 59.985 | 0 |  |  |  | 42.8983 | 42.8983 |  | 0 | 40.0438 | 0 | 62.0124 | 3.3309 | 72.606 | 596.1496 | [6 empty] | 0 | 596.1496 | -2550.421 | [13 empty] | 40742.8789 | 59.985 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56510.4648 | 42.8983
| 40742.8789 | 59.983 | 0 |  |  |  | 48.6151 | 48.6151 |  | 0 | 45.7607 | 0 | 61.9762 | 3.3309 | 72.4514 | 596.1496 | [6 empty] | 0 | 596.1496 | -2349.5008 | [13 empty] | 40742.8789 | 59.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56510.4648 | 48.6151
| 40742.8789 | 59.983 | 0 |  |  |  | 48.6151 | 48.6151 |  | 0 | 45.7607 | 0 | 61.9402 | 3.3309 | 72.2974 | 596.1496 | [6 empty] | 0 | 596.1496 | -2349.5008 | [13 empty] | 40742.8789 | 59.983 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56504.7422 | 48.6151
| 40742.8789 | 59.981 | 0 |  |  |  | 54.3429 | 54.3429 |  | 0 | 51.4885 | 0 | 61.917 | 3.3309 | 72.1442 | 596.1496 | [6 empty] | 0 | 596.1496 | -2177.6221 | [13 empty] | 40742.8789 | 59.981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 56504.7422 | 54.3429

## Graph 20 to 52s
60.0084

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW |  | MW | MW |  |  |  | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2011-07-18 20:51 | 40742.8685 | 60.007 | 60.0084 | 40742.8685 | 59.866 | 59.8751 | -448.2121 | 59.8799 | -463.9878 | 59.8807 | -465.0911 | 59.8804 | -466.0866 | 59.8807 | -467.0124 | 60.0084 | 596.1496 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 57050.2559 | -54.6898 | 59.8751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5645 | 1.5645 | No Evaluation | -653 | 56857.5725 | 815.3177 | 59.8799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6219 | 1.6219 | No Evaluation | -653 | 56872.1323 | 784.5325 | 59.8802 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.626 | 1.626 | No Evaluation | -653 | 56878.6644 | 782.4109 | 59.8804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6294 | 1.6294 | No Evaluation | -653 | 56882.8589 | 780.6965 | 59.8807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.6327 | 1.6327 | No Evaluation | -653 | 56884.0016 | 778.9891