## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Total Lost Generation: enter the MW data of the units that tripped as a single generator where the value typically goes to zero at t(0).
Column D: not applicable
Column E: Non Conforming Load
Column F: Pumped Hydro
Column G: not applicable
Column H: not applicable
Column I: not applicable
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D, E, F, G and H are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must be at 3 second sample rate for the full 25 minute minimum collection period that starts a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event.
The spreadsheet will work with larger sample size data.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data. The data must be numbers not text.
5 | Once data is in place in the "Data" worksheet, determine when the beginning of the event occurred. This is accomplished by knowing the UTC event time from the master event list.
Convert the UTC event time to your PI data time and then scroll through the Data worksheet column B data of frequency and observe when frequency moves from the normal, pre-event frequency.
This will usually be a single change in frequency of 0.008 to 0.010 Hz more or less. Note the row number in the worksheet that this change occurs. In this sample data spreadsheet this occurs in row 313 of the data.
6 | Edit cell "C8" of the "Entry Data" worksheet, change the formula in the cell "C8" to reference the row number identified in step 5 above. In the sample data of this workbook this formula is: "=Data!A313"
7 | Determine the end of the event to be evaluated. Use the same rules that are used for DCS only look at frequency instead of ACE. Scroll down the frequency data in column B of the "Data" worksheet until frequency reaches 60 Hz or the
pre-disturbance value. Note the row number in the worksheet that this occurs. In this sample data spreadsheet this occurs in row 424.
8 | Edit cell "C11" of the "Entry Data" worksheet, change the formula in the cell "C11" to reference the row number identified in step 7 above. In the sample data of this workbook this formula is: "=Data!A424"
9 | Skip for single BA Interconnections.
10 | Use the "copy" button provided to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized in the correct order on worksheet "Form 1 Summary Data" of this workbook.
Use PasteSpecial/Values when pasting the data into FRS Form 1 on the appropriate event row.
Steps | To be completed once at the initial setup of the evaluation spreadsheet for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Entry Data" worksheet. For example: "NYISO".
B | Enter your Balancing Authorities Frequency Response Obligation in cell "B2" of the "Entry Data" worksheet. For example: -80 MW/0.1 Hz (This value could change annually)
Note: For ease of use, only the necessary worksheets are displayed. If you are interested in viewing graphs and other hidden worksheets, select the "tab" at the bottom, right click, select unhide and select the worksheet you wish to unhide.

## Data
|  |  | JOU | Non- |  |  | Transferred | Contingent
|  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA
|  | Lost | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load
mm/dd/yy hh:mm:ss | Frequency | Generation | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Setting
Time (T) | Hz | MW |  | MW | MW |  |  |  | MW/0.1 Hz | MW | LaaR Tripped
2009-10-12 02:12 | 59.981 | 633 |  | 351.3615 | 0 |  |  |  | -420 | 7500 | 0
2009-10-12 02:12 | 59.98 | 633 |  | 351.3615 | 0 |  |  |  | -420 | 7500.33
2009-10-12 02:12 | 59.982 | 633 |  | 351.3615 | 0 |  |  |  | -420 | 7500.66
2009-10-12 02:12 | 59.981 | 633 |  | 357.9475 | 0 |  |  |  | -420 | 7500.99
2009-10-12 02:12 | 59.981 | 633 |  | 357.9475 | 0 |  |  |  | -420 | 7501.32
2009-10-12 02:12 | 59.982 | 633 |  | 357.9475 | 0 |  |  |  | -420 | 7501.65
2009-10-12 02:12 | 59.979 | 633 |  | 357.9475 | 0 |  |  |  | -420 | 7501.98
2009-10-12 02:12 | 59.98 | 633 |  | 357.9475 | 0 |  |  |  | -420 | 7502.31
2009-10-12 02:12 | 59.983 | 633 |  | 360.2347 | 0 |  |  |  | -420 | 7502.64
2009-10-12 02:12 | 59.986 | 633 |  | 360.2347 | 0 |  |  |  | -420 | 7502.97
2009-10-12 02:12 | 59.98 | 633 |  | 360.2347 | 0 |  |  |  | -420 | 7503.3
2009-10-12 02:13 | 59.976 | 633 |  | 360.2347 | 0 |  |  |  | -420 | 7503.63
2009-10-12 02:13 | 59.979 | 633 |  | 360.2347 | 0 |  |  |  | -420 | 7503.96
2009-10-12 02:13 | 59.981 | 633 |  | 346.5259 | 0 |  |  |  | -420 | 7504.29
2009-10-12 02:13 | 59.987 | 633 |  | 346.5259 | 0 |  |  |  | -420 | 7504.62
2009-10-12 02:13 | 59.99 | 633 |  | 346.5259 | 0 |  |  |  | -420 | 7504.95
2009-10-12 02:13 | 59.994 | 633 |  | 346.5259 | 0 |  |  |  | -420 | 7505.28
2009-10-12 02:13 | 59.995 | 633 |  | 346.5259 | 0 |  |  |  | -420 | 7505.61
2009-10-12 02:13 | 59.995 | 633 |  | 296.4434 | 0 |  |  |  | -420 | 7505.94
2009-10-12 02:13 | 59.995 | 633 |  | 296.4434 | 0 |  |  |  | -420 | 7506.27
2009-10-12 02:13 | 59.994 | 633 |  | 296.4434 | 0 |  |  |  | -420 | 7506.6
2009-10-12 02:13 | 59.994 | 633 |  | 296.4434 | 0 |  |  |  | -420 | 7506.93
2009-10-12 02:13 | 59.997 | 633 |  | 296.4434 | 0 |  |  |  | -420 | 7507.26
2009-10-12 02:13 | 60.001 | 633 |  | 341.0612 | 0 |  |  |  | -420 | 7507.59
2009-10-12 02:13 | 60.001 | 633 |  | 341.0612 | 0 |  |  |  | -420 | 7507.92
2009-10-12 02:13 | 60.003 | 633 |  | 341.0612 | 0 |  |  |  | -420 | 7508.25
2009-10-12 02:13 | 60.005 | 633 |  | 341.0612 | 0 |  |  |  | -420 | 7508.58
2009-10-12 02:13 | 60.003 | 633 |  | 341.0612 | 0 |  |  |  | -420 | 7508.91
2009-10-12 02:13 | 60.001 | 633 |  | 322.8263 | 0 |  |  |  | -420 | 7509.24
2009-10-12 02:13 | 60.003 | 633 |  | 322.8263 | 0 |  |  |  | -420 | 7509.57
2009-10-12 02:13 | 60.005 | 633 |  | 322.8263 | 0 |  |  |  | -420 | 7509.9
2009-10-12 02:14 | 60.001 | 633 |  | 322.8263 | 0 |  |  |  | -420 | 7510.23
2009-10-12 02:14 | 60.001 | 633 |  | 322.8263 | 0 |  |  |  | -420 | 7510.56
2009-10-12 02:14 | 60.004 | 633 |  | 321.5444 | 0 |  |  |  | -420 | 7510.89
2009-10-12 02:14 | 60.004 | 633 |  | 321.5444 | 0 |  |  |  | -420 | 7511.22
2009-10-12 02:14 | 60.004 | 633 |  | 321.5444 | 0 |  |  |  | -420 | 7511.55
2009-10-12 02:14 | 60.003 | 633 |  | 321.5444 | 0 |  |  |  | -420 | 7511.88
2009-10-12 02:14 | 60.002 | 633 |  | 321.5444 | 0 |  |  |  | -420 | 7512.21
2009-10-12 02:14 | 60.001 | 633 |  | 362.1363 | 0 |  |  |  | -420 | 7512.54
2009-10-12 02:14 | 59.999 | 633 |  | 362.1363 | 0 |  |  |  | -420 | 7512.87
2009-10-12 02:14 | 59.997 | 633 |  | 362.1363 | 0 |  |  |  | -420 | 7513.2
2009-10-12 02:14 | 59.998 | 633 |  | 362.1363 | 0 |  |  |  | -420 | 7513.53
2009-10-12 02:14 | 59.995 | 633 |  | 362.1363 | 0 |  |  |  | -420 | 7513.86
2009-10-12 02:14 | 59.993 | 633 |  | 336.3118 | 0 |  |  |  | -420 | 7514.19
2009-10-12 02:14 | 59.996 | 633 |  | 336.3118 | 0 |  |  |  | -420 | 7514.52
2009-10-12 02:14 | 59.999 | 633 |  | 336.3118 | 0 |  |  |  | -420 | 7514.85
2009-10-12 02:14 | 60.005 | 633 |  | 336.3118 | 0 |  |  |  | -420 | 7515.18
2009-10-12 02:14 | 60.007 | 633 |  | 336.3118 | 0 |  |  |  | -420 | 7515.51
2009-10-12 02:14 | 60.005 | 633 |  | 316.4431 | 0 |  |  |  | -420 | 7515.84
2009-10-12 02:14 | 60.002 | 633 |  | 316.4431 | 0 |  |  |  | -420 | 7516.17
2009-10-12 02:14 | 59.997 | 633 |  | 316.4431 | 0 |  |  |  | -420 | 7516.5
2009-10-12 02:15 | 59.999 | 633 |  | 316.4431 | 0 |  |  |  | -420 | 7516.83
2009-10-12 02:15 | 60.007 | 633 |  | 316.4431 | 0 |  |  |  | -420 | 7517.16
2009-10-12 02:15 | 60.01 | 633 |  | 325.4643 | 0 |  |  |  | -420 | 7517.49
2009-10-12 02:15 | 60.009 | 633 |  | 325.4643 | 0 |  |  |  | -420 | 7517.82
2009-10-12 02:15 | 60.003 | 633 |  | 325.4643 | 0 |  |  |  | -420 | 7518.15
2009-10-12 02:15 | 59.995 | 633 |  | 325.4643 | 0 |  |  |  | -420 | 7518.48
2009-10-12 02:15 | 59.994 | 633 |  | 325.4643 | 0 |  |  |  | -420 | 7518.81
2009-10-12 02:15 | 60 | 633 |  | 336.6142 | 0 |  |  |  | -420 | 7519.14
2009-10-12 02:15 | 60.001 | 633 |  | 336.6142 | 0 |  |  |  | -420 | 7519.47
2009-10-12 02:15 | 59.998 | 633 |  | 336.6142 | 0 |  |  |  | -420 | 7519.8
2009-10-12 02:15 | 59.995 | 633 |  | 336.6142 | 0 |  |  |  | -420 | 7520.13
2009-10-12 02:15 | 59.986 | 633 |  | 336.6142 | 0 |  |  |  | -420 | 7520.46
2009-10-12 02:15 | 59.986 | 633 |  | 316.7262 | 0 |  |  |  | -420 | 7520.79
2009-10-12 02:15 | 59.988 | 633 |  | 316.7262 | 0 |  |  |  | -420 | 7521.12
2009-10-12 02:15 | 59.989 | 633 |  | 316.7262 | 0 |  |  |  | -420 | 7521.45
2009-10-12 02:15 | 59.987 | 633 |  | 316.7262 | 0 |  |  |  | -420 | 7521.78
2009-10-12 02:15 | 59.985 | 633 |  | 316.7262 | 0 |  |  |  | -420 | 7522.11
2009-10-12 02:15 | 59.983 | 633 |  | 320.1955 | 0 |  |  |  | -420 | 7522.44
2009-10-12 02:15 | 59.982 | 633 |  | 320.1955 | 0 |  |  |  | -420 | 7522.77
2009-10-12 02:16 | 59.984 | 633 |  | 320.1955 | 0 |  |  |  | -420 | 7523.1
2009-10-12 02:16 | 59.985 | 633 |  | 320.1955 | 0 |  |  |  | -420 | 7523.43
2009-10-12 02:16 | 59.987 | 633 |  | 320.1955 | 0 |  |  |  | -420 | 7523.76
2009-10-12 02:16 | 59.99 | 633 |  | 341.8661 | 0 |  |  |  | -420 | 7524.09
2009-10-12 02:16 | 59.987 | 633 |  | 341.8661 | 0 |  |  |  | -420 | 7524.42
2009-10-12 02:16 | 59.983 | 633 |  | 341.8661 | 0 |  |  |  | -420 | 7524.75
2009-10-12 02:16 | 59.979 | 633 |  | 341.8661 | 0 |  |  |  | -420 | 7525.08
2009-10-12 02:16 | 59.983 | 633 |  | 341.8661 | 0 |  |  |  | -420 | 7525.41
2009-10-12 02:16 | 59.986 | 633 |  | 348.5978 | 0 |  |  |  | -420 | 7525.74
2009-10-12 02:16 | 59.988 | 633 |  | 348.5978 | 0 |  |  |  | -420 | 7526.07
2009-10-12 02:16 | 59.983 | 633 |  | 348.5978 | 0 |  |  |  | -420 | 7526.4
2009-10-12 02:16 | 59.978 | 633 |  | 348.5978 | 0 |  |  |  | -420 | 7526.73
2009-10-12 02:16 | 59.979 | 633 |  | 348.5978 | 0 |  |  |  | -420 | 7527.06
2009-10-12 02:16 | 59.989 | 633 |  | 329.085 | 0 |  |  |  | -420 | 7527.39
2009-10-12 02:16 | 59.988 | 633 |  | 329.085 | 0 |  |  |  | -420 | 7527.72
2009-10-12 02:16 | 59.983 | 633 |  | 329.085 | 0 |  |  |  | -420 | 7528.05
2009-10-12 02:16 | 59.991 | 633 |  | 329.085 | 0 |  |  |  | -420 | 7528.38
2009-10-12 02:16 | 59.989 | 633 |  | 329.085 | 0 |  |  |  | -420 | 7528.71
2009-10-12 02:16 | 59.993 | 633 |  | 342.4182 | 0 |  |  |  | -420 | 7529.04
2009-10-12 02:16 | 59.995 | 633 |  | 342.4182 | 0 |  |  |  | -420 | 7529.37
2009-10-12 02:17 | 59.998 | 633 |  | 342.4182 | 0 |  |  |  | -420 | 7529.7
2009-10-12 02:17 | 59.998 | 633 |  | 342.4182 | 0 |  |  |  | -420 | 7530.03
2009-10-12 02:17 | 59.999 | 633 |  | 342.4182 | 0 |  |  |  | -420 | 7530.36
2009-10-12 02:17 | 59.995 | 633 |  | 338.7946 | 0 |  |  |  | -420 | 7530.69
2009-10-12 02:17 | 59.992 | 633 |  | 338.7946 | 0 |  |  |  | -420 | 7531.02
2009-10-12 02:17 | 59.995 | 633 |  | 338.7946 | 0 |  |  |  | -420 | 7531.35
2009-10-12 02:17 | 60.001 | 633 |  | 338.7946 | 0 |  |  |  | -420 | 7531.68
2009-10-12 02:17 | 60.003 | 633 |  | 338.7946 | 0 |  |  |  | -420 | 7532.01
2009-10-12 02:17 | 60.009 | 633 |  | 335.931 | 0 |  |  |  | -420 | 7532.34
2009-10-12 02:17 | 60.009 | 633 |  | 335.931 | 0 |  |  |  | -420 | 7532.67
2009-10-12 02:17 | 60.012 | 633 |  | 335.931 | 0 |  |  |  | -420 | 7533
2009-10-12 02:17 | 60.011 | 633 |  | 335.931 | 0 |  |  |  | -420 | 7533.33
2009-10-12 02:17 | 60.008 | 633 |  | 335.931 | 0 |  |  |  | -420 | 7533.66
2009-10-12 02:17 | 60.007 | 633 |  | 339.7124 | 0 |  |  |  | -420 | 7533.99
2009-10-12 02:17 | 60.012 | 633 |  | 339.7124 | 0 |  |  |  | -420 | 7534.32
2009-10-12 02:17 | 60.013 | 633 |  | 339.7124 | 0 |  |  |  | -420 | 7534.65
2009-10-12 02:17 | 60.01 | 633 |  | 339.7124 | 0 |  |  |  | -420 | 7534.98
2009-10-12 02:17 | 60.007 | 633 |  | 339.7124 | 0 |  |  |  | -420 | 7535.31
2009-10-12 02:17 | 60.009 | 633 |  | 332.0247 | 0 |  |  |  | -420 | 7535.64
2009-10-12 02:17 | 60.006 | 633 |  | 332.0247 | 0 |  |  |  | -420 | 7535.97
2009-10-12 02:18 | 60.009 | 633 |  | 332.0247 | 0 |  |  |  | -420 | 7536.3
2009-10-12 02:18 | 60.009 | 633 |  | 332.0247 | 0 |  |  |  | -420 | 7536.63
2009-10-12 02:18 | 60.009 | 633 |  | 332.0247 | 0 |  |  |  | -420 | 7536.96
2009-10-12 02:18 | 60.009 | 633 |  | 330.759 | 0 |  |  |  | -420 | 7537.29
2009-10-12 02:18 | 60.004 | 633 |  | 330.759 | 0 |  |  |  | -420 | 7537.62
2009-10-12 02:18 | 60.001 | 633 |  | 330.759 | 0 |  |  |  | -420 | 7537.95
2009-10-12 02:18 | 59.993 | 633 |  | 330.759 | 0 |  |  |  | -420 | 7538.28
2009-10-12 02:18 | 59.991 | 633 |  | 330.759 | 0 |  |  |  | -420 | 7538.61
2009-10-12 02:18 | 59.992 | 633 |  | 323.42 | 0 |  |  |  | -420 | 7538.94
2009-10-12 02:18 | 59.994 | 633 |  | 323.42 | 0 |  |  |  | -420 | 7539.27
2009-10-12 02:18 | 59.994 | 633 |  | 323.42 | 0 |  |  |  | -420 | 7539.6
2009-10-12 02:18 | 59.995 | 633 |  | 323.42 | 0 |  |  |  | -420 | 7539.93
2009-10-12 02:18 | 59.99 | 633 |  | 323.42 | 0 |  |  |  | -420 | 7540.26
2009-10-12 02:18 | 59.99 | 633 |  | 342.3509 | 0 |  |  |  | -420 | 7540.59
2009-10-12 02:18 | 59.983 | 633 |  | 342.3509 | 0 |  |  |  | -420 | 7540.92
2009-10-12 02:18 | 59.977 | 633 |  | 342.3509 | 0 |  |  |  | -420 | 7541.25
2009-10-12 02:18 | 59.989 | 633 |  | 342.3509 | 0 |  |  |  | -420 | 7541.58
2009-10-12 02:18 | 59.995 | 633 |  | 342.3509 | 0 |  |  |  | -420 | 7541.91
2009-10-12 02:18 | 59.994 | 633 |  | 345.0818 | 0 |  |  |  | -420 | 7542.24
2009-10-12 02:18 | 59.989 | 633 |  | 345.0818 | 0 |  |  |  | -420 | 7542.57
2009-10-12 02:18 | 59.986 | 633 |  | 345.0818 | 0 |  |  |  | -420 | 7542.9
2009-10-12 02:19 | 59.984 | 633 |  | 345.0818 | 0 |  |  |  | -420 | 7543.23
2009-10-12 02:19 | 59.985 | 633 |  | 345.0818 | 0 |  |  |  | -420 | 7543.56
2009-10-12 02:19 | 59.986 | 633 |  | 346.5374 | 0 |  |  |  | -420 | 7543.89
2009-10-12 02:19 | 59.986 | 633 |  | 346.5374 | 0 |  |  |  | -420 | 7544.22
2009-10-12 02:19 | 59.98 | 633 |  | 346.5374 | 0 |  |  |  | -420 | 7544.55
2009-10-12 02:19 | 59.981 | 633 |  | 346.5374 | 0 |  |  |  | -420 | 7544.88
2009-10-12 02:19 | 59.989 | 633 |  | 346.5374 | 0 |  |  |  | -420 | 7545.21
2009-10-12 02:19 | 60.007 | 633 |  | 342.9058 | 0 |  |  |  | -420 | 7545.54
2009-10-12 02:19 | 60.007 | 633 |  | 342.9058 | 0 |  |  |  | -420 | 7545.87
2009-10-12 02:19 | 59.986 | 633 |  | 342.9058 | 0 |  |  |  | -420 | 7546.2
2009-10-12 02:19 | 59.981 | 633 |  | 342.9058 | 0 |  |  |  | -420 | 7546.53
2009-10-12 02:19 | 59.974 | 633 |  | 342.9058 | 0 |  |  |  | -420 | 7546.86
2009-10-12 02:19 | 59.976 | 633 |  | 340.0944 | 0 |  |  |  | -420 | 7547.19
2009-10-12 02:19 | 59.974 | 633 |  | 340.0944 | 0 |  |  |  | -420 | 7547.52
2009-10-12 02:19 | 59.977 | 633 |  | 340.0944 | 0 |  |  |  | -420 | 7547.85
2009-10-12 02:19 | 59.979 | 633 |  | 340.0944 | 0 |  |  |  | -420 | 7548.18
2009-10-12 02:19 | 59.982 | 633 |  | 340.0944 | 0 |  |  |  | -420 | 7548.51
2009-10-12 02:19 | 59.987 | 633 |  | 342.7712 | 0 |  |  |  | -420 | 7548.84
2009-10-12 02:19 | 59.988 | 633 |  | 342.7712 | 0 |  |  |  | -420 | 7549.17
2009-10-12 02:20 | 59.987 | 633 |  | 342.7712 | 0 |  |  |  | -420 | 7549.5
2009-10-12 02:20 | 59.987 | 633 |  | 342.7712 | 0 |  |  |  | -420 | 7549.83
2009-10-12 02:20 | 59.985 | 633 |  | 342.7712 | 0 |  |  |  | -420 | 7550.16
2009-10-12 02:20 | 59.984 | 633 |  | 342.9099 | 0 |  |  |  | -420 | 7550.49
2009-10-12 02:20 | 59.983 | 633 |  | 342.9099 | 0 |  |  |  | -420 | 7550.82
2009-10-12 02:20 | 59.989 | 633 |  | 342.9099 | 0 |  |  |  | -420 | 7551.15
2009-10-12 02:20 | 59.988 | 633 |  | 342.9099 | 0 |  |  |  | -420 | 7551.48
2009-10-12 02:20 | 59.984 | 633 |  | 342.9099 | 0 |  |  |  | -420 | 7551.81
2009-10-12 02:20 | 59.983 | 633 |  | 343.286 | 0 |  |  |  | -420 | 7552.14
2009-10-12 02:20 | 59.981 | 633 |  | 343.286 | 0 |  |  |  | -420 | 7552.47
2009-10-12 02:20 | 59.983 | 633 |  | 343.286 | 0 |  |  |  | -420 | 7552.8
2009-10-12 02:20 | 59.986 | 633 |  | 343.286 | 0 |  |  |  | -420 | 7553.13
2009-10-12 02:20 | 59.987 | 633 |  | 343.286 | 0 |  |  |  | -420 | 7553.46
2009-10-12 02:20 | 59.985 | 633 |  | 331.853 | 0 |  |  |  | -420 | 7553.79
2009-10-12 02:20 | 59.98 | 633 |  | 331.853 | 0 |  |  |  | -420 | 7554.12
2009-10-12 02:20 | 59.983 | 633 |  | 331.853 | 0 |  |  |  | -420 | 7554.45
2009-10-12 02:20 | 59.979 | 633 |  | 331.853 | 0 |  |  |  | -420 | 7554.78
2009-10-12 02:20 | 59.979 | 633 |  | 331.853 | 0 |  |  |  | -420 | 7555.11
2009-10-12 02:20 | 59.981 | 633 |  | 329.9882 | 0 |  |  |  | -420 | 7555.44
2009-10-12 02:20 | 59.98 | 633 |  | 329.9882 | 0 |  |  |  | -420 | 7555.77
2009-10-12 02:20 | 59.981 | 633 |  | 329.9882 | 0 |  |  |  | -420 | 7556.1
2009-10-12 02:21 | 59.98 | 633 |  | 329.9882 | 0 |  |  |  | -420 | 7556.43
2009-10-12 02:21 | 59.977 | 633 |  | 329.9882 | 0 |  |  |  | -420 | 7556.76
2009-10-12 02:21 | 59.979 | 633 |  | 255.4442 | 0 |  |  |  | -420 | 7557.09
2009-10-12 02:21 | 59.979 | 633 |  | 255.4442 | 0 |  |  |  | -420 | 7557.42
2009-10-12 02:21 | 59.976 | 633 |  | 255.4442 | 0 |  |  |  | -420 | 7557.75
2009-10-12 02:21 | 59.972 | 633 |  | 255.4442 | 0 |  |  |  | -420 | 7558.08
2009-10-12 02:21 | 59.971 | 633 |  | 255.4442 | 0 |  |  |  | -420 | 7558.41
2009-10-12 02:21 | 59.973 | 633 |  | 254.8383 | 0 |  |  |  | -420 | 7558.74
2009-10-12 02:21 | 59.973 | 633 |  | 254.8383 | 0 |  |  |  | -420 | 7559.07
2009-10-12 02:21 | 59.971 | 633 |  | 254.8383 | 0 |  |  |  | -420 | 7559.4
2009-10-12 02:21 | 59.975 | 633 |  | 254.8383 | 0 |  |  |  | -420 | 7559.73
2009-10-12 02:21 | 59.977 | 633 |  | 254.8383 | 0 |  |  |  | -420 | 7560.06
2009-10-12 02:21 | 59.975 | 633 |  | 257.147 | 0 |  |  |  | -420 | 7560.39
2009-10-12 02:21 | 59.98 | 633 |  | 257.147 | 0 |  |  |  | -420 | 7560.72
2009-10-12 02:21 | 59.979 | 633 |  | 257.147 | 0 |  |  |  | -420 | 7561.05
2009-10-12 02:21 | 59.982 | 633 |  | 257.147 | 0 |  |  |  | -420 | 7561.38
2009-10-12 02:21 | 59.982 | 633 |  | 257.147 | 0 |  |  |  | -420 | 7561.71
2009-10-12 02:21 | 59.982 | 633 |  | 262.2894 | 0 |  |  |  | -420 | 7562.04
2009-10-12 02:21 | 59.981 | 633 |  | 262.2894 | 0 |  |  |  | -420 | 7562.37
2009-10-12 02:22 | 59.984 | 633 |  | 262.2894 | 0 |  |  |  | -420 | 7562.7
2009-10-12 02:22 | 59.985 | 633 |  | 262.2894 | 0 |  |  |  | -420 | 7563.03
2009-10-12 02:22 | 59.989 | 633 |  | 262.2894 | 0 |  |  |  | -420 | 7563.36
2009-10-12 02:22 | 59.993 | 633 |  | 256.6479 | 0 |  |  |  | -420 | 7563.69
2009-10-12 02:22 | 59.998 | 633 |  | 256.6479 | 0 |  |  |  | -420 | 7564.02
2009-10-12 02:22 | 59.998 | 633 |  | 256.6479 | 0 |  |  |  | -420 | 7564.35
2009-10-12 02:22 | 60.007 | 633 |  | 256.6479 | 0 |  |  |  | -420 | 7564.68
2009-10-12 02:22 | 60.01 | 633 |  | 256.6479 | 0 |  |  |  | -420 | 7565.01
2009-10-12 02:22 | 60.014 | 633 |  | 256.3073 | 0 |  |  |  | -420 | 7565.34
2009-10-12 02:22 | 60.013 | 633 |  | 256.3073 | 0 |  |  |  | -420 | 7565.67
2009-10-12 02:22 | 60.008 | 633 |  | 256.3073 | 0 |  |  |  | -420 | 7566
2009-10-12 02:22 | 60.01 | 633 |  | 256.3073 | 0 |  |  |  | -420 | 7566.33
2009-10-12 02:22 | 60.019 | 633 |  | 256.3073 | 0 |  |  |  | -420 | 7566.66
2009-10-12 02:22 | 60.023 | 633 |  | 249.0864 | 0 |  |  |  | -420 | 7566.99
2009-10-12 02:22 | 60.02 | 633 |  | 249.0864 | 0 |  |  |  | -420 | 7567.32
2009-10-12 02:22 | 60.021 | 633 |  | 249.0864 | 0 |  |  |  | -420 | 7567.65
2009-10-12 02:22 | 60.02 | 633 |  | 249.0864 | 0 |  |  |  | -420 | 7567.98
2009-10-12 02:22 | 60.019 | 633 |  | 249.0864 | 0 |  |  |  | -420 | 7568.31
2009-10-12 02:22 | 60.022 | 633 |  | 253.7425 | 0 |  |  |  | -420 | 7568.64
2009-10-12 02:22 | 60.025 | 633 |  | 253.7425 | 0 |  |  |  | -420 | 7568.97
2009-10-12 02:22 | 60.026 | 633 |  | 253.7425 | 0 |  |  |  | -420 | 7569.3
2009-10-12 02:23 | 60.02 | 633 |  | 253.7425 | 0 |  |  |  | -420 | 7569.63
2009-10-12 02:23 | 60.018 | 633 |  | 253.7425 | 0 |  |  |  | -420 | 7569.96
2009-10-12 02:23 | 60.018 | 633 |  | 257.4212 | 0 |  |  |  | -420 | 7570.29
2009-10-12 02:23 | 60.019 | 633 |  | 257.4212 | 0 |  |  |  | -420 | 7570.62
2009-10-12 02:23 | 60.019 | 633 |  | 257.4212 | 0 |  |  |  | -420 | 7570.95
2009-10-12 02:23 | 60.022 | 633 |  | 257.4212 | 0 |  |  |  | -420 | 7571.28
2009-10-12 02:23 | 60.022 | 633 |  | 257.4212 | 0 |  |  |  | -420 | 7571.61
2009-10-12 02:23 | 60.02 | 633 |  | 261.7382 | 0 |  |  |  | -420 | 7571.94
2009-10-12 02:23 | 60.02 | 633 |  | 261.7382 | 0 |  |  |  | -420 | 7572.27
2009-10-12 02:23 | 60.02 | 633 |  | 261.7382 | 0 |  |  |  | -420 | 7572.6
2009-10-12 02:23 | 60.02 | 633 |  | 261.7382 | 0 |  |  |  | -420 | 7572.93
2009-10-12 02:23 | 60.021 | 633 |  | 261.7382 | 0 |  |  |  | -420 | 7573.26
2009-10-12 02:23 | 60.018 | 633 |  | 271.876 | 0 |  |  |  | -420 | 7573.59
2009-10-12 02:23 | 60.014 | 633 |  | 271.876 | 0 |  |  |  | -420 | 7573.92
2009-10-12 02:23 | 60.014 | 633 |  | 271.876 | 0 |  |  |  | -420 | 7574.25
2009-10-12 02:23 | 60.013 | 633 |  | 271.876 | 0 |  |  |  | -420 | 7574.58
2009-10-12 02:23 | 60.01 | 633 |  | 271.876 | 0 |  |  |  | -420 | 7574.91
2009-10-12 02:23 | 60.011 | 633 |  | 262.0735 | 0 |  |  |  | -420 | 7575.24
2009-10-12 02:23 | 60.011 | 633 |  | 262.0735 | 0 |  |  |  | -420 | 7575.57
2009-10-12 02:24 | 60.012 | 633 |  | 262.0735 | 0 |  |  |  | -420 | 7575.9
2009-10-12 02:24 | 60.009 | 633 |  | 262.0735 | 0 |  |  |  | -420 | 7576.23
2009-10-12 02:24 | 60.009 | 633 |  | 262.0735 | 0 |  |  |  | -420 | 7576.56
2009-10-12 02:24 | 60.009 | 633 |  | 260.3644 | 0 |  |  |  | -420 | 7576.89
2009-10-12 02:24 | 60.002 | 633 |  | 260.3644 | 0 |  |  |  | -420 | 7577.22
2009-10-12 02:24 | 59.999 | 633 |  | 260.3644 | 0 |  |  |  | -420 | 7577.55
2009-10-12 02:24 | 59.995 | 633 |  | 260.3644 | 0 |  |  |  | -420 | 7577.88
2009-10-12 02:24 | 59.997 | 633 |  | 260.3644 | 0 |  |  |  | -420 | 7578.21
2009-10-12 02:24 | 59.998 | 633 |  | 352.6444 | 0 |  |  |  | -420 | 7578.54
2009-10-12 02:24 | 59.998 | 633 |  | 352.6444 | 0 |  |  |  | -420 | 7578.87
2009-10-12 02:24 | 59.995 | 633 |  | 352.6444 | 0 |  |  |  | -420 | 7579.2
2009-10-12 02:24 | 59.995 | 633 |  | 352.6444 | 0 |  |  |  | -420 | 7579.53
2009-10-12 02:24 | 59.993 | 633 |  | 352.6444 | 0 |  |  |  | -420 | 7579.86
2009-10-12 02:24 | 59.988 | 633 |  | 354.8957 | 0 |  |  |  | -420 | 7580.19
2009-10-12 02:24 | 59.982 | 633 |  | 354.8957 | 0 |  |  |  | -420 | 7580.52
2009-10-12 02:24 | 59.982 | 633 |  | 354.8957 | 0 |  |  |  | -420 | 7580.85
2009-10-12 02:24 | 59.982 | 633 |  | 354.8957 | 0 |  |  |  | -420 | 7581.18
2009-10-12 02:24 | 59.984 | 633 |  | 354.8957 | 0 |  |  |  | -420 | 7581.51
2009-10-12 02:24 | 59.978 | 633 |  | 340.4694 | 0 |  |  |  | -420 | 7581.84
2009-10-12 02:24 | 59.978 | 633 |  | 340.4694 | 0 |  |  |  | -420 | 7582.17
2009-10-12 02:24 | 59.975 | 633 |  | 340.4694 | 0 |  |  |  | -420 | 7582.5
2009-10-12 02:25 | 59.974 | 633 |  | 340.4694 | 0 |  |  |  | -420 | 7582.83
2009-10-12 02:25 | 59.979 | 633 |  | 340.4694 | 0 |  |  |  | -420 | 7583.16
2009-10-12 02:25 | 59.98 | 633 |  | 337.6429 | 0 |  |  |  | -420 | 7583.49
2009-10-12 02:25 | 59.98 | 633 |  | 337.6429 | 0 |  |  |  | -420 | 7583.82
2009-10-12 02:25 | 59.984 | 633 |  | 337.6429 | 0 |  |  |  | -420 | 7584.15
2009-10-12 02:25 | 59.988 | 633 |  | 337.6429 | 0 |  |  |  | -420 | 7584.48
2009-10-12 02:25 | 59.988 | 633 |  | 337.6429 | 0 |  |  |  | -420 | 7584.81
2009-10-12 02:25 | 59.992 | 633 |  | 284.3608 | 0 |  |  |  | -420 | 7585.14
2009-10-12 02:25 | 59.991 | 633 |  | 284.3608 | 0 |  |  |  | -420 | 7585.47
2009-10-12 02:25 | 59.991 | 633 |  | 284.3608 | 0 |  |  |  | -420 | 7585.8
2009-10-12 02:25 | 59.993 | 633 |  | 284.3608 | 0 |  |  |  | -420 | 7586.13
2009-10-12 02:25 | 59.996 | 633 |  | 284.3608 | 0 |  |  |  | -420 | 7586.46
2009-10-12 02:25 | 60.002 | 633 |  | 260.468 | 0 |  |  |  | -420 | 7586.79
2009-10-12 02:25 | 60.003 | 633 |  | 260.468 | 0 |  |  |  | -420 | 7587.12
2009-10-12 02:25 | 60.004 | 633 |  | 260.468 | 0 |  |  |  | -420 | 7587.45
2009-10-12 02:25 | 60.004 | 633 |  | 260.468 | 0 |  |  |  | -420 | 7587.78
2009-10-12 02:25 | 60.002 | 633 |  | 260.468 | 0 |  |  |  | -420 | 7588.11
2009-10-12 02:25 | 60.008 | 633 |  | 253.1415 | 0 |  |  |  | -420 | 7588.44
2009-10-12 02:25 | 60.01 | 633 |  | 253.1415 | 0 |  |  |  | -420 | 7588.77
2009-10-12 02:26 | 60.01 | 633 |  | 253.1415 | 0 |  |  |  | -420 | 7589.1
2009-10-12 02:26 | 60.011 | 633 |  | 253.1415 | 0 |  |  |  | -420 | 7589.43
2009-10-12 02:26 | 60.014 | 633 |  | 253.1415 | 0 |  |  |  | -420 | 7589.76
2009-10-12 02:26 | 60.013 | 633 |  | 251.9299 | 0 |  |  |  | -420 | 7590.09
2009-10-12 02:26 | 60.011 | 633 |  | 251.9299 | 0 |  |  |  | -420 | 7590.42
2009-10-12 02:26 | 60.011 | 633 |  | 251.9299 | 0 |  |  |  | -420 | 7590.75
2009-10-12 02:26 | 60.022 | 633 |  | 251.9299 | 0 |  |  |  | -420 | 7591.08
2009-10-12 02:26 | 60.017 | 633 |  | 251.9299 | 0 |  |  |  | -420 | 7591.41
2009-10-12 02:26 | 60.013 | 633 |  | 250.6742 | 0 |  |  |  | -420 | 7591.74
2009-10-12 02:26 | 60.014 | 633 |  | 250.6742 | 0 |  |  |  | -420 | 7592.07
2009-10-12 02:26 | 60.017 | 633 |  | 250.6742 | 0 |  |  |  | -420 | 7592.4
2009-10-12 02:26 | 60.019 | 633 |  | 250.6742 | 0 |  |  |  | -420 | 7592.73
2009-10-12 02:26 | 60.019 | 633 |  | 250.6742 | 0 |  |  |  | -420 | 7593.06
2009-10-12 02:26 | 60.027 | 633 |  | 253.6319 | 0 |  |  |  | -420 | 7593.39
2009-10-12 02:26 | 60.026 | 633 |  | 253.6319 | 0 |  |  |  | -420 | 7593.72
2009-10-12 02:26 | 60.022 | 633 |  | 253.6319 | 0 |  |  |  | -420 | 7594.05
2009-10-12 02:26 | 60.017 | 633 |  | 253.6319 | 0 |  |  |  | -420 | 7594.38
2009-10-12 02:26 | 60.019 | 633 |  | 253.6319 | 0 |  |  |  | -420 | 7594.71
2009-10-12 02:26 | 60.019 | 633 |  | 246.9573 | 0 |  |  |  | -420 | 7595.04
2009-10-12 02:26 | 60.021 | 633 |  | 246.9573 | 0 |  |  |  | -420 | 7595.37
2009-10-12 02:26 | 60.021 | 633 |  | 246.9573 | 0 |  |  |  | -420 | 7595.7
2009-10-12 02:27 | 60.019 | 633 |  | 246.9573 | 0 |  |  |  | -420 | 7596.03
2009-10-12 02:27 | 60.022 | 633 |  | 246.9573 | 0 |  |  |  | -420 | 7596.36
2009-10-12 02:27 | 60.031 | 633 |  | 254.5418 | 0 |  |  |  | -420 | 7596.69
2009-10-12 02:27 | 60.037 | 633 |  | 254.5418 | 0 |  |  |  | -420 | 7597.02
2009-10-12 02:27 | 60.036 | 633 |  | 254.5418 | 0 |  |  |  | -420 | 7597.35
2009-10-12 02:27 | 60.046 | 633 |  | 254.5418 | 0 |  |  |  | -420 | 7597.68
2009-10-12 02:27 | 60.048 | 633 |  | 165.1017 | 0 |  |  |  | -420 | 7598.01
2009-10-12 02:27 | 60.043 | 633 |  | 165.1017 | 0 |  |  |  | -420 | 7598.34
2009-10-12 02:27 | 60.041 | 633 |  | 165.1017 | 0 |  |  |  | -420 | 7598.67
2009-10-12 02:27 | 60.041 | 633 |  | 165.1017 | 0 |  |  |  | -420 | 7599
2009-10-12 02:27 | 60.039 | 633 |  | 165.1017 | 0 |  |  |  | -420 | 7599.33
2009-10-12 02:27 | 60.043 | 633 |  | 165.4764 | 0 |  |  |  | -420 | 7599.66
2009-10-12 02:27 | 60.045 | 633 |  | 165.4764 | 0 |  |  |  | -420 | 7599.99
2009-10-12 02:27 | 60.041 | 633 |  | 165.4764 | 0 |  |  |  | -420 | 7600.32
2009-10-12 02:27 | 60.041 | 633 |  | 165.4764 | 0 |  |  |  | -420 | 7600.65
2009-10-12 02:27 | 60.039 | 633 |  | 165.4764 | 0 |  |  |  | -420 | 7600.98
2009-10-12 02:27 | 59.978 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7601.31
2009-10-12 02:27 | 59.836 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7570
2009-10-12 02:27 | 59.869 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7569
2009-10-12 02:28 | 59.891 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.88 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.875 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.883 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.886 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.885 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.888 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.89 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.894 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.893 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.894 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.891 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.885 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.885 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.887 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.888 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.89 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.889 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7570
2009-10-12 02:28 | 59.873 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7568
2009-10-12 02:28 | 59.857 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7565
2009-10-12 02:28 | 59.852 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7560
2009-10-12 02:29 | 59.858 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7563
2009-10-12 02:29 | 59.866 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7564
2009-10-12 02:29 | 59.865 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7566
2009-10-12 02:29 | 59.866 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7570
2009-10-12 02:29 | 59.871 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7570
2009-10-12 02:29 | 59.879 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7570
2009-10-12 02:29 | 59.88 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7570
2009-10-12 02:29 | 59.886 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7570
2009-10-12 02:29 | 59.89 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7569
2009-10-12 02:29 | 59.889 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7575
2009-10-12 02:29 | 59.893 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7573
2009-10-12 02:29 | 59.903 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7571
2009-10-12 02:29 | 59.902 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7573
2009-10-12 02:29 | 59.904 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7575
2009-10-12 02:29 | 59.907 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7577
2009-10-12 02:29 | 59.916 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7577
2009-10-12 02:29 | 59.916 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7578
2009-10-12 02:29 | 59.918 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7579
2009-10-12 02:29 | 59.92 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7580
2009-10-12 02:29 | 59.92 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7581
2009-10-12 02:30 | 59.917 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7585
2009-10-12 02:30 | 59.921 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7588
2009-10-12 02:30 | 59.923 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7589
2009-10-12 02:30 | 59.925 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7589
2009-10-12 02:30 | 59.928 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7590
2009-10-12 02:30 | 59.932 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7590
2009-10-12 02:30 | 59.927 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7590
2009-10-12 02:30 | 59.931 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7591
2009-10-12 02:30 | 59.929 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7591
2009-10-12 02:30 | 59.931 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7591
2009-10-12 02:30 | 59.937 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7592
2009-10-12 02:30 | 59.945 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7592
2009-10-12 02:30 | 59.949 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7593
2009-10-12 02:30 | 59.942 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7594
2009-10-12 02:30 | 59.941 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7595
2009-10-12 02:30 | 59.945 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7655
2009-10-12 02:30 | 59.948 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7656
2009-10-12 02:30 | 59.949 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7656
2009-10-12 02:30 | 59.951 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7657
2009-10-12 02:30 | 59.953 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7657
2009-10-12 02:31 | 59.951 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7658
2009-10-12 02:31 | 59.952 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7658
2009-10-12 02:31 | 59.952 | 0 |  | 249.3376 | 0 |  |  |  | -420 | 7659
2009-10-12 02:31 | 59.952 | 0 |  | 249.3376 | 0 |  |  |  | -420 | 7659
2009-10-12 02:31 | 59.954 | 0 |  | 249.3376 | 0 |  |  |  | -420 | 7659
2009-10-12 02:31 | 59.953 | 0 |  | 249.3376 | 0 |  |  |  | -420 | 7660
2009-10-12 02:31 | 59.953 | 0 |  | 249.3376 | 0 |  |  |  | -420 | 7660
2009-10-12 02:31 | 59.954 | 0 |  | 258.2782 | 0 |  |  |  | -420 | 7661
2009-10-12 02:31 | 59.954 | 0 |  | 258.2782 | 0 |  |  |  | -420 | 7661
2009-10-12 02:31 | 59.957 | 0 |  | 258.2782 | 0 |  |  |  | -420 | 7625.4
2009-10-12 02:31 | 59.956 | 0 |  | 258.2782 | 0 |  |  |  | -420 | 7625.73
2009-10-12 02:31 | 59.956 | 0 |  | 258.2782 | 0 |  |  |  | -420 | 7626.06
2009-10-12 02:31 | 59.955 | 0 |  | 258.4064 | 0 |  |  |  | -420 | 7626.39
2009-10-12 02:31 | 59.961 | 0 |  | 258.4064 | 0 |  |  |  | -420 | 7626.72
2009-10-12 02:31 | 59.962 | 0 |  | 258.4064 | 0 |  |  |  | -420 | 7627.05
2009-10-12 02:31 | 59.968 | 0 |  | 258.4064 | 0 |  |  |  | -420 | 7627.38
2009-10-12 02:31 | 59.966 | 0 |  | 258.4064 | 0 |  |  |  | -420 | 7627.71
2009-10-12 02:31 | 59.968 | 0 |  | 260.5389 | 0 |  |  |  | -420 | 7628.04
2009-10-12 02:31 | 59.97 | 0 |  | 260.5389 | 0 |  |  |  | -420 | 7628.37
2009-10-12 02:32 | 59.97 | 0 |  | 260.5389 | 0 |  |  |  | -420 | 7628.7
2009-10-12 02:32 | 59.969 | 0 |  | 260.5389 | 0 |  |  |  | -420 | 7629.03
2009-10-12 02:32 | 59.97 | 0 |  | 260.5389 | 0 |  |  |  | -420 | 7629.36
2009-10-12 02:32 | 59.971 | 0 |  | 257.8821 | 0 |  |  |  | -420 | 7629.69
2009-10-12 02:32 | 59.973 | 0 |  | 257.8821 | 0 |  |  |  | -420 | 7630.02
2009-10-12 02:32 | 59.976 | 0 |  | 257.8821 | 0 |  |  |  | -420 | 7630.35
2009-10-12 02:32 | 59.978 | 0 |  | 257.8821 | 0 |  |  |  | -420 | 7630.68
2009-10-12 02:32 | 59.976 | 0 |  | 257.8821 | 0 |  |  |  | -420 | 7631.01
2009-10-12 02:32 | 59.976 | 0 |  | 258.5887 | 0 |  |  |  | -420 | 7631.34
2009-10-12 02:32 | 59.978 | 0 |  | 258.5887 | 0 |  |  |  | -420 | 7631.67
2009-10-12 02:32 | 59.98 | 0 |  | 258.5887 | 0 |  |  |  | -420 | 7632
2009-10-12 02:32 | 59.982 | 0 |  | 258.5887 | 0 |  |  |  | -420 | 7632.33
2009-10-12 02:32 | 59.98 | 0 |  | 258.5887 | 0 |  |  |  | -420 | 7632.66
2009-10-12 02:32 | 59.979 | 0 |  | 261.9062 | 0 |  |  |  | -420 | 7632.99
2009-10-12 02:32 | 59.979 | 0 |  | 261.9062 | 0 |  |  |  | -420 | 7633.32
2009-10-12 02:32 | 59.983 | 0 |  | 261.9062 | 0 |  |  |  | -420 | 7633.65
2009-10-12 02:32 | 59.984 | 0 |  | 261.9062 | 0 |  |  |  | -420 | 7633.98
2009-10-12 02:32 | 59.988 | 0 |  | 261.9062 | 0 |  |  |  | -420 | 7634.31
2009-10-12 02:32 | 59.987 | 0 |  | 256.7478 | 0 |  |  |  | -420 | 7634.64
2009-10-12 02:32 | 59.987 | 0 |  | 256.7478 | 0 |  |  |  | -420 | 7634.97
2009-10-12 02:33 | 59.993 | 0 |  | 256.7478 | 0 |  |  |  | -420 | 7635.3
2009-10-12 02:33 | 59.992 | 0 |  | 256.7478 | 0 |  |  |  | -420 | 7635.63
2009-10-12 02:33 | 59.989 | 0 |  | 256.7478 | 0 |  |  |  | -420 | 7635.96
2009-10-12 02:33 | 59.986 | 0 |  | 167.432 | 0 |  |  |  | -420 | 7636.29
2009-10-12 02:33 | 59.983 | 0 |  | 167.432 | 0 |  |  |  | -420 | 7636.62
2009-10-12 02:33 | 59.988 | 0 |  | 167.432 | 0 |  |  |  | -420 | 7636.95
2009-10-12 02:33 | 59.996 | 0 |  | 167.432 | 0 |  |  |  | -420 | 7637.28
2009-10-12 02:33 | 59.998 | 0 |  | 167.432 | 0 |  |  |  | -420 | 7637.61
2009-10-12 02:33 | 60.001 | 0 |  | 164.9734 | 0 |  |  |  | -420 | 7637.94
2009-10-12 02:33 | 59.999 | 0 |  | 164.9734 | 0 |  |  |  | -420 | 7638.27
2009-10-12 02:33 | 59.999 | 0 |  | 164.9734 | 0 |  |  |  | -420 | 7638.6
2009-10-12 02:33 | 60.002 | 0 |  | 164.9734 | 0 |  |  |  | -420 | 7638.93
2009-10-12 02:33 | 60.007 | 0 |  | 164.9734 | 0 |  |  |  | -420 | 7639.26
2009-10-12 02:33 | 60.008 | 0 |  | 157.6281 | 0 |  |  |  | -420 | 7639.59
2009-10-12 02:33 | 60.014 | 0 |  | 157.6281 | 0 |  |  |  | -420 | 7639.92
2009-10-12 02:33 | 60.017 | 0 |  | 157.6281 | 0 |  |  |  | -420 | 7640.25
2009-10-12 02:33 | 60.021 | 0 |  | 157.6281 | 0 |  |  |  | -420 | 7640.58
2009-10-12 02:33 | 60.017 | 0 |  | 157.6281 | 0 |  |  |  | -420 | 7640.91
2009-10-12 02:33 | 60.019 | 0 |  | 155.5317 | 0 |  |  |  | -420 | 7641.24
2009-10-12 02:33 | 60.023 | 0 |  | 155.5317 | 0 |  |  |  | -420 | 7641.57
2009-10-12 02:34 | 60.025 | 0 |  | 155.5317 | 0 |  |  |  | -420 | 7641.9
2009-10-12 02:34 | 60.021 | 0 |  | 155.5317 | 0 |  |  |  | -420 | 7642.23
2009-10-12 02:34 | 60.024 | 0 |  | 155.5317 | 0 |  |  |  | -420 | 7642.56
2009-10-12 02:34 | 60.024 | 0 |  | 160.4472 | 0 |  |  |  | -420 | 7642.89
2009-10-12 02:34 | 60.02 | 0 |  | 160.4472 | 0 |  |  |  | -420 | 7643.22
2009-10-12 02:34 | 60.025 | 0 |  | 160.4472 | 0 |  |  |  | -420 | 7643.55
2009-10-12 02:34 | 60.02 | 0 |  | 160.4472 | 0 |  |  |  | -420 | 7643.88
2009-10-12 02:34 | 60.02 | 0 |  | 160.4472 | 0 |  |  |  | -420 | 7644.21
2009-10-12 02:34 | 60.022 | 0 |  | 163.9586 | 0 |  |  |  | -420 | 7644.54
2009-10-12 02:34 | 60.022 | 0 |  | 163.9586 | 0 |  |  |  | -420 | 7644.87
2009-10-12 02:34 | 60.021 | 0 |  | 163.9586 | 0 |  |  |  | -420 | 7645.2
2009-10-12 02:34 | 60.023 | 0 |  | 163.9586 | 0 |  |  |  | -420 | 7645.53
2009-10-12 02:34 | 60.022 | 0 |  | 163.9586 | 0 |  |  |  | -420 | 7645.86
2009-10-12 02:34 | 60.019 | 0 |  | 166.0724 | 0 |  |  |  | -420 | 7646.19
2009-10-12 02:34 | 60.018 | 0 |  | 166.0724 | 0 |  |  |  | -420 | 7646.52
2009-10-12 02:34 | 60.018 | 0 |  | 166.0724 | 0 |  |  |  | -420 | 7646.85
2009-10-12 02:34 | 60.019 | 0 |  | 166.0724 | 0 |  |  |  | -420 | 7647.18
2009-10-12 02:34 | 60.019 | 0 |  | 166.0724 | 0 |  |  |  | -420 | 7647.51
2009-10-12 02:34 | 60.015 | 0 |  | 163.7666 | 0 |  |  |  | -420 | 7647.84
2009-10-12 02:34 | 60.016 | 0 |  | 163.7666 | 0 |  |  |  | -420 | 7648.17
2009-10-12 02:34 | 60.013 | 0 |  | 163.7666 | 0 |  |  |  | -420 | 7648.5
2009-10-12 02:35 | 60.012 | 0 |  | 163.7666 | 0 |  |  |  | -420 | 7648.83
2009-10-12 02:35 | 60.01 | 0 |  | 163.7666 | 0 |  |  |  | -420 | 7649.16
2009-10-12 02:35 | 60.007 | 0 |  | 165.1017 | 0 |  |  |  | -420 | 7649.49
2009-10-12 02:35 | 60.009 | 0 |  | 165.1017 | 0 |  |  |  | -420 | 7649.82
2009-10-12 02:35 | 60.009 | 0 |  | 165.1017 | 0 |  |  |  | -420 | 7650.15
2009-10-12 02:35 | 60.003 | 0 |  | 165.1017 | 0 |  |  |  | -420 | 7650.48
2009-10-12 02:35 | 59.999 | 0 |  | 165.1017 | 0 |  |  |  | -420 | 7650.81
2009-10-12 02:35 | 59.992 | 0 |  | 165.4764 | 0 |  |  |  | -420 | 7651.14
2009-10-12 02:35 | 59.991 | 0 |  | 165.4764 | 0 |  |  |  | -420 | 7651.47
2009-10-12 02:35 | 59.992 | 0 |  | 165.4764 | 0 |  |  |  | -420 | 7651.8
2009-10-12 02:35 | 59.988 | 0 |  | 165.4764 | 0 |  |  |  | -420 | 7652.13
2009-10-12 02:35 | 59.985 | 0 |  | 165.4764 | 0 |  |  |  | -420 | 7652.46
2009-10-12 02:35 | 59.984 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7652.79
2009-10-12 02:35 | 59.984 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7616
2009-10-12 02:35 | 59.982 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7626
2009-10-12 02:35 | 59.982 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7632
2009-10-12 02:35 | 59.979 | 0 |  | 206.4591 | 0 |  |  |  | -420 | 7632
2009-10-12 02:35 | 59.976 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7632
2009-10-12 02:35 | 59.976 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.982 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.978 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.974 | 0 |  | 211.256 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.976 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.977 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.975 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.969 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.97 | 0 |  | 214.3467 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.973 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.978 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.978 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.975 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.976 | 0 |  | 212.1727 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.975 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.969 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.966 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.966 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.969 | 0 |  | 215.5982 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.968 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.965 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7632
2009-10-12 02:36 | 59.97 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7632
2009-10-12 02:37 | 59.972 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7632
2009-10-12 02:37 | 59.967 | 0 |  | 218.3273 | 0 |  |  |  | -420 | 7632
2009-10-12 02:37 | 59.969 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7632
2009-10-12 02:37 | 59.969 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7632
2009-10-12 02:37 | 59.967 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7631
2009-10-12 02:37 | 59.966 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7625
2009-10-12 02:37 | 59.965 | 0 |  | 217.3794 | 0 |  |  |  | -420 | 7623
2009-10-12 02:37 | 59.967 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7621
2009-10-12 02:37 | 59.965 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7623
2009-10-12 02:37 | 59.964 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7625
2009-10-12 02:37 | 59.97 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7627
2009-10-12 02:37 | 59.969 | 0 |  | 214.8304 | 0 |  |  |  | -420 | 7628
2009-10-12 02:37 | 59.968 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7628
2009-10-12 02:37 | 59.965 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7629
2009-10-12 02:37 | 59.97 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7630
2009-10-12 02:37 | 59.968 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7631
2009-10-12 02:37 | 59.965 | 0 |  | 227.6559 | 0 |  |  |  | -420 | 7635
2009-10-12 02:37 | 59.969 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7638
2009-10-12 02:37 | 59.967 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7639
2009-10-12 02:38 | 59.966 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7642
2009-10-12 02:38 | 59.979 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7644
2009-10-12 02:38 | 59.983 | 0 |  | 225.0181 | 0 |  |  |  | -420 | 7645
2009-10-12 02:38 | 59.974 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7647
2009-10-12 02:38 | 59.965 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7648
2009-10-12 02:38 | 59.962 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7649
2009-10-12 02:38 | 59.961 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7650
2009-10-12 02:38 | 59.961 | 0 |  | 228.3652 | 0 |  |  |  | -420 | 7651
2009-10-12 02:38 | 59.963 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7652
2009-10-12 02:38 | 59.959 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7653
2009-10-12 02:38 | 59.951 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7654
2009-10-12 02:38 | 59.953 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7655
2009-10-12 02:38 | 59.957 | 0 |  | 234.0753 | 0 |  |  |  | -420 | 7655
2009-10-12 02:38 | 59.956 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7656
2009-10-12 02:38 | 59.963 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7656
2009-10-12 02:38 | 59.961 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7657
2009-10-12 02:38 | 59.963 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7657
2009-10-12 02:38 | 59.963 | 0 |  | 228.7982 | 0 |  |  |  | -420 | 7658
2009-10-12 02:38 | 59.968 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7658
2009-10-12 02:38 | 59.968 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7659
2009-10-12 02:38 | 59.97 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7659
2009-10-12 02:39 | 59.973 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7659
2009-10-12 02:39 | 59.965 | 0 |  | 229.467 | 0 |  |  |  | -420 | 7660
2009-10-12 02:39 | 59.967 | 0 |  | 228.9802 | 0 |  |  |  | -420 | 7660
2009-10-12 02:39 | 59.972 | 0 |  | 228.9802 | 0 |  |  |  | -420 | 7661
2009-10-12 02:39 | 59.976 | 0 |  | 228.9802 | 0 |  |  |  | -420 | 7661
2009-10-12 02:39 | 59.969 | 0 |  | 228.9802 | 0 |  |  |  | -420 | 7662
2009-10-12 02:39 | 59.973 | 0 |  | 228.9802 | 0 |  |  |  | -420 | 7662
2009-10-12 02:39 | 59.978 | 0 |  | 219.9756 | 0 |  |  |  | -420 | 7663
2009-10-12 02:39 | 59.981 | 0 |  | 219.9756 | 0 |  |  |  | -420 | 7663
2009-10-12 02:39 | 59.981 | 0 |  | 219.9756 | 0 |  |  |  | -420 | 7664
2009-10-12 02:39 | 59.982 | 0 |  | 219.9756 | 0 |  |  |  | -420 | 7664
2009-10-12 02:39 | 59.984 | 0 |  | 219.9756 | 0 |  |  |  | -420 | 7665
2009-10-12 02:39 | 59.982 | 0 |  | 229.0892 | 0 |  |  |  | -420 | 7666
2009-10-12 02:39 | 59.979 | 0 |  | 229.0892 | 0 |  |  |  | -420 | 7666
2009-10-12 02:39 | 59.98 | 0 |  | 229.0892 | 0 |  |  |  | -420 | 7667
2009-10-12 02:39 | 59.978 | 0 |  | 229.0892 | 0 |  |  |  | -420 | 7668
2009-10-12 02:39 | 59.98 | 0 |  | 229.0892 | 0 |  |  |  | -420 | 7668
2009-10-12 02:39 | 59.98 | 0 |  | 229.6633 | 0 |  |  |  | -420 | 7669
2009-10-12 02:39 | 59.978 | 0 |  | 229.6633 | 0 |  |  |  | -420 | 7669
2009-10-12 02:40 | 59.972 | 0 |  | 229.6633 | 0 |  |  |  | -420 | 7670
2009-10-12 02:40 | 59.971 | 0 |  | 229.6633 | 0 |  |  |  | -420 | 7670
2009-10-12 02:40 | 59.974 | 0 |  | 229.6633 | 0 |  |  |  | -420 | 7671
2009-10-12 02:40 | 59.975 | 0 |  | 229.2339 | 0 |  |  |  | -420 | 7671
2009-10-12 02:40 | 59.972 | 0 |  | 229.2339 | 0 |  |  |  | -420 | 7672
2009-10-12 02:40 | 59.969 | 0 |  | 229.2339 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.974 | 0 |  | 229.2339 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.972 | 0 |  | 229.2339 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.972 | 0 |  | 231.4099 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.977 | 0 |  | 231.4099 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.978 | 0 |  | 231.4099 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.976 | 0 |  | 231.4099 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.974 | 0 |  | 231.4099 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.977 | 0 |  | 218.6223 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.978 | 0 |  | 218.6223 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.979 | 0 |  | 218.6223 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.977 | 0 |  | 218.6223 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.974 | 0 |  | 218.6223 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.971 | 0 |  | 213.5359 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.971 | 0 |  | 213.5359 | 0 |  |  |  | -420 | 7673
2009-10-12 02:40 | 59.968 | 0 |  | 213.5359 | 0 |  |  |  | -420 | 7673
2009-10-12 02:41 | 59.966 | 0 |  | 213.5359 | 0 |  |  |  | -420 | 7674
2009-10-12 02:41 | 59.971 | 0 |  | 213.5359 | 0 |  |  |  | -420 | 7675
2009-10-12 02:41 | 59.973 | 0 |  | 225.6519 | 0 |  |  |  | -420 | 7676
2009-10-12 02:41 | 59.969 | 0 |  | 225.6519 | 0 |  |  |  | -420 | 7677
2009-10-12 02:41 | 59.972 | 0 |  | 225.6519 | 0 |  |  |  | -420 | 7678
2009-10-12 02:41 | 59.973 | 0 |  | 225.6519 | 0 |  |  |  | -420 | 7679
2009-10-12 02:41 | 59.97 | 0 |  | 225.6519 | 0 |  |  |  | -420 | 7680
2009-10-12 02:41 | 59.974 | 0 |  | 212.5736 | 0 |  |  |  | -420 | 7681
2009-10-12 02:41 | 59.982 | 0 |  | 212.5736 | 0 |  |  |  | -420 | 7682
2009-10-12 02:41 | 59.985 | 0 |  | 212.5736 | 0 |  |  |  | -420 | 7684
2009-10-12 02:41 | 59.985 | 0 |  | 212.5736 | 0 |  |  |  | -420 | 7685
2009-10-12 02:41 | 59.989 | 0 |  | 212.5736 | 0 |  |  |  | -420 | 7687
2009-10-12 02:41 | 59.989 | 0 |  | 219.8973 | 0 |  |  |  | -420 | 7689
2009-10-12 02:41 | 59.987 | 0 |  | 219.8973 | 0 |  |  |  | -420 | 7690
2009-10-12 02:41 | 59.99 | 0 |  | 219.8973 | 0 |  |  |  | -420 | 7692
2009-10-12 02:41 | 59.996 | 0 |  | 219.8973 | 0 |  |  |  | -420 | 7692
2009-10-12 02:41 | 60.001 | 0 |  | 219.8973 | 0 |  |  |  | -420 | 7693
2009-10-12 02:41 | 60.004 | 0 |  | 231.1754 | 0 |  |  |  | -420 | 7693
2009-10-12 02:41 | 60.006 | 0 |  | 231.1754 | 0 |  |  |  | -420 | 7694
2009-10-12 02:42 | 60.014 | 0 |  | 231.1754 | 0 |  |  |  | -420 | 7694
2009-10-12 02:42 | 60.019 | 0 |  | 231.1754 | 0 |  |  |  | -420 | 7695
2009-10-12 02:42 | 60.025 | 0 |  | 231.1754 | 0 |  |  |  | -420 | 7695
2009-10-12 02:42 | 60.026 | 0 |  | 226.6341 | 0 |  |  |  | -420 | 7695
2009-10-12 02:42 | 60.029 | 0 |  | 226.6341 | 0 |  |  |  | -420 | 7696
2009-10-12 02:42 | 60.029 | 0 |  | 226.6341 | 0 |  |  |  | -420 | 7696
2009-10-12 02:42 | 60.036 | 0 |  | 226.6341 | 0 |  |  |  | -420 | 7697
2009-10-12 02:42 | 60.037 | 0 |  | 226.6341 | 0 |  |  |  | -420 | 7697
2009-10-12 02:42 | 60.036 | 0 |  | 227.2551 | 0 |  |  |  | -420 | 7697
2009-10-12 02:42 | 60.041 | 0 |  | 227.2551 | 0 |  |  |  | -420 | 7698
2009-10-12 02:42 | 60.044 | 0 |  | 227.2551 | 0 |  |  |  | -420 | 7698
2009-10-12 02:42 | 60.043 | 0 |  | 227.2551 | 0 |  |  |  | -420 | 7698.33
2009-10-12 02:42 | 60.048 | 0 |  | 227.2551 | 0 |  |  |  | -420 | 7698.66
2009-10-12 02:42 | 60.046 | 0 |  | 229.2902 | 0 |  |  |  | -420 | 7698.99
2009-10-12 02:42 | 60.043 | 0 |  | 229.2902 | 0 |  |  |  | -420 | 7699.32
2009-10-12 02:42 | 60.043 | 0 |  | 229.2902 | 0 |  |  |  | -420 | 7699.65
2009-10-12 02:42 | 60.043 | 0 |  | 229.2902 | 0 |  |  |  | -420 | 7699.98
2009-10-12 02:42 | 60.043 | 0 |  | 229.2902 | 0 |  |  |  | -420 | 7700.31
2009-10-12 02:42 | 60.04 | 0 |  | 221.4614 | 0 |  |  |  | -420 | 7700.64
2009-10-12 02:42 | 60.041 | 0 |  | 221.4614 | 0 |  |  |  | -420 | 7700.97
2009-10-12 02:42 | 60.039 | 0 |  | 221.4614 | 0 |  |  |  | -420 | 7701.3
2009-10-12 02:43 | 60.036 | 0 |  | 221.4614 | 0 |  |  |  | -420 | 7701.63
2009-10-12 02:43 | 60.033 | 0 |  | 221.4614 | 0 |  |  |  | -420 | 7701.96
2009-10-12 02:43 | 60.034 | 0 |  | 241.2744 | 0 |  |  |  | -420 | 7702.29
2009-10-12 02:43 | 60.037 | 0 |  | 241.2744 | 0 |  |  |  | -420 | 7702.62
2009-10-12 02:43 | 60.035 | 0 |  | 241.2744 | 0 |  |  |  | -420 | 7702.95
2009-10-12 02:43 | 60.033 | 0 |  | 241.2744 | 0 |  |  |  | -420 | 7703.28
2009-10-12 02:43 | 60.036 | 0 |  | 241.2744 | 0 |  |  |  | -420 | 7703.61
2009-10-12 02:43 | 60.034 | 0 |  | 243.0719 | 0 |  |  |  | -420 | 7703.94
2009-10-12 02:43 | 60.032 | 0 |  | 243.0719 | 0 |  |  |  | -420 | 7704.27
2009-10-12 02:43 | 60.034 | 0 |  | 243.0719 | 0 |  |  |  | -420 | 7704.6
2009-10-12 02:43 | 60.033 | 0 |  | 243.0719 | 0 |  |  |  | -420 | 7704.93
2009-10-12 02:43 | 60.035 | 0 |  | 243.0719 | 0 |  |  |  | -420 | 7705.26
2009-10-12 02:43 | 60.035 | 0 |  | 241.6702 | 0 |  |  |  | -420 | 7705.59
2009-10-12 02:43 | 60.039 | 0 |  | 241.6702 | 0 |  |  |  | -420 | 7705.92
2009-10-12 02:43 | 60.037 | 0 |  | 241.6702 | 0 |  |  |  | -420 | 7706.25
2009-10-12 02:43 | 60.036 | 0 |  | 241.6702 | 0 |  |  |  | -420 | 7706.58
2009-10-12 02:43 | 60.034 | 0 |  | 241.6702 | 0 |  |  |  | -420 | 7706.91
2009-10-12 02:43 | 60.037 | 0 |  | 228.1493 | 0 |  |  |  | -420 | 7707.24
2009-10-12 02:43 | 60.037 | 0 |  | 228.1493 | 0 |  |  |  | -420 | 7707.57
2009-10-12 02:44 | 60.038 | 0 |  | 228.1493 | 0 |  |  |  | -420 | 7707.9
2009-10-12 02:44 | 60.04 | 0 |  | 228.1493 | 0 |  |  |  | -420 | 7708.23
2009-10-12 02:44 | 60.045 | 0 |  | 228.1493 | 0 |  |  |  | -420 | 7708.56
2009-10-12 02:44 | 60.045 | 0 |  | 235.129 | 0 |  |  |  | -420 | 7708.89
2009-10-12 02:44 | 60.043 | 0 |  | 235.129 | 0 |  |  |  | -420 | 7709.22
2009-10-12 02:44 | 60.04 | 0 |  | 235.129 | 0 |  |  |  | -420 | 7709.55
2009-10-12 02:44 | 60.046 | 0 |  | 235.129 | 0 |  |  |  | -420 | 7709.88
2009-10-12 02:44 | 60.042 | 0 |  | 235.129 | 0 |  |  |  | -420 | 7710.21
2009-10-12 02:44 | 60.039 | 0 |  | 246.4331 | 0 |  |  |  | -420 | 7710.54
2009-10-12 02:44 | 60.039 | 0 |  | 246.4331 | 0 |  |  |  | -420 | 7710.87
2009-10-12 02:44 | 60.037 | 0 |  | 246.4331 | 0 |  |  |  | -420 | 7711.2
2009-10-12 02:44 | 60.034 | 0 |  | 246.4331 | 0 |  |  |  | -420 | 7711.53
2009-10-12 02:44 | 60.032 | 0 |  | 246.4331 | 0 |  |  |  | -420 | 7711.86
2009-10-12 02:44 | 60.031 | 0 |  | 236.5535 | 0 |  |  |  | -420 | 7712.19
2009-10-12 02:44 | 60.027 | 0 |  | 236.5535 | 0 |  |  |  | -420 | 7712.52
2009-10-12 02:44 | 60.031 | 0 |  | 236.5535 | 0 |  |  |  | -420 | 7712.85
2009-10-12 02:44 | 60.031 | 0 |  | 236.5535 | 0 |  |  |  | -420 | 7713.18
2009-10-12 02:44 | 60.031 | 0 |  | 236.5535 | 0 |  |  |  | -420 | 7713.51
2009-10-12 02:44 | 60.039 | 0 |  | 230.2976 | 0 |  |  |  | -420 | 7713.84
2009-10-12 02:44 | 60.039 | 0 |  | 230.2976 | 0 |  |  |  | -420 | 7714.17
2009-10-12 02:44 | 60.037 | 0 |  | 230.2976 | 0 |  |  |  | -420 | 7714.5
2009-10-12 02:45 | 60.035 | 0 |  | 230.2976 | 0 |  |  |  | -420 | 7714.83
2009-10-12 02:45 | 60.04 | 0 |  | 230.2976 | 0 |  |  |  | -420 | 7715.16
2009-10-12 02:45 | 60.042 | 0 |  | 231.1755 | 0 |  |  |  | -420 | 7715.49
2009-10-12 02:45 | 60.036 | 0 |  | 231.1755 | 0 |  |  |  | -420 | 7715.82
2009-10-12 02:45 | 60.04 | 0 |  | 231.1755 | 0 |  |  |  | -420 | 7716.15
2009-10-12 02:45 | 60.045 | 0 |  | 231.1755 | 0 |  |  |  | -420 | 7716.48
2009-10-12 02:45 | 60.048 | 0 |  | 231.1755 | 0 |  |  |  | -420 | 7716.81
2009-10-12 02:45 | 60.044 | 0 |  | 225.6176 | 0 |  |  |  | -420 | 7717.14
2009-10-12 02:45 | 60.044 | 0 |  | 225.6176 | 0 |  |  |  | -420 | 7717.47
2009-10-12 02:45 | 60.044 | 0 |  | 225.6176 | 0 |  |  |  | -420 | 7717.8
2009-10-12 02:45 | 60.04 | 0 |  | 225.6176 | 0 |  |  |  | -420 | 7718.13
2009-10-12 02:45 | 60.045 | 0 |  | 225.6176 | 0 |  |  |  | -420 | 7718.46
2009-10-12 02:45 | 60.044 | 0 |  | 230.7344 | 0 |  |  |  | -420 | 7718.79
2009-10-12 02:45 | 60.039 | 0 |  | 230.7344 | 0 |  |  |  | -420 | 7719.12
2009-10-12 02:45 | 60.042 | 0 |  | 230.7344 | 0 |  |  |  | -420 | 7719.45
2009-10-12 02:45 | 60.041 | 0 |  | 230.7344 | 0 |  |  |  | -420 | 7719.78
2009-10-12 02:45 | 60.038 | 0 |  | 230.7344 | 0 |  |  |  | -420 | 7720.11
2009-10-12 02:45 | 60.037 | 0 |  | 234.8471 | 0 |  |  |  | -420 | 7720.44
2009-10-12 02:45 | 60.039 | 0 |  | 234.8471 | 0 |  |  |  | -420 | 7720.77
2009-10-12 02:46 | 60.04 | 0 |  | 234.8471 | 0 |  |  |  | -420 | 7721.1
2009-10-12 02:46 | 60.039 | 0 |  | 234.8471 | 0 |  |  |  | -420 | 7721.43
2009-10-12 02:46 | 60.038 | 0 |  | 234.8471 | 0 |  |  |  | -420 | 7721.76
2009-10-12 02:46 | 60.039 | 0 |  | 228.9609 | 0 |  |  |  | -420 | 7722.09
2009-10-12 02:46 | 60.037 | 0 |  | 228.9609 | 0 |  |  |  | -420 | 7722.42
2009-10-12 02:46 | 60.037 | 0 |  | 228.9609 | 0 |  |  |  | -420 | 7722.75
2009-10-12 02:46 | 60.039 | 0 |  | 228.9609 | 0 |  |  |  | -420 | 7723.08
2009-10-12 02:46 | 60.038 | 0 |  | 228.9609 | 0 |  |  |  | -420 | 7723.41
2009-10-12 02:46 | 60.035 | 0 |  | 231.1779 | 0 |  |  |  | -420 | 7723.74
2009-10-12 02:46 | 60.033 | 0 |  | 231.1779 | 0 |  |  |  | -420 | 7724.07
2009-10-12 02:46 | 60.03 | 0 |  | 231.1779 | 0 |  |  |  | -420 | 7724.4
2009-10-12 02:46 | 60.032 | 0 |  | 231.1779 | 0 |  |  |  | -420 | 7724.73
2009-10-12 02:46 | 60.037 | 0 |  | 231.1779 | 0 |  |  |  | -420 | 7725.06
2009-10-12 02:46 | 60.042 | 0 |  | 236.4893 | 0 |  |  |  | -420 | 7725.39
2009-10-12 02:46 | 60.036 | 0 |  | 236.4893 | 0 |  |  |  | -420 | 7725.72
2009-10-12 02:46 | 60.031 | 0 |  | 236.4893 | 0 |  |  |  | -420 | 7726.05
2009-10-12 02:46 | 60.031 | 0 |  | 236.4893 | 0 |  |  |  | -420 | 7726.38
2009-10-12 02:46 | 60.034 | 0 |  | 236.4893 | 0 |  |  |  | -420 | 7726.71
2009-10-12 02:46 | 60.032 | 0 |  | 245.0389 | 0 |  |  |  | -420 | 7727.04
2009-10-12 02:46 | 60.038 | 0 |  | 245.0389 | 0 |  |  |  | -420 | 7727.37
2009-10-12 02:46 | 60.044 | 0 |  | 245.0389 | 0 |  |  |  | -420 | 7727.7
2009-10-12 02:47 | 60.042 | 0 |  | 245.0389 | 0 |  |  |  | -420 | 7728.03
2009-10-12 02:47 | 60.04 | 0 |  | 245.0389 | 0 |  |  |  | -420 | 7728.36
2009-10-12 02:47 | 60.04 | 0 |  | 223.6057 | 0 |  |  |  | -420 | 7728.69
2009-10-12 02:47 | 60.043 | 0 |  | 223.6057 | 0 |  |  |  | -420 | 7729.02
2009-10-12 02:47 | 60.041 | 0 |  | 223.6057 | 0 |  |  |  | -420 | 7729.35
2009-10-12 02:47 | 60.038 | 0 |  | 223.6057 | 0 |  |  |  | -420 | 7729.68
2009-10-12 02:47 | 60.043 | 0 |  | 223.6057 | 0 |  |  |  | -420 | 7730.01
2009-10-12 02:47 | 60.042 | 0 |  | 231.1194 | 0 |  |  |  | -420 | 7730.34
2009-10-12 02:47 | 60.036 | 0 |  | 231.1194 | 0 |  |  |  | -420 | 7730.67
2009-10-12 02:47 | 60.041 | 0 |  | 231.1194 | 0 |  |  |  | -420 | 7731
2009-10-12 02:47 | 60.042 | 0 |  | 231.1194 | 0 |  |  |  | -420 | 7731.33
2009-10-12 02:47 | 60.043 | 0 |  | 231.1194 | 0 |  |  |  | -420 | 7731.66
2009-10-12 02:47 | 60.036 | 0 |  | 237.2066 | 0 |  |  |  | -420 | 7731.99
2009-10-12 02:47 | 60.039 | 0 |  | 237.2066 | 0 |  |  |  | -420 | 7732.32
2009-10-12 02:47 | 60.037 | 0 |  | 237.2066 | 0 |  |  |  | -420 | 7732.65
2009-10-12 02:47 | 60.035 | 0 |  | 237.2066 | 0 |  |  |  | -420 | 7732.98
2009-10-12 02:47 | 60.035 | 0 |  | 237.2066 | 0 |  |  |  | -420 | 7733.31
2009-10-12 02:47 | 60.036 | 0 |  | 240.5164 | 0 |  |  |  | -420 | 7733.64
2009-10-12 02:47 | 60.03 | 0 |  | 240.5164 | 0 |  |  |  | -420 | 7733.97
2009-10-12 02:48 | 60.03 | 0 |  | 240.5164 | 0 |  |  |  | -420 | 7734.3
2009-10-12 02:48 | 60.031 | 0 |  | 240.5164 | 0 |  |  |  | -420 | 7734.63
2009-10-12 02:48 | 60.032 | 0 |  | 240.5164 | 0 |  |  |  | -420 | 7734.96
2009-10-12 02:48 | 60.031 | 0 |  | 237.5661 | 0 |  |  |  | -420 | 7735.29
2009-10-12 02:48 | 60.032 | 0 |  | 237.5661 | 0 |  |  |  | -420 | 7735.62
2009-10-12 02:48 | 60.032 | 0 |  | 237.5661 | 0 |  |  |  | -420 | 7735.95
2009-10-12 02:48 | 60.037 | 0 |  | 237.5661 | 0 |  |  |  | -420 | 7736.28
2009-10-12 02:48 | 60.04 | 0 |  | 237.5661 | 0 |  |  |  | -420 | 7736.61
2009-10-12 02:48 | 60.042 | 0 |  | 231.5814 | 0 |  |  |  | -420 | 7736.94
2009-10-12 02:48 | 60.036 | 0 |  | 231.5814 | 0 |  |  |  | -420 | 7737.27
2009-10-12 02:48 | 60.041 | 0 |  | 231.5814 | 0 |  |  |  | -420 | 7737.6
2009-10-12 02:48 | 60.04 | 0 |  | 231.5814 | 0 |  |  |  | -420 | 7737.93
2009-10-12 02:48 | 60.036 | 0 |  | 231.5814 | 0 |  |  |  | -420 | 7738.26
2009-10-12 02:48 | 60.038 | 0 |  | 235.8508 | 0 |  |  |  | -420 | 7738.59
2009-10-12 02:48 | 60.041 | 0 |  | 235.8508 | 0 |  |  |  | -420 | 7738.92
2009-10-12 02:48 | 60.04 | 0 |  | 235.8508 | 0 |  |  |  | -420 | 7739.25
2009-10-12 02:48 | 60.033 | 0 |  | 235.8508 | 0 |  |  |  | -420 | 7739.58
2009-10-12 02:48 | 60.034 | 0 |  | 235.8508 | 0 |  |  |  | -420 | 7739.91
2009-10-12 02:48 | 60.04 | 0 |  | 233.56 | 0 |  |  |  | -420 | 7740.24
2009-10-12 02:48 | 60.041 | 0 |  | 233.56 | 0 |  |  |  | -420 | 7740.57
2009-10-12 02:49 | 60.037 | 0 |  | 233.56 | 0 |  |  |  | -420 | 7740.9
2009-10-12 02:49 | 60.036 | 0 |  | 233.56 | 0 |  |  |  | -420 | 7741.23
2009-10-12 02:49 | 60.038 | 0 |  | 233.56 | 0 |  |  |  | -420 | 7741.56
2009-10-12 02:49 | 60.039 | 0 |  | 219.01 | 0 |  |  |  | -420 | 7741.89
2009-10-12 02:49 | 60.034 | 0 |  | 219.01 | 0 |  |  |  | -420 | 7742.22
2009-10-12 02:49 | 60.033 | 0 |  | 219.01 | 0 |  |  |  | -420 | 7742.55
2009-10-12 02:49 | 60.034 | 0 |  | 219.01 | 0 |  |  |  | -420 | 7742.88
2009-10-12 02:49 | 60.029 | 0 |  | 219.01 | 0 |  |  |  | -420 | 7743.21
2009-10-12 02:49 | 60.031 | 0 |  | 205.3389 | 0 |  |  |  | -420 | 7743.54
2009-10-12 02:49 | 60.03 | 0 |  | 205.3389 | 0 |  |  |  | -420 | 7743.87
2009-10-12 02:49 | 60.026 | 0 |  | 205.3389 | 0 |  |  |  | -420 | 7744.2
2009-10-12 02:49 | 60.022 | 0 |  | 205.3389 | 0 |  |  |  | -420 | 7744.53
2009-10-12 02:49 | 60.024 | 0 |  | 205.3389 | 0 |  |  |  | -420 | 7744.86
2009-10-12 02:49 | 60.023 | 0 |  | 236.2854 | 0 |  |  |  | -420 | 7745.19
2009-10-12 02:49 | 60.021 | 0 |  | 236.2854 | 0 |  |  |  | -420 | 7745.52
2009-10-12 02:49 | 60.023 | 0 |  | 236.2854 | 0 |  |  |  | -420 | 7745.85
2009-10-12 02:49 | 60.026 | 0 |  | 236.2854 | 0 |  |  |  | -420 | 7746.18
2009-10-12 02:49 | 60.026 | 0 |  | 236.2854 | 0 |  |  |  | -420 | 7746.51
2009-10-12 02:49 | 60.024 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7746.84
2009-10-12 02:49 | 60.024 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7747.17
2009-10-12 02:50 | 60.023 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7747.5
2009-10-12 02:50 | 60.023 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7747.83
2009-10-12 02:50 | 60.026 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7748.16
2009-10-12 02:50 | 60.029 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7748.49
2009-10-12 02:50 | 60.024 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7748.82
2009-10-12 02:50 | 60.021 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7749.15
2009-10-12 02:50 | 60.025 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7749.48
2009-10-12 02:50 | 60.025 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7749.81
2009-10-12 02:50 | 60.026 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7750.14
2009-10-12 02:50 | 60.024 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7750.47
2009-10-12 02:50 | 60.023 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7750.8
2009-10-12 02:50 | 60.026 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7751.13
2009-10-12 02:50 | 60.02 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7751.46
2009-10-12 02:50 | 60.02 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7751.79
2009-10-12 02:50 | 60.015 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7752.12
2009-10-12 02:50 | 60.016 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7752.45
2009-10-12 02:50 | 60.015 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7752.78
2009-10-12 02:50 | 60.015 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7753.11
2009-10-12 02:50 | 60.017 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7753.44
2009-10-12 02:50 | 60.012 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7753.77
2009-10-12 02:50 | 60.008 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7754.1
2009-10-12 02:51 | 60.002 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7754.43
2009-10-12 02:51 | 59.999 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7754.76
2009-10-12 02:51 | 60.002 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7755.09
2009-10-12 02:51 | 60.004 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7755.42
2009-10-12 02:51 | 60.001 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7755.75
2009-10-12 02:51 | 59.993 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7756.08
2009-10-12 02:51 | 59.992 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7756.41
2009-10-12 02:51 | 59.987 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7756.74
2009-10-12 02:51 | 59.985 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7757.07
2009-10-12 02:51 | 59.986 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7757.4
2009-10-12 02:51 | 59.984 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7757.73
2009-10-12 02:51 | 59.98 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7758.06
2009-10-12 02:51 | 59.977 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7758.39
2009-10-12 02:51 | 59.976 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7758.72
2009-10-12 02:51 | 59.972 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7759.05
2009-10-12 02:51 | 59.977 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7759.38
2009-10-12 02:51 | 59.975 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7759.71
2009-10-12 02:51 | 59.971 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7760.04
2009-10-12 02:51 | 59.971 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7760.37
2009-10-12 02:52 | 59.979 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7760.7
2009-10-12 02:52 | 59.98 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7761.03
2009-10-12 02:52 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7761.36
2009-10-12 02:52 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7761.69
2009-10-12 02:52 | 59.981 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7762.02
2009-10-12 02:52 | 59.979 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7762.35
2009-10-12 02:52 | 59.976 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7762.68
2009-10-12 02:52 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7763.01
2009-10-12 02:52 | 59.976 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7763.34
2009-10-12 02:52 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7763.67
2009-10-12 02:52 | 59.971 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7764
2009-10-12 02:52 | 59.97 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7764.33
2009-10-12 02:52 | 59.971 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7764.66
2009-10-12 02:52 | 59.99 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7764.99
2009-10-12 02:52 | 59.999 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7765.32
2009-10-12 02:52 | 59.999 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7765.65
2009-10-12 02:52 | 59.999 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7765.98
2009-10-12 02:52 | 60.003 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7766.31
2009-10-12 02:52 | 60.005 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7766.64
2009-10-12 02:52 | 60.01 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7766.97
2009-10-12 02:52 | 60.02 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7767.3
2009-10-12 02:53 | 60.022 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7767.63
2009-10-12 02:53 | 60.025 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7767.96
2009-10-12 02:53 | 60.025 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7768.29
2009-10-12 02:53 | 60.023 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7768.62
2009-10-12 02:53 | 60.029 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7768.95
2009-10-12 02:53 | 60.029 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7769.28
2009-10-12 02:53 | 60.028 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7769.61
2009-10-12 02:53 | 60.031 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7769.94
2009-10-12 02:53 | 60.032 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7770.27
2009-10-12 02:53 | 60.033 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7770.6
2009-10-12 02:53 | 60.03 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7770.93
2009-10-12 02:53 | 60.021 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7771.26
2009-10-12 02:53 | 60.019 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7771.59
2009-10-12 02:53 | 60.017 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7771.92
2009-10-12 02:53 | 60.017 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7772.25
2009-10-12 02:53 | 60.015 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7772.58
2009-10-12 02:53 | 60.015 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7772.91
2009-10-12 02:53 | 60.009 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7773.24
2009-10-12 02:53 | 60.008 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7773.57
2009-10-12 02:54 | 60.005 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7773.9
2009-10-12 02:54 | 60.005 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7774.23
2009-10-12 02:54 | 59.999 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7774.56
2009-10-12 02:54 | 59.997 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7774.89
2009-10-12 02:54 | 60 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7775.22
2009-10-12 02:54 | 59.998 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7775.55
2009-10-12 02:54 | 59.994 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7775.88
2009-10-12 02:54 | 59.992 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7776.21
2009-10-12 02:54 | 59.988 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7776.54
2009-10-12 02:54 | 59.985 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7776.87
2009-10-12 02:54 | 59.988 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7777.2
2009-10-12 02:54 | 59.988 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7777.53
2009-10-12 02:54 | 59.983 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7777.86
2009-10-12 02:54 | 59.983 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7778.19
2009-10-12 02:54 | 59.986 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7778.52
2009-10-12 02:54 | 59.987 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7778.85
2009-10-12 02:54 | 59.986 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7779.18
2009-10-12 02:54 | 59.985 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7779.51
2009-10-12 02:54 | 59.983 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7779.84
2009-10-12 02:54 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7780.17
2009-10-12 02:54 | 59.98 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7780.5
2009-10-12 02:55 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7780.83
2009-10-12 02:55 | 59.975 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7781.16
2009-10-12 02:55 | 59.973 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7781.49
2009-10-12 02:55 | 59.976 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7781.82
2009-10-12 02:55 | 59.976 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7782.15
2009-10-12 02:55 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7782.48
2009-10-12 02:55 | 59.979 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7782.81
2009-10-12 02:55 | 59.977 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7783.14
2009-10-12 02:55 | 59.977 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7783.47
2009-10-12 02:55 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7783.8
2009-10-12 02:55 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7784.13
2009-10-12 02:55 | 59.983 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7784.46
2009-10-12 02:55 | 59.981 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7784.79
2009-10-12 02:55 | 59.978 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7785.12
2009-10-12 02:55 | 59.979 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7785.45
2009-10-12 02:55 | 59.979 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7785.78
2009-10-12 02:55 | 59.983 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7786.11
2009-10-12 02:55 | 59.99 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7786.44
2009-10-12 02:55 | 59.992 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7786.77
2009-10-12 02:55 | 59.99 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7787.1
2009-10-12 02:56 | 59.988 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7787.43
2009-10-12 02:56 | 59.99 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7787.76
2009-10-12 02:56 | 59.993 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7788.09
2009-10-12 02:56 | 59.993 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7788.42
2009-10-12 02:56 | 59.994 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7788.75
2009-10-12 02:56 | 59.993 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7789.08
2009-10-12 02:56 | 59.989 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7789.41
2009-10-12 02:56 | 59.986 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7789.74
2009-10-12 02:56 | 59.985 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7790.07
2009-10-12 02:56 | 59.987 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7790.4
2009-10-12 02:56 | 59.986 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7790.73
2009-10-12 02:56 | 59.985 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7791.06
2009-10-12 02:56 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7791.39
2009-10-12 02:56 | 59.982 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7791.72
2009-10-12 02:56 | 59.987 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7792.05
2009-10-12 02:56 | 59.997 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7792.38
2009-10-12 02:56 | 60 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7792.71
2009-10-12 02:56 | 60.003 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7793.04
2009-10-12 02:56 | 60.003 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7793.37
2009-10-12 02:56 | 60.003 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7793.7
2009-10-12 02:57 | 60.002 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7794.03
2009-10-12 02:57 | 60.004 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7794.36
2009-10-12 02:57 | 60.005 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7794.69
2009-10-12 02:57 | 60.009 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7795.02
2009-10-12 02:57 | 60.012 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7795.35
2009-10-12 02:57 | 60.021 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7795.68
2009-10-12 02:57 | 60.022 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7796.01
2009-10-12 02:57 | 60.02 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7796.34
2009-10-12 02:57 | 60.018 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7796.67
2009-10-12 02:57 | 60.02 | 0 |  | 223.0157 | 0 |  |  |  | -420 | 7797
2009-10-12 02:57 | 60.02 | 0
2009-10-12 02:57 | 60.018 | 0
2009-10-12 02:57 | 60.019 | 0
2009-10-12 02:57 | 60.018 | 0
2009-10-12 02:57 | 60.017 | 0
2009-10-12 02:57 | 60.016 | 0
2009-10-12 02:57 | 60.016 | 0
2009-10-12 02:57 | 60.014 | 0
2009-10-12 02:57 | 60.014 | 0
2009-10-12 02:58 | 60.013 | 0
2009-10-12 02:58 | 60.015 | 0
2009-10-12 02:58 | 60.016 | 0
2009-10-12 02:58 | 60.019 | 0
2009-10-12 02:58 | 60.021 | 0
2009-10-12 02:58 | 60.02 | 0
2009-10-12 02:58 | 60.024 | 0
2009-10-12 02:58 | 60.026 | 0
2009-10-12 02:58 | 60.026 | 0
2009-10-12 02:58 | 60.022 | 0
2009-10-12 02:58 | 60.022 | 0
2009-10-12 02:58 | 60.024 | 0
2009-10-12 02:58 | 60.029 | 0
2009-10-12 02:58 | 60.028 | 0
2009-10-12 02:58 | 60.032 | 0
2009-10-12 02:58 | 60.035 | 0
2009-10-12 02:58 | 60.028 | 0
2009-10-12 02:58 | 60.021 | 0
2009-10-12 02:58 | 60.024 | 0
2009-10-12 02:58 | 60.025 | 0
2009-10-12 02:58 | 60.022 | 0
2009-10-12 02:59 | 60.023 | 0
2009-10-12 02:59 | 60.02 | 0
2009-10-12 02:59 | 60.02 | 0
2009-10-12 02:59 | 60.02 | 0
2009-10-12 02:59 | 60.017 | 0
2009-10-12 02:59 | 60.012 | 0
2009-10-12 02:59 | 60.01 | 0
2009-10-12 02:59 | 60.01 | 0
2009-10-12 02:59 | 60.01 | 0
2009-10-12 02:59 | 60.012 | 0
2009-10-12 02:59 | 60.012 | 0
2009-10-12 02:59 | 60.014 | 0
2009-10-12 02:59 | 60.013 | 0
2009-10-12 02:59 | 60.011 | 0
2009-10-12 02:59 | 60.01 | 0
2009-10-12 02:59 | 60.01 | 0
2009-10-12 02:59 | 60.011 | 0
2009-10-12 02:59 | 60.016 | 0
2009-10-12 02:59 | 60.018 | 0
2009-10-12 03:00 | 60.019 | 0
2009-10-12 03:00 | 60.019 | 0
2009-10-12 03:00 | 60.02 | 0
2009-10-12 03:00 | 60.018 | 0
2009-10-12 03:00 | 60.016 | 0
2009-10-12 03:00 | 60.016 | 0
2009-10-12 03:00 | 60.023 | 0
2009-10-12 03:00 | 60.022 | 0
2009-10-12 03:00 | 60.015 | 0
2009-10-12 03:00 | 60.016 | 0
2009-10-12 03:00 | 60.017 | 0
2009-10-12 03:00 | 60.01 | 0
2009-10-12 03:00 | 60.004 | 0
2009-10-12 03:00 | 59.995 | 0
2009-10-12 03:00 | 59.982 | 0
2009-10-12 03:00 | 59.974 | 0
2009-10-12 03:00 | 59.97 | 0
2009-10-12 03:00 | 59.968 | 0
2009-10-12 03:00 | 59.968 | 0
2009-10-12 03:00 | 59.972 | 0
2009-10-12 03:00 | 59.966 | 0
2009-10-12 03:01 | 59.964 | 0
2009-10-12 03:01 | 59.966 | 0
2009-10-12 03:01 | 59.963 | 0
2009-10-12 03:01 | 59.965 | 0
2009-10-12 03:01 | 59.968 | 0
2009-10-12 03:01 | 59.97 | 0
2009-10-12 03:01 | 59.97 | 0
2009-10-12 03:01 | 59.972 | 0
2009-10-12 03:01 | 59.976 | 0
2009-10-12 03:01 | 59.975 | 0
2009-10-12 03:01 | 59.977 | 0
2009-10-12 03:01 | 59.976 | 0
2009-10-12 03:01 | 59.974 | 0
2009-10-12 03:01 | 59.974 | 0
2009-10-12 03:01 | 59.974 | 0
2009-10-12 03:01 | 59.977 | 0
2009-10-12 03:01 | 59.979 | 0
2009-10-12 03:01 | 59.983 | 0
2009-10-12 03:01 | 59.985 | 0
2009-10-12 03:02 | 59.98 | 0
2009-10-12 03:02 | 59.979 | 0
2009-10-12 03:02 | 59.987 | 0
2009-10-12 03:02 | 59.986 | 0
2009-10-12 03:02 | 59.98 | 0
2009-10-12 03:02 | 59.982 | 0
2009-10-12 03:02 | 59.985 | 0
2009-10-12 03:02 | 59.987 | 0
2009-10-12 03:02 | 59.992 | 0
2009-10-12 03:02 | 59.996 | 0
2009-10-12 03:02 | 59.997 | 0
2009-10-12 03:02 | 59.997 | 0
2009-10-12 03:02 | 59.997 | 0
2009-10-12 03:02 | 59.996 | 0
2009-10-12 03:02 | 59.996 | 0
2009-10-12 03:02 | 59.998 | 0
2009-10-12 03:02 | 60.009 | 0
2009-10-12 03:02 | 60.01 | 0
2009-10-12 03:02 | 60.005 | 0
2009-10-12 03:02 | 60.004 | 0
2009-10-12 03:02 | 60.003 | 0
2009-10-12 03:03 | 60.001 | 0
2009-10-12 03:03 | 60.004 | 0
2009-10-12 03:03 | 60.007 | 0
2009-10-12 03:03 | 60.008 | 0
2009-10-12 03:03 | 60.008 | 0
2009-10-12 03:03 | 60.006 | 0
2009-10-12 03:03 | 60.006 | 0
2009-10-12 03:03 | 60 | 0
2009-10-12 03:03 | 59.999 | 0
2009-10-12 03:03 | 60 | 0
2009-10-12 03:03 | 60.004 | 0
2009-10-12 03:03 | 60.013 | 0
2009-10-12 03:03 | 60.015 | 0
2009-10-12 03:03 | 60.012 | 0
2009-10-12 03:03 | 60.009 | 0
2009-10-12 03:03 | 60.008 | 0
2009-10-12 03:03 | 60.011 | 0
2009-10-12 03:03 | 60.013 | 0
2009-10-12 03:03 | 60.016 | 0
2009-10-12 03:04 | 60.018 | 0
2009-10-12 03:04 | 60.019 | 0
2009-10-12 03:04 | 60.013 | 0
2009-10-12 03:04 | 60.011 | 0
2009-10-12 03:04 | 60.009 | 0
2009-10-12 03:04 | 60.008 | 0
2009-10-12 03:04 | 60.011 | 0
2009-10-12 03:04 | 60.015 | 0
2009-10-12 03:04 | 60.021 | 0
2009-10-12 03:04 | 60.018 | 0
2009-10-12 03:04 | 60.019 | 0
2009-10-12 03:04 | 60.019 | 0
2009-10-12 03:04 | 60.022 | 0
2009-10-12 03:04 | 60.025 | 0
2009-10-12 03:04 | 60.03 | 0
2009-10-12 03:04 | 60.027 | 0
2009-10-12 03:04 | 60.021 | 0
2009-10-12 03:04 | 60.023 | 0
2009-10-12 03:04 | 60.02 | 0
2009-10-12 03:04 | 60.024 | 0
2009-10-12 03:05 | 60.022 | 0
2009-10-12 03:05 | 60.022 | 0
2009-10-12 03:05 | 60.025 | 0
2009-10-12 03:05 | 60.023 | 0
2009-10-12 03:05 | 60.02 | 0
2009-10-12 03:05 | 60.018 | 0
2009-10-12 03:05 | 60.008 | 0
2009-10-12 03:05 | 60.012 | 0
2009-10-12 03:05 | 60.019 | 0
2009-10-12 03:05 | 60.019 | 0
2009-10-12 03:05 | 60.016 | 0
2009-10-12 03:05 | 60.015 | 0
2009-10-12 03:05 | 60.014 | 0
2009-10-12 03:05 | 60.016 | 0
2009-10-12 03:05 | 60.019 | 0
2009-10-12 03:05 | 60.016 | 0
2009-10-12 03:05 | 60.014 | 0
2009-10-12 03:05 | 60.018 | 0
2009-10-12 03:05 | 60.023 | 0
2009-10-12 03:05 | 60.024 | 0
2009-10-12 03:06 | 60.026 | 0
2009-10-12 03:06 | 60.024 | 0
2009-10-12 03:06 | 60.02 | 0
2009-10-12 03:06 | 60.019 | 0
2009-10-12 03:06 | 60.025 | 0
2009-10-12 03:06 | 60.028 | 0
2009-10-12 03:06 | 60.031 | 0
2009-10-12 03:06 | 60.029 | 0
2009-10-12 03:06 | 60.026 | 0
2009-10-12 03:06 | 60.029 | 0
2009-10-12 03:06 | 60.033 | 0
2009-10-12 03:06 | 60.03 | 0
2009-10-12 03:06 | 60.016 | 0
2009-10-12 03:06 | 60.019 | 0
2009-10-12 03:06 | 60.028 | 0
2009-10-12 03:06 | 60.021 | 0
2009-10-12 03:06 | 60.015 | 0
2009-10-12 03:06 | 60.012 | 0
2009-10-12 03:06 | 60.014 | 0
2009-10-12 03:06 | 60.013 | 0
2009-10-12 03:06 | 60.016 | 0
2009-10-12 03:07 | 60.016 | 0
2009-10-12 03:07 | 60.013 | 0
2009-10-12 03:07 | 60.007 | 0
2009-10-12 03:07 | 59.994 | 0
2009-10-12 03:07 | 59.993 | 0
2009-10-12 03:07 | 59.993 | 0
2009-10-12 03:07 | 59.994 | 0
2009-10-12 03:07 | 59.994 | 0
2009-10-12 03:07 | 59.993 | 0
2009-10-12 03:07 | 59.988 | 0
2009-10-12 03:07 | 59.985 | 0
2009-10-12 03:07 | 59.982 | 0
2009-10-12 03:07 | 59.98 | 0
2009-10-12 03:07 | 59.981 | 0
2009-10-12 03:07 | 59.982 | 0
2009-10-12 03:07 | 59.98 | 0
2009-10-12 03:07 | 59.98 | 0
2009-10-12 03:07 | 59.98 | 0
2009-10-12 03:07 | 59.983 | 0
2009-10-12 03:08 | 59.981 | 0
2009-10-12 03:08 | 59.981 | 0
2009-10-12 03:08 | 59.981 | 0
2009-10-12 03:08 | 59.981 | 0
2009-10-12 03:08 | 59.98 | 0
2009-10-12 03:08 | 59.978 | 0
2009-10-12 03:08 | 59.979 | 0
2009-10-12 03:08 | 59.978 | 0
2009-10-12 03:08 | 59.976 | 0
2009-10-12 03:08 | 59.975 | 0
2009-10-12 03:08 | 59.975 | 0
2009-10-12 03:08 | 59.979 | 0
2009-10-12 03:08 | 59.975 | 0
2009-10-12 03:08 | 59.976 | 0
2009-10-12 03:08 | 59.977 | 0
2009-10-12 03:08 | 59.975 | 0
2009-10-12 03:08 | 59.979 | 0
2009-10-12 03:08 | 59.98 | 0
2009-10-12 03:08 | 59.978 | 0
2009-10-12 03:08 | 59.979 | 0
2009-10-12 03:08 | 59.983 | 0
2009-10-12 03:09 | 59.987 | 0
2009-10-12 03:09 | 59.984 | 0
2009-10-12 03:09 | 59.98 | 0
2009-10-12 03:09 | 59.98 | 0
2009-10-12 03:09 | 59.979 | 0
2009-10-12 03:09 | 59.975 | 0
2009-10-12 03:09 | 59.979 | 0
2009-10-12 03:09 | 59.983 | 0
2009-10-12 03:09 | 59.983 | 0
2009-10-12 03:09 | 59.99 | 0
2009-10-12 03:09 | 59.987 | 0
2009-10-12 03:09 | 59.976 | 0
2009-10-12 03:09 | 59.979 | 0
2009-10-12 03:09 | 59.983 | 0
2009-10-12 03:09 | 59.979 | 0
2009-10-12 03:09 | 59.978 | 0
2009-10-12 03:09 | 59.975 | 0
2009-10-12 03:09 | 59.989 | 0
2009-10-12 03:09 | 59.999 | 0
2009-10-12 03:10 | 59.989 | 0
2009-10-12 03:10 | 59.986 | 0
2009-10-12 03:10 | 59.983 | 0
2009-10-12 03:10 | 59.982 | 0
2009-10-12 03:10 | 59.99 | 0
2009-10-12 03:10 | 59.995 | 0
2009-10-12 03:10 | 59.99 | 0
2009-10-12 03:10 | 59.989 | 0
2009-10-12 03:10 | 59.996 | 0
2009-10-12 03:10 | 60 | 0
2009-10-12 03:10 | 60.004 | 0
2009-10-12 03:10 | 60.004 | 0
2009-10-12 03:10 | 59.999 | 0
2009-10-12 03:10 | 59.998 | 0
2009-10-12 03:10 | 59.996 | 0
2009-10-12 03:10 | 60.001 | 0
2009-10-12 03:10 | 60.001 | 0
2009-10-12 03:10 | 60.003 | 0
2009-10-12 03:10 | 60.004 | 0
2009-10-12 03:10 | 60.004 | 0
2009-10-12 03:10 | 60.006 | 0
2009-10-12 03:11 | 60.003 | 0
2009-10-12 03:11 | 60.006 | 0
2009-10-12 03:11 | 60.009 | 0
2009-10-12 03:11 | 60.01 | 0
2009-10-12 03:11 | 60.009 | 0
2009-10-12 03:11 | 60.015 | 0
2009-10-12 03:11 | 60.014 | 0
2009-10-12 03:11 | 60.009 | 0
2009-10-12 03:11 | 60.008 | 0
2009-10-12 03:11 | 60.01 | 0
2009-10-12 03:11 | 60.009 | 0
2009-10-12 03:11 | 60.013 | 0
2009-10-12 03:11 | 60.014 | 0
2009-10-12 03:11 | 60.012 | 0
2009-10-12 03:11 | 60.01 | 0
2009-10-12 03:11 | 60.007 | 0
2009-10-12 03:11 | 60.003 | 0
2009-10-12 03:11 | 60 | 0
2009-10-12 03:11 | 59.998 | 0
2009-10-12 03:11 | 59.999 | 0
2009-10-12 03:12 | 60.002 | 0
2009-10-12 03:12 | 60.003 | 0
2009-10-12 03:12 | 59.999 | 0
2009-10-12 03:12 | 60.001 | 0
2009-10-12 03:12 | 59.995 | 0
2009-10-12 03:12 | 59.987 | 0
2009-10-12 03:12 | 59.988 | 0
2009-10-12 03:12 | 59.99 | 0
2009-10-12 03:12 | 59.992 | 0
2009-10-12 03:12 | 59.992 | 0

## Entry Data
Balancing Authority Name: | HQ
Balancing Authority Frequency Response Obligation (FRO from FRS Form 1) | -141
Note: See "Instruction" tab for more detailed instructions.
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Determine Time of T(0) and edit formula in cell "C8" to reference the correct row of the "Data" worksheet. | 40098.1023
T(0) is the first change in frequency of about 0.010 Hz (10 mHz) which should be the first scan of frequency data of the event.
Step 3. | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
Step 4. | Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 5. | Paste data into FRS Form 1 in the appropriate row on the "BA Event Data" worksheet.
Step 6. | Save this workbook using the following file name format:MyBA_yymmdd_hhmm_FRS_Form2.xlsm
| 2009-10-12 02:27 | Date yymmdd
| 40098.1023 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
Copy Data for Pasting into Form 1
Note on C8: Cell "C8": Observe the first change in frequency that identifies the beginning of the event. Look in column "B" of the "Data" worksheet. Select and edit the formula in this cell ("=Data!Axxx") to reference that row number in the "Data" sheet of this first change in frequency where xxx is that row number.
Note on C11: Cell "C11": Similar to identifying the end of a DCS event but only looking at frequency, observe frequency following the beginning of the event. When actual frequency recovers to 60.00 Hz or to the pre-event frequency, edit the formula in this cell to reference that row number in the "Data" worksheet that this occurs. ("=Data!Axxx")

## IPFR
IPFR = Interconnection Primary Frequency Response

## Evaluation
scan rate | 2 | seconds |  |  | Date: | 2009-10-12 02:27 |  |  | Balancing Authority | HQ | [10 empty] | A Point | 40098.1023 |  |  |  |  | A Point | 40098.1023 | [13 empty] | Non-Conforming Load sign convention | - | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27 | [12 empty] | Date: | 2009-10-12 02:27
[5 empty] | Time of T(0) | 40098.1023 |  |  | Grid Nominal Frequency | 60 | Hz | [9 empty] | FPointA | 60.039 | 40098.1023 |  |  |  | FPointA | 60.039 | 40098.1023 | [26 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023 | [12 empty] | Time of T(0) | 40098.1023
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 |  |  | Capacity @ Droop for Minimum Performance | 4230 | MW | [9 empty] | A Value | 60.0417 |  |  |  |  | A Value | 60.0417 | [27 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062 | [12 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40098.1062
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz |  | Droop Setting | 5% | 3 | Hz | [8 empty] | C Value | 59.836 | #N/A |  |  |  | C Value | 59.836 | #N/A | [26 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz | [11 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 60.0417 | Hz
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8887 | Hz |  | Deadband Setting | 0 | Hz | [9 empty] | Delta FCA | -0.20575 |  |  |  |  | Delta FC | [28 empty] | Value B Post-Perturbation Average Frequency [T(+12 to T(+24)] | 59.8823 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+30)] | 59.8844 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+40)] | 59.8892 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+18 to T(+52)] | 59.8879 | Hz | [11 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8887 | Hz
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15304 | Hz |  | Hz Span | 3 | Hz | [9 empty] | FR C | -307.6528 | MW/0.1 Hz | [32 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15946 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15732 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15257 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15381 | Hz | [11 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.15304 | Hz
[5 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW |  | Frequency Response Obligation (FRO) | -141 | MW/0.1 Hz | [9 empty] | Slope A-C dF/dT | #N/A | Hz/second |  |  |  |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | [18 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW | [11 empty] | Value A Pre-Perturbation Average Interchange MW [T(-2 ) to T(-16)] | 633 | MW
[5 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 0 | MW | [13 empty] | C Value Maximum Resource Loss | 633 | [5 empty] | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec | [18 empty] | Value B Post-Perturbation Average Interchange MW [T(+12 to T(+24)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+30)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+40)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+18 to T(+52)] | 0 | MW | [11 empty] | Value B Post-Perturbation Average Interchange MW [T(+20 to T(+52)] | 0 | MW
[5 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW | [13 empty] | Secondary C Value | No | n/a | Time |  |  | B Frequency Value | 59.8823 |  | 59.8844 |  | 59.8887 |  | 59.8879 |  | 59.8887 | [19 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW | [11 empty] | Pre to Post Perturbation Interchange Delta MW Actual | -633 | MW
[5 empty] | Initial Performance Ramp Magnitude Adjustment | 0 | MW | [19 empty] | Delta FB | -0.15946 | -397.4363 | -0.15732 | -402.6343 | -0.15304 | -415.1637 | -0.15381 | -411.9588 | -0.15304 | -413.8616 | [18 empty] | Net Total Adjustments | 44.4559 | MW | [11 empty] | Net Total Adjustments | 45.8265 | MW | [11 empty] | Net Total Adjustments | 47.2313 | MW | [11 empty] | Net Total Adjustments | 47.2321 | MW | [11 empty] | Net Total Adjustments | 47.3148 | MW
[5 empty] | EPFR Pre-Perturbation Average | -58.8674 | MW | [19 empty] | Slope B dF/dT | -0.0079732 |  | -0.0078661 |  | -0.0076522 |  | -0.0076903 |  | -0.0076522 | [19 empty] | EPFR for FRO Pre-Perturbation Average | -58.8674 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -58.8674 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -58.8674 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -58.8674 | MW | [11 empty] | EPFR for FRO Pre-Perturbation Average | -58.8674 | MW
[5 empty] | EPFR Post-Perturbation Average | 156.9246 | MW | [19 empty] | RatioB-C | 77.5032 |  | 76.4617 |  | 74.3829 |  | 74.753 |  | 74.3829 | [19 empty] | EPFR for FRO Post-Perturbation Average | 165.9766 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 162.9553 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 156.2529 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 157.9982 | MW | [11 empty] | EPFR for FRO Post-Perturbation Average | 156.9246 | MW
[5 empty] | EPFR Delta | 215.792 | MW |  | TC (frequency response filter constant) | 1 | Time Constant for delayed delivery of PFR during Sustained Measure | [15 empty] | Sustainability Index | -0.017185 |  | -0.019328 |  | -0.023605 |  | -0.022844 |  | -0.023605 | [19 empty] | EPFR for FRO Delta | 224.8441 | MW | [11 empty] | EPFR for FRO Delta | 221.8228 | MW | [11 empty] | EPFR for FRO Delta | 215.1203 | MW | [11 empty] | EPFR for FRO Delta | 216.8656 | MW | [11 empty] | EPFR for FRO Delta | 215.792 | MW
[21 empty] | Tzero | 40098.1023 | [33 empty] | EPFR for FRO Adjusted | 269.3 | MW | [11 empty] | EPFR for FRO Adjusted | 267.6493 | MW | [11 empty] | EPFR for FRO Adjusted | 262.3516 | MW | [11 empty] | EPFR for FRO Adjusted | 264.0977 | MW | [11 empty] | EPFR for FRO Adjusted | 263.1068 | MW
[21 empty] | FT+4 | 59.836 | [33 empty] | Pre JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -420 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [10 empty] | FT+10 | 59.891 | [33 empty] | Pre Non-Conforming Load MW | 165.4296 |  |  |  | Post-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.4296 |  |  |  | Post-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.4296 | MW |  |  | Post-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.4296 | MW |  |  | Post-Perturbation Bias Setting | -420 | MW/0.1 Hz | [6 empty] | Pre Non-Conforming Load MW | 165.4296 | MW |  |  | Post-Perturbation Bias Setting | -420 | MW/0.1 Hz
[9 empty] | 0 | Actual Interchange MW Average during frequency recovery period | [10 empty] | FT+20 | 59.883 | [33 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -175.3498 | MW | [6 empty] | Pre Pumped Hydro MW | 0 |  |  |  | EPFR for Bias Setting Pre-Perturbation Average | -175.3498 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -175.3498 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -175.3498 | MW | [6 empty] | Pre Pumped Hydro MW | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | -175.3498 | MW
[9 empty] | 437.5776 | Target Interchange MW Average during frequency recovery period | [10 empty] | FT+60 | 59.89 | [33 empty] | Pre Ramping Units MW | 0 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 494.3985 | MW | [6 empty] | Pre Ramping Units MW | 0 |  |  |  | EPFR for Bias Setting Post-Perturbation Average | 485.3989 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 465.4341 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 470.6329 | MW | [6 empty] | Pre Ramping Units MW | 0 | MW |  |  | EPFR for Bias Setting Post-Perturbation Average | 467.4349 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 215.792 | MW |  | 348.0951 | Interchange Average Ramp MW during frequency recovery period | [8 empty] | Interconnection Evaluation | [36 empty] | Pre Transferred Frequency Response MW | 0 |  |  |  | EPFR for Bias Setting Delta | 669.7483 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 |  |  |  | EPFR for Bias Setting Delta | 660.7487 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 640.7839 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 645.9827 | MW | [6 empty] | Pre Transferred Frequency Response MW | 0 | MW |  |  | EPFR for Bias Setting Delta | 642.7847 | MW
[9 empty] | 633 | Actual MW @ T(-4) | [45 empty] | Pre Contingent BA Lost Generation MW | 0 |  |  |  | Primary Frequency Response Delivery of Bias | -94.51% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 |  |  |  | Primary Frequency Response Delivery of Bias | -95.8% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -98.79% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -97.99% | [7 empty] | Pre Contingent BA Lost Generation MW | 0 | MW |  |  | Primary Frequency Response Delivery of Bias | -98.48%
[9 empty] | -693.629 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [45 empty] | Sum of Pre Perturbation Adjustments | 165.4296 | [12 empty] | Sum of Pre Perturbation Adjustments | 165.4296 | [12 empty] | Sum of Pre Perturbation Adjustments | 165.4296 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 165.4296 | MW | [11 empty] | Sum of Pre Perturbation Adjustments | 165.4296 | MW
[9 empty] | 0:06 | Event Duration (h:mm:ss)
[9 empty] | Yes | Target MW Average minus MW @ T(-4) less than zero | [10 empty] | B Value Average Resource Loss | 633 | [33 empty] | Post JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 |  |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW | [6 empty] | Post JOU Dynamic Schedules MW | 0 | MW |  |  | Pre-Perturbation BA Load | 7600.1963 | MW
[9 empty] | 498.2066 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average LaaR Loss | 0 | [33 empty] | Post Non-Conforming Load MW | 209.8855 |  |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | 211.256 |  |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | 212.6609 | MW |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | 212.6617 | MW |  |  | Post-Perturbation BA Load | 7570 | MW | [6 empty] | Post Non-Conforming Load MW | 212.7443 | MW |  |  | Post-Perturbation BA Load | 7570 | MW
[9 empty] | 60.629 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [10 empty] | B Value Average Net Loss | 633 | [33 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 0 |  |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW | [6 empty] | Post Pumped Hydro MW | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -30.1963 | MW
[9 empty] | Yes | Interchange Actual Average minus MW @ T(-4) less than zero | [45 empty] | Post Ramping Units MW | 0 |  |  |  | Load Dampening Frequency Response | -18.9361 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 |  |  |  | Load Dampening Frequency Response | -19.194 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -19.792 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -19.6328 | MW/0.1 Hz | [6 empty] | Post Ramping Units MW | 0 | MW |  |  | Load Dampening Frequency Response | -19.7304 | MW/0.1 Hz
[9 empty] | No | Interchange Average MW minus MW @ T(-4) greater than zero | [13 empty] | Interconnection Bias Total | [31 empty] | Post Transferred Frequency Response MW | 0 |  |  |  | Load Dampening % of Total BA Frequency Response | -4.77% | [7 empty] | Post Transferred Frequency Response MW | 0 |  |  |  | Load Dampening % of Total BA Frequency Response | -4.77% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -4.77% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -4.77% | [7 empty] | Post Transferred Frequency Response MW | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | -4.77%
[9 empty] | No | Interchange Target MW Average minus MW @ T(-4) greater than zero | [13 empty] | EI | ERCOT | WECC | [29 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | [12 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW | [11 empty] | Post Contingent BA Lost Generation MW | 0 | MW
[9 empty] | -195.4224 | Interchange Target Relative Average Change - MW (High Frequency Event) | [10 empty] | Interconnection Bias Setting | -660 |  | -6349 | -660 | -2024 | [29 empty] | Sum of Post Perturbation Adjustments | 209.8855 | [12 empty] | Sum of Post Perturbation Adjustments | 211.256 | [12 empty] | Sum of Post Perturbation Adjustments | 212.6609 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 212.6617 | MW | [11 empty] | Sum of Post Perturbation Adjustments | 212.7443 | MW
[9 empty] | -633 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [10 empty] | IPFR as a % of Bias Setting | 0% | [33 empty] | Net Total Adjustments MW | 44.4559 | [12 empty] | Net Total Adjustments MW | 45.8265 | [12 empty] | Net Total Adjustments MW | 47.2313 | MW | [11 empty] | Net Total Adjustments MW | 47.2321 | MW | [11 empty] | Net Total Adjustments MW | 47.3148 | MW
[9 empty] | Down | Ramp Direction during frequency recovery period | [10 empty] | Interconnection Total Energy | 37446 | 60.07%
[21 empty] | Interconnection Peak Energy | 62339 |  |  |  |  | Frequency and Interconnection Frequency Response @ different Average periods of B | [11 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 12 to 24 second Average Period Evaluation | [13 empty] | 18 to 30 second Average Period Evaluation | [13 empty] | 20 to 40 second Average Period Evaluation | [13 empty] | 18 to 52 second Average Period Evaluation | [13 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 2.9334 | P.U. |  | No Evaluation | P.U. Sustianed Response P.U. Performance | [45 empty] | Initial P.U. Performance for FRO | 2.8153 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 2.8536 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 2.9425 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 2.9189 | P.U. | [11 empty] | Initial P.U. Performance for FRO | 2.9334 | P.U.
[56 empty] | Initial P.U. Performance Adjusted for FRO | 2.3505 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 2.365 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 2.4128 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 2.3968 | P.U. | [11 empty] | Initial P.U. Performance Adjusted for FRO | 2.4059 | P.U.
[9 empty] | Initial | [6 empty] | Generator | Generator | Generator | Generator | Generator | Generator | Generator | LaaR | Total | Interconnection | FR B | [15 empty] | JOU | Non- |  |  | Transferred | Contingent |  |  | FRO |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected |  |  |  |  | JOU | Non- |  |  | Transferred | Contingent |  |  | Frequency | Expected
[7 empty] | FRO |  | Measure |  |  | Average | Average |  | Average | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Trip | Generation | Primary | 20 to 52 sec |  | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Expected |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net |  |  |  | Net | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Response | Net
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | MW | MW | MW | MW | MW | MW | MW | MW | Trip | Frequency | Average |  | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Primary |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual |  |  |  | Actual | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Obligation | Actual
|  |  | Total | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [8 empty] | MW | Response | MW |  | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | Freq Response |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange |  |  | Frequency | Interchange | Imp(-) Exp (+) | Load (-) | Load (-) Gen (+) | Gen (+) | Rec (-) Del (+) | Load (-) Gen (+) | Setting |  | EPFR | Interchange
|  |  | Generation | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery | [12 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW |  | T | Hz | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW
|  | Frequency | Lost | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW | 633 | [8 empty] | MW/0.1 Hz
0
T-72 sec | 40098.1015 | 60.027 | 633 |  |  |  | -38.0706 | -38.0706 | [15 empty] | 0 |  |  | T-72 sec | [10 empty] | T-72 sec | 40098.1015 | 60.027 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7593.39 | -38.0706 | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015 | [12 empty] | T-72 sec | 40098.1015
T-70 sec | 40098.1015 | 60.027 | 633 |  |  |  | -38.0706 | -38.0706 | [15 empty] | 0 |  |  | T-70 sec | [10 empty] | T-70 sec | 40098.1015 | 60.027 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7593.39 | -38.0706 | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015 | [12 empty] | T-70 sec | 40098.1015
T-68 sec | 40098.1015 | 60.026 | 633 |  |  |  | -36.6614 | -36.6614 | [15 empty] | 0 |  |  | T-68 sec | [10 empty] | T-68 sec | 40098.1015 | 60.026 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7593.72 | -36.6614 | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015 | [12 empty] | T-68 sec | 40098.1015
T-66 sec | 40098.1016 | 60.022 | 633 |  |  |  | -31.0191 | -31.0191 | [15 empty] | 0 |  |  | T-66 sec | [10 empty] | T-66 sec | 40098.1016 | 60.022 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7594.05 | -31.0191 | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016 | [12 empty] | T-66 sec | 40098.1016
T-64 sec | 40098.1016 | 60.022 | 633 |  |  |  | -31.0191 | -31.0191 | [15 empty] | 0 |  |  | T-64 sec | [10 empty] | T-64 sec | 40098.1016 | 60.022 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7594.05 | -31.0191 | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016 | [12 empty] | T-64 sec | 40098.1016
T-62 sec | 40098.1016 | 60.017 | 633 |  |  |  | -23.9676 | -23.9676 | [15 empty] | 0 |  |  | T-62 sec | [10 empty] | T-62 sec | 40098.1016 | 60.017 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7594.38 | -23.9676 | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016 | [12 empty] | T-62 sec | 40098.1016
T-60 sec | 40098.1016 | 60.019 | 633 |  |  |  | -26.7914 | -26.7914 |  | 0.97244 | 633 | [12 empty] | 0 |  |  | T-60 sec | [10 empty] | T-60 sec | 40098.1016 | 60.019 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7594.71 | -26.7914 | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016 | [12 empty] | T-60 sec | 40098.1016
T-58 sec | 40098.1017 | 60.019 | 633 |  |  |  | -26.7914 | -26.7914 |  | 0.97244 | 633.9724 | [12 empty] | 0 |  |  | T-58 sec | [10 empty] | T-58 sec | 40098.1017 | 60.019 | 633 | 0 | 253.6319 | 0 | 0 | 0 | 0 | -420 | 7594.71 | -26.7914 | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017 | [12 empty] | T-58 sec | 40098.1017
T-56 sec | 40098.1017 | 60.019 | 633 |  |  |  | -26.7914 | -26.7914 |  | 0.97244 | 634.9449 | [12 empty] | 0 |  |  | T-56 sec | [10 empty] | T-56 sec | 40098.1017 | 60.019 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7595.04 | -26.7914 | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017 | [12 empty] | T-56 sec | 40098.1017
T-54 sec | 40098.1017 | 60.021 | 633 |  |  |  | -29.6099 | -29.6099 |  | 0.97244 | 633.0989 | [12 empty] | 0 |  |  | T-54 sec | [10 empty] | T-54 sec | 40098.1017 | 60.021 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7595.37 | -29.6099 | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017 | [12 empty] | T-54 sec | 40098.1017
T-52 sec | 40098.1017 | 60.021 | 633 |  |  |  | -29.6099 | -29.6099 |  | 0.97244 | 634.0713 | [12 empty] | 0 |  |  | T-52 sec | [10 empty] | T-52 sec | 40098.1017 | 60.021 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7595.37 | -29.6099 | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017 | [12 empty] | T-52 sec | 40098.1017
T-50 sec | 40098.1017 | 60.021 | 633 |  |  |  | -29.6099 | -29.6099 |  | 0.97244 | 635.0437 | [12 empty] | 0 |  |  | T-50 sec | [10 empty] | T-50 sec | 40098.1017 | 60.021 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7595.7 | -29.6099 | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017 | [12 empty] | T-50 sec | 40098.1017
T-48 sec | 40098.1018 | 60.019 | 633 |  |  |  | -26.7914 | -26.7914 |  | 0.97244 | 638.8346 | [12 empty] | 0 |  |  | T-48 sec | [10 empty] | T-48 sec | 40098.1018 | 60.019 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7596.03 | -26.7914 | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018 | [12 empty] | T-48 sec | 40098.1018
T-46 sec | 40098.1018 | 60.019 | 633 |  |  |  | -26.7914 | -26.7914 |  | 0.97244 | 639.8071 | [12 empty] | 0 |  |  | T-46 sec | [10 empty] | T-46 sec | 40098.1018 | 60.019 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7596.03 | -26.7914 | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018 | [12 empty] | T-46 sec | 40098.1018
T-44 sec | 40098.1018 | 60.022 | 633 |  |  |  | -31.0191 | -31.0191 |  | 0.97244 | 636.5518 | [12 empty] | 0 |  |  | T-44 sec | [10 empty] | T-44 sec | 40098.1018 | 60.022 | 633 | 0 | 246.9573 | 0 | 0 | 0 | 0 | -420 | 7596.36 | -31.0191 | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018 | [12 empty] | T-44 sec | 40098.1018
T-42 sec | 40098.1018 | 60.031 | 633 |  |  |  | -43.7075 | -43.7075 |  | 0.97244 | 624.8358 | [12 empty] | 0 |  |  | T-42 sec | [10 empty] | T-42 sec | 40098.1018 | 60.031 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7596.69 | -43.7075 | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018 | [12 empty] | T-42 sec | 40098.1018
T-40 sec | 40098.1019 | 60.031 | 633 |  |  |  | -43.7075 | -43.7075 |  | 0.97244 | 625.8083 | [12 empty] | 0 |  |  | T-40 sec | [10 empty] | T-40 sec | 40098.1019 | 60.031 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7596.69 | -43.7075 | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019 | [12 empty] | T-40 sec | 40098.1019
T-38 sec | 40098.1019 | 60.037 | 633 |  |  |  | -52.1682 | -52.1682 |  | 0.97244 | 618.32 | [12 empty] | 0 |  |  | T-38 sec | [10 empty] | T-38 sec | 40098.1019 | 60.037 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7597.02 | -52.1682 | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019 | [12 empty] | T-38 sec | 40098.1019
T-36 sec | 40098.1019 | 60.036 | 633 |  |  |  | -50.759 | -50.759 |  | 0.97244 | 620.7016 | [12 empty] | 0 |  |  | T-36 sec | [10 empty] | T-36 sec | 40098.1019 | 60.036 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7597.35 | -50.759 | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019 | [12 empty] | T-36 sec | 40098.1019
T-34 sec | 40098.1019 | 60.036 | 633 |  |  |  | -50.759 | -50.759 |  | 0.97244 | 621.6741 | [12 empty] | 0 |  |  | T-34 sec | [10 empty] | T-34 sec | 40098.1019 | 60.036 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7597.35 | -50.759 | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019 | [12 empty] | T-34 sec | 40098.1019
T-32 sec | 40098.102 | 60.046 | 633 |  |  |  | -64.862 | -64.862 |  | 0.97244 | 608.5435 | [12 empty] | 0 |  |  | T-32 sec | [10 empty] | T-32 sec | 40098.102 | 60.046 | 633 | 0 | 254.5418 | 0 | 0 | 0 | 0 | -420 | 7597.68 | -64.862 | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102 | [12 empty] | T-32 sec | 40098.102
T-30 sec | 40098.102 | 60.048 | 633 |  |  |  | -67.6805 | -67.6805 |  | 0.97244 | 606.6975 | [12 empty] | 0 |  |  | T-30 sec | [10 empty] | T-30 sec | 40098.102 | 60.048 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7598.01 | -67.6805 | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102 | [12 empty] | T-30 sec | 40098.102
T-28 sec | 40098.102 | 60.048 | 633 |  |  |  | -67.6805 | -67.6805 |  | 0.97244 | 607.6699 | [12 empty] | 0 |  |  | T-28 sec | [10 empty] | T-28 sec | 40098.102 | 60.048 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7598.01 | -67.6805 | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102 | [12 empty] | T-28 sec | 40098.102
T-26 sec | 40098.102 | 60.043 | 633 |  |  |  | -60.629 | -60.629 |  | 0.97244 | 615.6939 | [12 empty] | 0 |  |  | T-26 sec | [10 empty] | T-26 sec | 40098.102 | 60.043 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7598.34 | -60.629 | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102 | [12 empty] | T-26 sec | 40098.102
T-24 sec | 40098.102 | 60.041 | 633 |  |  |  | -57.8105 | -57.8105 |  | 0.97244 | 619.4848 | [12 empty] | 0 |  |  | T-24 sec | [10 empty] | T-24 sec | 40098.102 | 60.041 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7598.67 | -57.8105 | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102 | [12 empty] | T-24 sec | 40098.102
T-22 sec | 40098.1021 | 60.041 | 633 |  |  |  | -57.8105 | -57.8105 |  | 0.97244 | 620.4572 | [12 empty] | 0 |  |  | T-22 sec | [10 empty] | T-22 sec | 40098.1021 | 60.041 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7598.67 | -57.8105 | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021 | [12 empty] | T-22 sec | 40098.1021
T-20 sec | 40098.1021 | 60.041 | 633 |  |  |  | -57.8105 | -57.8105 |  | 0.97244 | 621.4296 | [12 empty] | 0 |  |  | T-20 sec | [10 empty] | T-20 sec | 40098.1021 | 60.041 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7599 | -57.8105 | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021 | [12 empty] | T-20 sec | 40098.1021
T-18 sec | 40098.1021 | 60.039 | 633 |  |  |  | -54.9921 | -54.9921 |  | 0.97244 | 625.2205 | [12 empty] | 0 |  |  | T-18 sec | [10 empty] | T-18 sec | 40098.1021 | 60.039 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7599.33 | -54.9921 | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021 | [12 empty] | T-18 sec | 40098.1021
T-16 sec | 40098.1021 | 60.039 | 633 | 60.0417 | 633 |  | -54.9921 | -54.9921 |  | 0.97244 | 626.1929 | [12 empty] | 0 |  |  | T-16 sec | 60.0417 | [9 empty] | T-16 sec | 40098.1021 | 60.039 | 633 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7599.33 | -54.9921 | T-16 sec | 40098.1021 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-16 sec | 40098.1021 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-16 sec | 40098.1021 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-16 sec | 40098.1021 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-16 sec | 40098.1021 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-14 sec | 40098.1022 | 60.043 | 633 | 60.0417 | 633 |  | -60.629 | -60.629 |  | 0.97244 | 621.5285 | [12 empty] | 0 |  |  | T-14 sec | 60.0417 | [9 empty] | T-14 sec | 40098.1022 | 60.043 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7599.66 | -60.629 | T-14 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-14 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-14 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-14 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-14 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-12 sec | 40098.1022 | 60.045 | 633 | 60.0417 | 633 |  | -63.4474 | -63.4474 |  | 0.97244 | 619.6825 | [12 empty] | 0 |  |  | T-12 sec | 60.0417 | [9 empty] | T-12 sec | 40098.1022 | 60.045 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7599.99 | -63.4474 | T-12 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-12 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-12 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-12 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-12 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-10 sec | 40098.1022 | 60.045 | 633 | 60.0417 | 633 |  | -63.4474 | -63.4474 |  | 0.97244 | 620.6549 | [12 empty] | 0 |  |  | T-10 sec | 60.0417 | [9 empty] | T-10 sec | 40098.1022 | 60.045 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7599.99 | -63.4474 | T-10 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-10 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-10 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-10 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-10 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-08 sec | 40098.1022 | 60.041 | 633 | 60.0417 | 633 |  | -57.8105 | -57.8105 |  | 0.97244 | 627.2642 | [12 empty] | 0 |  |  | T-08 sec | 60.0417 | [9 empty] | T-08 sec | 40098.1022 | 60.041 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7600.32 | -57.8105 | T-08 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-08 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-08 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-08 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-08 sec | 40098.1022 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-06 sec | 40098.1023 | 60.041 | 633 | 60.0417 | 633 |  | -57.8105 | -57.8105 |  | 0.97244 | 628.2367 | [12 empty] | 0 |  |  | T-06 sec | 60.0417 | [9 empty] | T-06 sec | 40098.1023 | 60.041 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7600.65 | -57.8105 | T-06 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-06 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-06 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-06 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-06 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-04 sec | 40098.1023 | 60.041 | 633 | 60.0417 | 633 |  | -57.8105 | -57.8105 |  | 0.97244 | 629.2091 | [12 empty] | 0 |  |  | T-04 sec | 60.0417 | [9 empty] | T-04 sec | 40098.1023 | 60.041 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7600.65 | -57.8105 | T-04 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-04 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-04 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-04 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-04 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T-02 sec | 40098.1023 | 60.039 | 633 | 60.0417 | 633 |  | -54.9921 | -54.9921 |  | 0.97244 | 633 | [12 empty] | 0 |  |  | T-02 sec | 60.0417 | [9 empty] | T-02 sec | 40098.1023 | 60.039 | 633 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7600.98 | -54.9921 | T-02 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-02 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-02 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-02 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674 |  | T-02 sec | 40098.1023 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -58.8674
T+0 sec | 40098.1023 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 719.0112 |  |  |  |  | 633 | [7 empty] | 633 | -992.9519 |  | T+0 sec | [10 empty] | T+0 sec | 40098.1023 | 59.978 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7601.31 | 31.0191 | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023 | [12 empty] | T+0 sec | 40098.1023
T+02 sec | 40098.1023 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | -4.1659 | 714.8452 | 0 | 716.9282 | 691.783 | 691.783 | 633 | [7 empty] | 633 | -992.9519 |  | T+02 sec | [10 empty] | T+02 sec | 40098.1023 | 59.978 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7601.31 | 31.0191 | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023 | [12 empty] | T+02 sec | 40098.1023
T+04 sec | 40098.1024 | 59.836 | 0 |  |  |  | 231.2421 | 231.2421 |  | -4.1659 | 910.9023 | 0 | 781.5862 | 687.617 | 689.7 | 633 | [7 empty] | 633 | -307.6528 |  | T+04 sec | [10 empty] | T+04 sec | 40098.1024 | 59.836 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7570 | 231.2421 | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024 | [12 empty] | T+04 sec | 40098.1024
T+06 sec | 40098.1024 | 59.836 | 0 |  |  |  | 231.2421 | 231.2421 |  | -4.1659 | 906.7364 | 0 | 812.8738 | 683.4511 | 687.617 | 633 | [6 empty] | 0 | 633 | -307.6528 |  | T+06 sec | [10 empty] | T+06 sec | 40098.1024 | 59.836 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7570 | 231.2421 | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024 | [12 empty] | T+06 sec | 40098.1024
T+08 sec | 40098.1024 | 59.869 | 0 |  |  |  | 184.7107 | 184.7107 |  | -4.1659 | 856.0391 | 0 | 821.5069 | 679.2852 | 685.5341 | 633 | [6 empty] | 0 | 633 | -366.4245 |  | T+08 sec | [10 empty] | T+08 sec | 40098.1024 | 59.869 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7569 | 184.7107 | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024 | [12 empty] | T+08 sec | 40098.1024
T+10 sec | 40098.1024 | 59.891 | 0 |  |  |  | 153.6916 | 153.6916 |  | -4.1659 | 820.8541 | 0 | 821.3981 | 675.1193 | 683.4511 | 633 | [6 empty] | 0 | 633 | -419.8974 |  | T+10 sec | [10 empty] | T+10 sec | 40098.1024 | 59.891 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7570 | 153.6916 | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024 | [12 empty] | T+10 sec | 40098.1024
T+12 sec | 40098.1025 | 59.891 | 0 |  |  |  | 153.6916 | 153.6916 |  | -4.1659 | 816.6882 | 0 | 820.7252 | 670.9534 | 681.3682 | 633 | [6 empty] | 0 | 633 | -419.8974 |  | T+12 sec | 59.8823 | -397.4363 | [8 empty] | T+12 sec | 40098.1025 | 59.891 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7570 | 153.6916 | T+12 sec | 40098.1025 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025 | [12 empty] | T+12 sec | 40098.1025
T+14 sec | 40098.1025 | 59.88 | 0 |  |  |  | 169.1985 | 169.1985 |  | -4.1659 | 828.0292 | 0 | 821.6382 | 666.7875 | 679.2852 | 633 | [6 empty] | 0 | 633 | -391.3474 |  | T+14 sec | 59.8823 | -397.4363 | [8 empty] | T+14 sec | 40098.1025 | 59.88 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7570 | 169.1985 | T+14 sec | 40098.1025 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025 | [12 empty] | T+14 sec | 40098.1025
T+16 sec | 40098.1025 | 59.875 | 0 |  |  |  | 176.25 | 176.25 |  | -4.1659 | 830.9148 | 0 | 822.6689 | 662.6216 | 677.2023 | 633 | [6 empty] | 0 | 633 | -379.6103 |  | T+16 sec | 59.8823 | -397.4363 | [8 empty] | T+16 sec | 40098.1025 | 59.875 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 176.25 | T+16 sec | 40098.1025 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025 | [12 empty] | T+16 sec | 40098.1025
T+18 sec | 40098.1025 | 59.875 | 0 |  |  |  | 176.25 | 176.25 |  | -4.1659 | 826.7488 | 0 | 823.0769 | 658.4556 | 675.1193 | 633 | [6 empty] | 0 | 633 | -379.6103 |  | T+18 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 |  |  | 59.8879 | -411.9588 |  |  | T+18 sec | 40098.1025 | 59.875 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 176.25 | T+18 sec | 40098.1025 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+18 sec | 40098.1025 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+18 sec | 40098.1025 | [12 empty] | T+18 sec | 40098.1025 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+18 sec | 40098.1025
T+20 sec | 40098.1026 | 59.883 | 0 | 59.8887 | 0 |  | 164.9708 | 164.9708 | 848.792 | -4.1659 | 811.3038 | 0 | 822.0066 | 654.2897 | 673.0363 | 633 | [6 empty] | 0 | 633 | -398.7388 | -413.8616 | T+20 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+20 sec | 40098.1026 | 59.883 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 164.9708 | T+20 sec | 40098.1026 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+20 sec | 40098.1026 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+20 sec | 40098.1026 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+20 sec | 40098.1026 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+20 sec | 40098.1026 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+22 sec | 40098.1026 | 59.886 | 0 | 59.8887 | 0 |  | 160.7378 | 160.7378 | 848.792 | -4.1659 | 802.9048 | 0 | 820.4148 | 650.1238 | 670.9534 | 633 | [6 empty] | 0 | 633 | -406.4248 | -413.8616 | T+22 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+22 sec | 40098.1026 | 59.886 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 160.7378 | T+22 sec | 40098.1026 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+22 sec | 40098.1026 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+22 sec | 40098.1026 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+22 sec | 40098.1026 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+22 sec | 40098.1026 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+24 sec | 40098.1026 | 59.886 | 0 | 59.8887 | 0 |  | 160.7378 | 160.7378 | 848.792 | -4.1659 | 798.7389 | 0 | 818.7474 | 645.9579 | 668.8704 | 633 | [6 empty] | 0 | 633 | -406.4248 | -413.8616 | T+24 sec | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+24 sec | 40098.1026 | 59.886 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 160.7378 | T+24 sec | 40098.1026 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | -420 | 7570 | 165.9766 | 902.3 | T+24 sec | 40098.1026 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+24 sec | 40098.1026 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+24 sec | 40098.1026 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+24 sec | 40098.1026 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+26 sec | 40098.1026 | 59.885 | 0 | 59.8887 | 0 |  | 162.1524 | 162.1524 | 848.792 | -4.1659 | 795.9876 | 0 | 817.1217 | 641.792 | 666.7875 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+26 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+26 sec | 40098.1026 | 59.885 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.1524 | T+26 sec | 40098.1026 | [12 empty] | T+26 sec | 40098.1026 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+26 sec | 40098.1026 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+26 sec | 40098.1026 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+26 sec | 40098.1026 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+28 sec | 40098.1027 | 59.888 | 0 | 59.8887 | 0 |  | 157.9193 | 157.9193 | 848.792 | -4.1659 | 787.5886 | 0 | 815.1529 | 637.6261 | 664.7045 | 633 | [6 empty] | 0 | 633 | -411.7087 | -413.8616 | T+28 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+28 sec | 40098.1027 | 59.888 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9193 | T+28 sec | 40098.1027 | [12 empty] | T+28 sec | 40098.1027 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+28 sec | 40098.1027 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+28 sec | 40098.1027 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+28 sec | 40098.1027 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+30 sec | 40098.1027 | 59.888 | 0 | 59.8887 | 0 |  | 157.9193 | 157.9193 | 848.792 | -4.1659 | 783.4227 | 0 | 813.1697 | 633.4602 | 662.6216 | 633 | [6 empty] | 0 | 633 | -411.7087 | -413.8616 | T+30 sec |  |  | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+30 sec | 40098.1027 | 59.888 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9193 | T+30 sec | 40098.1027 | [12 empty] | T+30 sec | 40098.1027 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.9553 | 900.6493 | T+30 sec | 40098.1027 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+30 sec | 40098.1027 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+30 sec | 40098.1027 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+32 sec | 40098.1027 | 59.89 | 0 | 59.8887 | 0 |  | 155.1009 | 155.1009 | 848.792 | -4.1659 | 776.4383 | 0 | 811.0091 | 629.2943 | 660.5386 | 633 | [6 empty] | 0 | 633 | -417.1319 | -413.8616 | T+32 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+32 sec | 40098.1027 | 59.89 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 155.1009 | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | [12 empty] | T+32 sec | 40098.1027 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+32 sec | 40098.1027 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+32 sec | 40098.1027 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+34 sec | 40098.1027 | 59.894 | 0 | 59.8887 | 0 |  | 149.4586 | 149.4586 | 848.792 | -4.1659 | 766.6301 | 0 | 808.5436 | 625.1283 | 658.4556 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+34 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+34 sec | 40098.1027 | 59.894 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 149.4586 | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | [12 empty] | T+34 sec | 40098.1027 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+34 sec | 40098.1027 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+34 sec | 40098.1027 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+36 sec | 40098.1027 | 59.894 | 0 | 59.8887 | 0 |  | 149.4586 | 149.4586 | 848.792 | -4.1659 | 762.4642 | 0 | 806.1183 | 620.9624 | 656.3727 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+36 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+36 sec | 40098.1027 | 59.894 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 149.4586 | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | [12 empty] | T+36 sec | 40098.1027 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+36 sec | 40098.1027 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+36 sec | 40098.1027 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+38 sec | 40098.1028 | 59.893 | 0 | 59.8887 | 0 |  | 150.8678 | 150.8678 | 848.792 | -4.1659 | 759.7075 | 0 | 803.7978 | 616.7965 | 654.2897 | 633 | [6 empty] | 0 | 633 | -425.5508 | -413.8616 | T+38 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+38 sec | 40098.1028 | 59.893 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 150.8678 | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | [12 empty] | T+38 sec | 40098.1028 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+38 sec | 40098.1028 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+38 sec | 40098.1028 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+40 sec | 40098.1028 | 59.894 | 0 | 59.8887 | 0 |  | 149.4586 | 149.4586 | 848.792 | -4.1659 | 754.1324 | 0 | 801.4328 | 612.6306 | 652.2068 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+40 sec |  |  |  |  | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+40 sec | 40098.1028 | 59.894 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 149.4586 | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | [12 empty] | T+40 sec | 40098.1028 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.2529 | 895.3516 | T+40 sec | 40098.1028 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+40 sec | 40098.1028 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+42 sec | 40098.1028 | 59.894 | 0 | 59.8887 | 0 |  | 149.4586 | 149.4586 | 848.792 | -4.1659 | 749.9665 | 0 | 799.0934 | 608.4647 | 650.1238 | 633 | [6 empty] | 0 | 633 | -428.4294 | -413.8616 | T+42 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+42 sec | 40098.1028 | 59.894 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 149.4586 | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | [12 empty] | T+42 sec | 40098.1028 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+42 sec | 40098.1028 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+44 sec | 40098.1028 | 59.891 | 0 | 59.8887 | 0 |  | 153.6916 | 153.6916 | 848.792 | -4.1659 | 750.0336 | 0 | 796.9604 | 604.2988 | 648.0409 | 633 | [6 empty] | 0 | 633 | -419.8974 | -413.8616 | T+44 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+44 sec | 40098.1028 | 59.891 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7570 | 153.6916 | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | [12 empty] | T+44 sec | 40098.1028 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+44 sec | 40098.1028 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+46 sec | 40098.1029 | 59.885 | 0 | 59.8887 | 0 |  | 162.1524 | 162.1524 | 848.792 | -4.1659 | 754.3284 | 0 | 795.184 | 600.1329 | 645.9579 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+46 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+46 sec | 40098.1029 | 59.885 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.1524 | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | [12 empty] | T+46 sec | 40098.1029 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+46 sec | 40098.1029 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+48 sec | 40098.1029 | 59.885 | 0 | 59.8887 | 0 |  | 162.1524 | 162.1524 | 848.792 | -4.1659 | 750.1625 | 0 | 793.3832 | 595.967 | 643.875 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+48 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+48 sec | 40098.1029 | 59.885 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.1524 | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | [12 empty] | T+48 sec | 40098.1029 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+48 sec | 40098.1029 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+50 sec | 40098.1029 | 59.885 | 0 | 59.8887 | 0 |  | 162.1524 | 162.1524 | 848.792 | -4.1659 | 745.9966 | 0 | 791.5606 | 591.801 | 641.792 | 633 | [6 empty] | 0 | 633 | -403.8235 | -413.8616 | T+50 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+50 sec | 40098.1029 | 59.885 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 162.1524 | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | [12 empty] | T+50 sec | 40098.1029 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+50 sec | 40098.1029 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+52 sec | 40098.1029 | 59.887 | 0 | 59.8887 | 0 |  | 159.3285 | 159.3285 | 848.792 | -4.1659 | 739.0069 | 0 | 789.6142 | 587.6351 | 639.709 | 633 | [6 empty] | 0 | 633 | -409.0497 | -413.8616 | T+52 sec | [6 empty] | 59.8879 | -411.9588 | 59.8887 | -413.8616 | T+52 sec | 40098.1029 | 59.887 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 159.3285 | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | [12 empty] | T+52 sec | 40098.1029 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9982 | 897.0977 | T+52 sec | 40098.1029 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.9246 | 896.1068
T+54 sec | 40098.103 | 59.887 | 0 |  |  |  | 159.3285 | 159.3285 |  | -4.1659 | 734.8409 | 0 | 787.658 | 583.4692 | 637.6261 | 633 | [6 empty] | 0 | 633 | -409.0497 |  | T+54 sec | [10 empty] | T+54 sec | 40098.103 | 59.887 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 159.3285 | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103 | [12 empty] | T+54 sec | 40098.103
T+56 sec | 40098.103 | 59.888 | 0 |  |  |  | 157.9193 | 157.9193 |  | -4.1659 | 729.2658 | 0 | 785.6445 | 579.3033 | 635.5431 | 633 | [6 empty] | 0 | 633 | -411.7087 |  | T+56 sec | [10 empty] | T+56 sec | 40098.103 | 59.888 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 157.9193 | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103 | [12 empty] | T+56 sec | 40098.103
T+58 sec | 40098.103 | 59.89 | 0 |  |  |  | 155.1009 | 155.1009 |  | -4.1659 | 722.2814 | 0 | 783.5324 | 575.1374 | 633.4602 | 633 | [6 empty] | 0 | 633 | -417.1319 |  | T+58 sec | [10 empty] | T+58 sec | 40098.103 | 59.89 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 155.1009 | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103 | [12 empty] | T+58 sec | 40098.103
T+60 sec | 40098.103 | 59.89 | 0 |  |  |  | 155.1009 | 155.1009 |  | -4.1659 | 718.1155 | 0 | 781.4221 | 570.9715 | 631.3772 | 633 | [6 empty] | 0 | 633 | -417.1319 |  | T+60 sec | [10 empty] | T+60 sec | 40098.103 | 59.89 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7570 | 155.1009 | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103 | [12 empty] | T+60 sec | 40098.103
T+62 sec | 40098.103 | 59.889 | 0 |  |  |  | 156.5101 | 156.5101 |  | -4.1659 | 715.3588 | 0 | 779.3577 | 566.8056 | 629.2943 | 633 | [6 empty] | 0 | 633 | -414.4026 |  | T+62 sec | [10 empty] | T+62 sec | 40098.103 | 59.889 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7570 | 156.5101 | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103 | [12 empty] | T+62 sec | 40098.103
T+64 sec | 40098.1031 | 59.873 | 0 |  |  |  | 179.0685 | 179.0685 |  | -4.1659 | 733.7513 | 0 | 777.9757 | 562.6396 | 627.2113 | 633 | [6 empty] | 0 | 633 | -375.1137 |  | T+64 sec | [10 empty] | T+64 sec | 40098.1031 | 59.873 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7568 | 179.0685 | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031 | [12 empty] | T+64 sec | 40098.1031
T+66 sec | 40098.1031 | 59.873 | 0 |  |  |  | 179.0685 | 179.0685 |  | -4.1659 | 729.5854 | 0 | 776.5524 | 558.4737 | 625.1283 | 633 | [6 empty] | 0 | 633 | -375.1137 |  | T+66 sec | [10 empty] | T+66 sec | 40098.1031 | 59.873 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7568 | 179.0685 | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031 | [12 empty] | T+66 sec | 40098.1031
T+68 sec | 40098.1031 | 59.857 | 0 |  |  |  | 201.6322 | 201.6322 |  | -4.1659 | 747.9832 | 0 | 775.7361 | 554.3078 | 623.0454 | 633 | [6 empty] | 0 | 633 | -342.6224 |  | T+68 sec | [10 empty] | T+68 sec | 40098.1031 | 59.857 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7565 | 201.6322 | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031 | [12 empty] | T+68 sec | 40098.1031
T+70 sec | 40098.1031 | 59.852 | 0 |  |  |  | 208.6783 | 208.6783 |  | -4.1659 | 750.8634 | 0 | 775.0452 | 550.1419 | 620.9624 | 633 | [6 empty] | 0 | 633 | -333.599 |  | T+70 sec | [10 empty] | T+70 sec | 40098.1031 | 59.852 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7560 | 208.6783 | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031 | [12 empty] | T+70 sec | 40098.1031
T+72 sec | 40098.1032 | 59.852 | 0 |  |  |  | 208.6783 | 208.6783 |  | -4.1659 | 746.6975 | 0 | 774.2791 | 545.976 | 618.8795 | 633 | [6 empty] | 0 | 633 | -333.599 |  | T+72 sec | [10 empty] | T+72 sec | 40098.1032 | 59.852 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7560 | 208.6783 | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032 | [12 empty] | T+72 sec | 40098.1032
T+74 sec | 40098.1032 | 59.858 | 0 |  |  |  | 200.2176 | 200.2176 |  | -4.1659 | 734.0709 | 0 | 773.221 | 541.8101 | 616.7965 | 633 | [6 empty] | 0 | 633 | -344.4931 |  | T+74 sec | [10 empty] | T+74 sec | 40098.1032 | 59.858 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7563 | 200.2176 | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032 | [12 empty] | T+74 sec | 40098.1032
T+76 sec | 40098.1032 | 59.866 | 0 |  |  |  | 188.9384 | 188.9384 |  | -4.1659 | 718.6258 | 0 | 771.8211 | 537.6442 | 614.7136 | 633 | [6 empty] | 0 | 633 | -360.1731 |  | T+76 sec | [10 empty] | T+76 sec | 40098.1032 | 59.866 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7564 | 188.9384 | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032 | [12 empty] | T+76 sec | 40098.1032
T+78 sec | 40098.1032 | 59.866 | 0 |  |  |  | 188.9384 | 188.9384 |  | -4.1659 | 714.4599 | 0 | 770.3871 | 533.4783 | 612.6306 | 633 | [6 empty] | 0 | 633 | -360.1731 |  | T+78 sec | [10 empty] | T+78 sec | 40098.1032 | 59.866 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7564 | 188.9384 | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032 | [12 empty] | T+78 sec | 40098.1032
T+80 sec | 40098.1033 | 59.865 | 0 |  |  |  | 190.3476 | 190.3476 |  | -4.1659 | 711.7032 | 0 | 768.9558 | 529.3123 | 610.5476 | 633 | [6 empty] | 0 | 633 | -358.1364 |  | T+80 sec | [10 empty] | T+80 sec | 40098.1033 | 59.865 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7566 | 190.3476 | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033 | [12 empty] | T+80 sec | 40098.1033
| 40098.1033 | 59.866 | 0 |  |  |  | 188.9384 | 188.9384 |  | -4.1659 | 706.128 | 0 | 767.4599 | 525.1464 | 608.4647 | 633 | [6 empty] | 0 | 633 | -360.1731 | [13 empty] | 40098.1033 | 59.866 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7570 | 188.9384
| 40098.1033 | 59.866 | 0 |  |  |  | 188.9384 | 188.9384 |  | -4.1659 | 701.9621 | 0 | 765.9367 | 520.9805 | 606.3817 | 633 | [6 empty] | 0 | 633 | -360.1731 | [13 empty] | 40098.1033 | 59.866 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7570 | 188.9384
| 40098.1033 | 59.871 | 0 |  |  |  | 181.8923 | 181.8923 |  | -4.1659 | 690.7501 | 0 | 764.2279 | 516.8146 | 604.2988 | 633 | [6 empty] | 0 | 633 | -370.714 | [13 empty] | 40098.1033 | 59.871 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7570 | 181.8923
| 40098.1033 | 59.879 | 0 |  |  |  | 170.6077 | 170.6077 |  | -4.1659 | 675.2996 | 0 | 762.2517 | 512.6487 | 602.2158 | 633 | [6 empty] | 0 | 633 | -388.9441 | [13 empty] | 40098.1033 | 59.879 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7570 | 170.6077
| 40098.1034 | 59.879 | 0 |  |  |  | 170.6077 | 170.6077 |  | -4.1659 | 671.1337 | 0 | 760.2709 | 508.4828 | 600.1329 | 633 | [6 empty] | 0 | 633 | -388.9441 | [13 empty] | 40098.1034 | 59.879 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7570 | 170.6077
| 40098.1034 | 59.88 | 0 |  |  |  | 169.1985 | 169.1985 |  | -4.1659 | 665.5586 | 0 | 758.2557 | 504.3169 | 598.0499 | 633 | [6 empty] | 0 | 633 | -391.3474 | [13 empty] | 40098.1034 | 59.88 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7570 | 169.1985
| 40098.1034 | 59.886 | 0 |  |  |  | 160.7378 | 160.7378 |  | -4.1659 | 652.9319 | 0 | 756.0615 | 500.151 | 595.967 | 633 | [6 empty] | 0 | 633 | -406.4248 | [13 empty] | 40098.1034 | 59.886 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7570 | 160.7378
| 40098.1034 | 59.886 | 0 |  |  |  | 160.7378 | 160.7378 |  | -4.1659 | 648.766 | 0 | 753.8718 | 495.985 | 593.884 | 633 | [6 empty] | 0 | 633 | -406.4248 | [13 empty] | 40098.1034 | 59.886 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7570 | 160.7378
| 40098.1035 | 59.89 | 0 |  |  |  | 155.1009 | 155.1009 |  | -4.1659 | 638.9632 | 0 | 751.5736 | 491.8191 | 591.801 | 633 | [6 empty] | 0 | 633 | -417.1319 | [13 empty] | 40098.1035 | 59.89 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7569 | 155.1009
| 40098.1035 | 59.889 | 0 |  |  |  | 156.5101 | 156.5101 |  | -4.1659 | 636.2065 | 0 | 749.3115 | 487.6532 | 589.7181 | 633 | [6 empty] | 0 | 633 | -414.4026 | [13 empty] | 40098.1035 | 59.889 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7575 | 156.5101
| 40098.1035 | 59.889 | 0 |  |  |  | 156.5101 | 156.5101 |  | -4.1659 | 632.0406 | 0 | 747.0563 | 483.4873 | 587.6351 | 633 | [6 empty] | 0 | 633 | -414.4026 | [13 empty] | 40098.1035 | 59.889 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7575 | 156.5101
| 40098.1035 | 59.893 | 0 |  |  |  | 150.8678 | 150.8678 |  | -4.1659 | 622.2324 | 0 | 744.7011 | 479.3214 | 585.5522 | 633 | [6 empty] | 0 | 633 | -425.5508 | [13 empty] | 40098.1035 | 59.893 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7573 | 150.8678
| 40098.1036 | 59.903 | 0 |  |  |  | 136.7702 | 136.7702 |  | -4.1659 | 603.9688 | 0 | 742.095 | 475.1555 | 583.4692 | 633 | [6 empty] | 0 | 633 | -456.216 | [13 empty] | 40098.1036 | 59.903 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7571 | 136.7702
| 40098.1036 | 59.903 | 0 |  |  |  | 136.7702 | 136.7702 |  | -4.1659 | 599.8029 | 0 | 739.5078 | 470.9896 | 581.3863 | 633 | [6 empty] | 0 | 633 | -456.216 | [13 empty] | 40098.1036 | 59.903 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7571 | 136.7702
| 40098.1036 | 59.902 | 0 |  |  |  | 138.1794 | 138.1794 |  | -4.1659 | 597.0462 | 0 | 736.9639 | 466.8236 | 579.3033 | 633 | [6 empty] | 0 | 633 | -452.9532 | [13 empty] | 40098.1036 | 59.902 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7573 | 138.1794
| 40098.1036 | 59.904 | 0 |  |  |  | 135.3609 | 135.3609 |  | -4.1659 | 590.0619 | 0 | 734.3866 | 462.6577 | 577.2203 | 633 | [6 empty] | 0 | 633 | -459.526 | [13 empty] | 40098.1036 | 59.904 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7575 | 135.3609
| 40098.1036 | 59.904 | 0 |  |  |  | 135.3609 | 135.3609 |  | -4.1659 | 585.896 | 0 | 731.8265 | 458.4918 | 575.1374 | 633 | [6 empty] | 0 | 633 | -459.526 | [13 empty] | 40098.1036 | 59.904 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7575 | 135.3609
| 40098.1037 | 59.907 | 0 |  |  |  | 131.1279 | 131.1279 |  | -4.1659 | 577.497 | 0 | 729.2107 | 454.3259 | 573.0544 | 633 | [6 empty] | 0 | 633 | -469.7642 | [13 empty] | 40098.1037 | 59.907 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7577 | 131.1279
| 40098.1037 | 59.916 | 0 |  |  |  | 118.4395 | 118.4395 |  | -4.1659 | 560.6427 | 0 | 726.4012 | 450.16 | 570.9715 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7577 | 118.4395
| 40098.1037 | 59.916 | 0 |  |  |  | 118.4395 | 118.4395 |  | -4.1659 | 556.4768 | 0 | 723.6156 | 445.9941 | 568.8885 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7577 | 118.4395
| 40098.1037 | 59.916 | 0 |  |  |  | 118.4395 | 118.4395 |  | -4.1659 | 552.3109 | 0 | 720.8526 | 441.8282 | 566.8056 | 633 | [6 empty] | 0 | 633 | -503.3814 | [13 empty] | 40098.1037 | 59.916 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7578 | 118.4395
| 40098.1038 | 59.918 | 0 |  |  |  | 115.621 | 115.621 |  | -4.1659 | 545.3265 | 0 | 718.0665 | 437.6623 | 564.7226 | 633 | [6 empty] | 0 | 633 | -511.5123 | [13 empty] | 40098.1038 | 59.918 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7579 | 115.621
| 40098.1038 | 59.918 | 0 |  |  |  | 115.621 | 115.621 |  | -4.1659 | 541.1606 | 0 | 715.3023 | 433.4963 | 562.6396 | 633 | [6 empty] | 0 | 633 | -511.5123 | [13 empty] | 40098.1038 | 59.918 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7579 | 115.621
| 40098.1038 | 59.92 | 0 |  |  |  | 112.8026 | 112.8026 |  | -4.1659 | 534.1762 | 0 | 712.5158 | 429.3304 | 560.5567 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1038 | 59.92 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7580 | 112.8026
| 40098.1038 | 59.92 | 0 |  |  |  | 112.8026 | 112.8026 |  | -4.1659 | 530.0103 | 0 | 709.7505 | 425.1645 | 558.4737 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1038 | 59.92 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7581 | 112.8026
| 40098.1039 | 59.92 | 0 |  |  |  | 112.8026 | 112.8026 |  | -4.1659 | 525.8444 | 0 | 707.0057 | 420.9986 | 556.3908 | 633 | [6 empty] | 0 | 633 | -519.9102 | [13 empty] | 40098.1039 | 59.92 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7581 | 112.8026
| 40098.1039 | 59.917 | 0 |  |  |  | 117.0303 | 117.0303 |  | -4.1659 | 525.9061 | 0 | 704.3424 | 416.8327 | 554.3078 | 633 | [6 empty] | 0 | 633 | -507.4143 | [13 empty] | 40098.1039 | 59.917 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7585 | 117.0303
| 40098.1039 | 59.921 | 0 |  |  |  | 111.388 | 111.388 |  | -4.1659 | 516.098 | 0 | 701.6143 | 412.6668 | 552.2249 | 633 | [6 empty] | 0 | 633 | -524.23 | [13 empty] | 40098.1039 | 59.921 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7588 | 111.388
| 40098.1039 | 59.921 | 0 |  |  |  | 111.388 | 111.388 |  | -4.1659 | 511.932 | 0 | 698.9045 | 408.5009 | 550.1419 | 633 | [6 empty] | 0 | 633 | -524.23 | [13 empty] | 40098.1039 | 59.921 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7588 | 111.388
| 40098.1039 | 59.923 | 0 |  |  |  | 108.5695 | 108.5695 |  | -4.1659 | 504.9477 | 0 | 696.1727 | 404.335 | 548.059 | 633 | [6 empty] | 0 | 633 | -533.0543 | [13 empty] | 40098.1039 | 59.923 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7589 | 108.5695
| 40098.104 | 59.925 | 0 |  |  |  | 105.7511 | 105.7511 |  | -4.1659 | 497.9633 | 0 | 693.4198 | 400.169 | 545.976 | 633 | [6 empty] | 0 | 633 | -542.1808 | [13 empty] | 40098.104 | 59.925 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7589 | 105.7511
| 40098.104 | 59.925 | 0 |  |  |  | 105.7511 | 105.7511 |  | -4.1659 | 493.7974 | 0 | 690.6853 | 396.0031 | 543.893 | 633 | [6 empty] | 0 | 633 | -542.1808 | [13 empty] | 40098.104 | 59.925 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7589 | 105.7511
| 40098.104 | 59.928 | 0 |  |  |  | 101.518 | 101.518 |  | -4.1659 | 485.3984 | 0 | 687.9111 | 391.8372 | 541.8101 | 633 | [6 empty] | 0 | 633 | -556.4906 | [13 empty] | 40098.104 | 59.928 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7590 | 101.518
| 40098.104 | 59.932 | 0 |  |  |  | 95.8811 | 95.8811 |  | -4.1659 | 475.5956 | 0 | 685.0802 | 387.6713 | 539.7271 | 633 | [6 empty] | 0 | 633 | -576.7614 | [13 empty] | 40098.104 | 59.932 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7590 | 95.8811
| 40098.1041 | 59.932 | 0 |  |  |  | 95.8811 | 95.8811 |  | -4.1659 | 471.4297 | 0 | 682.2691 | 383.5054 | 537.6442 | 633 | [6 empty] | 0 | 633 | -576.7614 | [13 empty] | 40098.1041 | 59.932 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7590 | 95.8811
| 40098.1041 | 59.927 | 0 |  |  |  | 102.9326 | 102.9326 |  | -4.1659 | 474.3153 | 0 | 679.5684 | 379.3395 | 535.5612 | 633 | [6 empty] | 0 | 633 | -551.6253 | [13 empty] | 40098.1041 | 59.927 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7590 | 102.9326
| 40098.1041 | 59.931 | 0 |  |  |  | 97.2903 | 97.2903 |  | -4.1659 | 464.5071 | 0 | 676.8112 | 375.1736 | 533.4783 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1041 | 59.931 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7591 | 97.2903
| 40098.1041 | 59.931 | 0 |  |  |  | 97.2903 | 97.2903 |  | -4.1659 | 460.3412 | 0 | 674.071 | 371.0076 | 531.3953 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1041 | 59.931 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7591 | 97.2903
| 40098.1042 | 59.929 | 0 |  |  |  | 100.1088 | 100.1088 |  | -4.1659 | 458.9937 | 0 | 671.3826 | 366.8417 | 529.3123 | 633 | [6 empty] | 0 | 633 | -561.4236 | [13 empty] | 40098.1042 | 59.929 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7591 | 100.1088
| 40098.1042 | 59.931 | 0 |  |  |  | 97.2903 | 97.2903 |  | -4.1659 | 452.0094 | 0 | 668.6743 | 362.6758 | 527.2294 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1042 | 59.931 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7591 | 97.2903
| 40098.1042 | 59.931 | 0 |  |  |  | 97.2903 | 97.2903 |  | -4.1659 | 447.8435 | 0 | 665.9812 | 358.5099 | 525.1464 | 633 | [6 empty] | 0 | 633 | -571.5565 | [13 empty] | 40098.1042 | 59.931 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7591 | 97.2903
| 40098.1042 | 59.937 | 0 |  |  |  | 88.8296 | 88.8296 |  | -4.1659 | 435.2168 | 0 | 663.2009 | 354.344 | 523.0635 | 633 | [6 empty] | 0 | 633 | -604.2978 | [13 empty] | 40098.1042 | 59.937 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7592 | 88.8296
| 40098.1042 | 59.945 | 0 |  |  |  | 77.5504 | 77.5504 |  | -4.1659 | 419.7717 | 0 | 660.3029 | 350.1781 | 520.9805 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1042 | 59.945 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7592 | 77.5504
| 40098.1043 | 59.945 | 0 |  |  |  | 77.5504 | 77.5504 |  | -4.1659 | 415.6058 | 0 | 657.4241 | 346.0122 | 518.8976 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1043 | 59.945 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7592 | 77.5504
| 40098.1043 | 59.949 | 0 |  |  |  | 71.9081 | 71.9081 |  | -4.1659 | 405.7976 | 0 | 654.4983 | 341.8463 | 516.8146 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1043 | 59.949 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7593 | 71.9081
| 40098.1043 | 59.942 | 0 |  |  |  | 81.7781 | 81.7781 |  | -4.1659 | 411.5016 | 0 | 651.7052 | 337.6803 | 514.7316 | 633 | [6 empty] | 0 | 633 | -634.5953 | [13 empty] | 40098.1043 | 59.942 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7594 | 81.7781
| 40098.1043 | 59.942 | 0 |  |  |  | 81.7781 | 81.7781 |  | -4.1659 | 407.3357 | 0 | 648.9283 | 333.5144 | 512.6487 | 633 | [6 empty] | 0 | 633 | -634.5953 | [13 empty] | 40098.1043 | 59.942 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7594 | 81.7781
| 40098.1044 | 59.941 | 0 |  |  |  | 83.1873 | 83.1873 |  | -4.1659 | 404.579 | 0 | 646.1828 | 329.3485 | 510.5657 | 633 | [6 empty] | 0 | 633 | -628.2999 | [13 empty] | 40098.1044 | 59.941 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7595 | 83.1873
| 40098.1044 | 59.945 | 0 |  |  |  | 77.5504 | 77.5504 |  | -4.1659 | 394.7762 | 0 | 643.3894 | 325.1826 | 508.4828 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1044 | 59.945 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7655 | 77.5504
| 40098.1044 | 59.945 | 0 |  |  |  | 77.5504 | 77.5504 |  | -4.1659 | 390.6103 | 0 | 640.6116 | 321.0167 | 506.3998 | 633 | [6 empty] | 0 | 633 | -654.2618 | [13 empty] | 40098.1044 | 59.945 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7655 | 77.5504
| 40098.1044 | 59.948 | 0 |  |  |  | 73.3174 | 73.3174 |  | -4.1659 | 382.2114 | 0 | 637.8029 | 316.8508 | 504.3169 | 633 | [6 empty] | 0 | 633 | -675.2137 | [13 empty] | 40098.1044 | 59.948 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 73.3174
| 40098.1045 | 59.949 | 0 |  |  |  | 71.9081 | 71.9081 |  | -4.1659 | 376.6362 | 0 | 634.9946 | 312.6849 | 502.2339 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1045 | 59.949 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 71.9081
| 40098.1045 | 59.949 | 0 |  |  |  | 71.9081 | 71.9081 |  | -4.1659 | 372.4703 | 0 | 632.2018 | 308.5189 | 500.151 | 633 | [6 empty] | 0 | 633 | -682.4898 | [13 empty] | 40098.1045 | 59.949 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 71.9081
| 40098.1045 | 59.951 | 0 |  |  |  | 69.0897 | 69.0897 |  | -4.1659 | 365.4859 | 0 | 629.3943 | 304.353 | 498.068 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1045 | 59.951 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 69.0897
| 40098.1045 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | -4.1659 | 358.5016 | 0 | 626.5725 | 300.1871 | 495.985 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1045 | 59.953 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 66.2712
| 40098.1045 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | -4.1659 | 354.3357 | 0 | 623.7659 | 296.0212 | 493.9021 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1045 | 59.953 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 66.2712
| 40098.1046 | 59.951 | 0 |  |  |  | 69.0897 | 69.0897 |  | -4.1659 | 352.9882 | 0 | 621.0029 | 291.8553 | 491.8191 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1046 | 59.951 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7658 | 69.0897
| 40098.1046 | 59.952 | 0 |  |  |  | 67.6805 | 67.6805 |  | -4.1659 | 347.4131 | 0 | 618.2393 | 287.6894 | 489.7362 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7658 | 67.6805
| 40098.1046 | 59.952 | 0 |  |  |  | 67.6805 | 67.6805 |  | -4.1659 | 343.2471 | 0 | 615.4894 | 283.5235 | 487.6532 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7658 | 67.6805
| 40098.1046 | 59.952 | 0 |  |  |  | 67.6805 | 67.6805 |  | -4.1659 | 339.0812 | 0 | 612.7527 | 279.3576 | 485.5703 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1046 | 59.952 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7659 | 67.6805
| 40098.1047 | 59.952 | 0 |  |  |  | 67.6805 | 67.6805 |  | -4.1659 | 334.9153 | 0 | 610.0288 | 275.1916 | 483.4873 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1047 | 59.952 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7659 | 67.6805
| 40098.1047 | 59.952 | 0 |  |  |  | 67.6805 | 67.6805 |  | -4.1659 | 330.7494 | 0 | 607.3174 | 271.0257 | 481.4043 | 633 | [6 empty] | 0 | 633 | -705.2902 | [13 empty] | 40098.1047 | 59.952 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7659 | 67.6805
| 40098.1047 | 59.954 | 0 |  |  |  | 64.862 | 64.862 |  | -4.1659 | 323.765 | 0 | 604.5909 | 266.8598 | 479.3214 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1047 | 59.954 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7659 | 64.862
| 40098.1047 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | -4.1659 | 321.0084 | 0 | 601.8901 | 262.6939 | 477.2384 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1047 | 59.953 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7660 | 66.2712
| 40098.1048 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | -4.1659 | 316.8424 | 0 | 599.201 | 258.528 | 475.1555 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1048 | 59.953 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7660 | 66.2712
| 40098.1048 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | -4.1659 | 312.6765 | 0 | 596.5232 | 254.3621 | 473.0725 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1048 | 59.953 | 0 | 0 | 249.3376 | 0 | 0 | 0 | 0 | -420 | 7660 | 66.2712
| 40098.1048 | 59.954 | 0 |  |  |  | 64.862 | 64.862 |  | -4.1659 | 307.1014 | 0 | 593.8434 | 250.1962 | 470.9896 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7661 | 64.862
| 40098.1048 | 59.954 | 0 |  |  |  | 64.862 | 64.862 |  | -4.1659 | 302.9355 | 0 | 591.1745 | 246.0303 | 468.9066 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7661 | 64.862
| 40098.1048 | 59.954 | 0 |  |  |  | 64.862 | 64.862 |  | -4.1659 | 298.7696 | 0 | 588.5162 | 241.8643 | 466.8236 | 633 | [6 empty] | 0 | 633 | -721.3561 | [13 empty] | 40098.1048 | 59.954 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7661 | 64.862
| 40098.1049 | 59.957 | 0 |  |  |  | 60.629 | 60.629 |  | -4.1659 | 290.3706 | 0 | 585.8302 | 237.6984 | 464.7407 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1049 | 59.957 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7625.4 | 60.629
| 40098.1049 | 59.957 | 0 |  |  |  | 60.629 | 60.629 |  | -4.1659 | 286.2047 | 0 | 583.155 | 233.5325 | 462.6577 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1049 | 59.957 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7625.4 | 60.629
| 40098.1049 | 59.956 | 0 |  |  |  | 62.0382 | 62.0382 |  | -4.1659 | 283.448 | 0 | 580.5027 | 229.3666 | 460.5748 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1049 | 59.956 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7625.73 | 62.0382
| 40098.1049 | 59.956 | 0 |  |  |  | 62.0382 | 62.0382 |  | -4.1659 | 279.2821 | 0 | 577.8605 | 225.2007 | 458.4918 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1049 | 59.956 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7626.06 | 62.0382
| 40098.105 | 59.956 | 0 |  |  |  | 62.0382 | 62.0382 |  | -4.1659 | 275.1162 | 0 | 575.2279 | 221.0348 | 456.4089 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.105 | 59.956 | 0 | 0 | 258.2782 | 0 | 0 | 0 | 0 | -420 | 7626.06 | 62.0382
| 40098.105 | 59.955 | 0 |  |  |  | 63.4474 | 63.4474 |  | -4.1659 | 272.3595 | 0 | 572.617 | 216.8689 | 454.3259 | 633 | [6 empty] | 0 | 633 | -729.6988 | [13 empty] | 40098.105 | 59.955 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7626.39 | 63.4474
| 40098.105 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | -4.1659 | 259.7382 | 0 | 569.9428 | 212.7029 | 452.243 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.105 | 59.961 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7626.72 | 54.9921
| 40098.105 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | -4.1659 | 255.5723 | 0 | 567.2786 | 208.537 | 450.16 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.105 | 59.961 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7626.72 | 54.9921
| 40098.1051 | 59.962 | 0 |  |  |  | 53.5775 | 53.5775 |  | -4.1659 | 249.9918 | 0 | 564.6124 | 204.3711 | 448.077 | 633 | [6 empty] | 0 | 633 | -793.7488 | [13 empty] | 40098.1051 | 59.962 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7627.05 | 53.5775
| 40098.1051 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | -4.1659 | 237.3705 | 0 | 561.8853 | 200.2052 | 445.9941 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1051 | 59.968 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7627.38 | 45.1221
| 40098.1051 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | -4.1659 | 233.2046 | 0 | 559.169 | 196.0393 | 443.9111 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1051 | 59.968 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7627.38 | 45.1221
| 40098.1051 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | -4.1659 | 231.8571 | 0 | 556.4861 | 191.8734 | 441.8282 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1051 | 59.966 | 0 | 0 | 258.4064 | 0 | 0 | 0 | 0 | -420 | 7627.71 | 47.9406
| 40098.1052 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | -4.1659 | 224.8728 | 0 | 553.79 | 187.7075 | 439.7452 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1052 | 59.968 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7628.04 | 45.1221
| 40098.1052 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | -4.1659 | 220.7069 | 0 | 551.1039 | 183.5416 | 437.6623 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1052 | 59.968 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7628.04 | 45.1221
| 40098.1052 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | -4.1659 | 213.7171 | 0 | 548.4048 | 179.3756 | 435.5793 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7628.37 | 42.2983
| 40098.1052 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | -4.1659 | 209.5512 | 0 | 545.7155 | 175.2097 | 433.4963 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7628.7 | 42.2983
| 40098.1052 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | -4.1659 | 205.3853 | 0 | 543.0357 | 171.0438 | 431.4134 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1052 | 59.97 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7628.7 | 42.2983
| 40098.1053 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | -4.1659 | 202.6286 | 0 | 540.3763 | 166.8779 | 429.3304 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1053 | 59.969 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7629.03 | 43.7075
| 40098.1053 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | -4.1659 | 197.0535 | 0 | 537.7149 | 162.712 | 427.2475 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1053 | 59.97 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7629.36 | 42.2983
| 40098.1053 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | -4.1659 | 192.8876 | 0 | 535.0624 | 158.5461 | 425.1645 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1053 | 59.97 | 0 | 0 | 260.5389 | 0 | 0 | 0 | 0 | -420 | 7629.36 | 42.2983
| 40098.1053 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | -4.1659 | 187.3124 | 0 | 532.4078 | 154.3802 | 423.0816 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1053 | 59.971 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7629.69 | 40.8891
| 40098.1054 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | -4.1659 | 180.3281 | 0 | 529.7405 | 150.2143 | 420.9986 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1054 | 59.973 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7630.02 | 38.0706
| 40098.1054 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | -4.1659 | 176.1621 | 0 | 527.082 | 146.0483 | 418.9156 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1054 | 59.973 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7630.02 | 38.0706
| 40098.1054 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | -4.1659 | 167.7632 | 0 | 524.4005 | 141.8824 | 416.8327 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1054 | 59.976 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7630.35 | 33.8375
| 40098.1054 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | -4.1659 | 160.7788 | 0 | 521.707 | 137.7165 | 414.7497 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1054 | 59.978 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7630.68 | 31.0191
| 40098.1055 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | -4.1659 | 156.6129 | 0 | 519.0225 | 133.5506 | 412.6668 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1055 | 59.978 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7630.68 | 31.0191
| 40098.1055 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | -4.1659 | 155.2654 | 0 | 516.3674 | 129.3847 | 410.5838 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 0 | 0 | 257.8821 | 0 | 0 | 0 | 0 | -420 | 7631.01 | 33.8375
| 40098.1055 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | -4.1659 | 151.0995 | 0 | 513.7205 | 125.2188 | 408.5009 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7631.34 | 33.8375
| 40098.1055 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | -4.1659 | 146.9336 | 0 | 511.0817 | 121.0529 | 406.4179 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1055 | 59.976 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7631.34 | 33.8375
| 40098.1055 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | -4.1659 | 139.9492 | 0 | 508.4308 | 116.8869 | 404.335 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1055 | 59.978 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7631.67 | 31.0191
| 40098.1056 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | -4.1659 | 132.9649 | 0 | 505.7679 | 112.721 | 402.252 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7632 | 28.2006
| 40098.1056 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | -4.1659 | 128.799 | 0 | 503.1132 | 108.5551 | 400.169 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7632 | 28.2006
| 40098.1056 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | -4.1659 | 121.8146 | 0 | 500.4468 | 104.3892 | 398.0861 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1056 | 59.982 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7632.33 | 25.3822
| 40098.1056 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | -4.1659 | 120.4671 | 0 | 497.808 | 100.2233 | 396.0031 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1056 | 59.98 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7632.66 | 28.2006
| 40098.1057 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | -4.1659 | 116.3012 | 0 | 495.1769 | 96.0574 | 393.9202 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1057 | 59.98 | 0 | 0 | 258.5887 | 0 | 0 | 0 | 0 | -420 | 7632.66 | 28.2006
| 40098.1057 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | -4.1659 | 113.5445 | 0 | 492.563 | 91.8915 | 391.8372 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7632.99 | 29.6099
| 40098.1057 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | -4.1659 | 109.3786 | 0 | 489.9563 | 87.7256 | 389.7543 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7633.32 | 29.6099
| 40098.1057 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | -4.1659 | 105.2127 | 0 | 487.3567 | 83.5596 | 387.6713 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1057 | 59.979 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7633.32 | 29.6099
| 40098.1058 | 59.983 | 0 |  |  |  | 23.9676 | 23.9676 |  | -4.1659 | 95.4045 | 0 | 484.7262 | 79.3937 | 385.5883 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1058 | 59.983 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7633.65 | 23.9676
| 40098.1058 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | -4.1659 | 89.8294 | 0 | 482.0935 | 75.2278 | 383.5054 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1058 | 59.984 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7633.98 | 22.5584
| 40098.1058 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | -4.1659 | 85.6635 | 0 | 479.4682 | 71.0619 | 381.4224 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1058 | 59.984 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7633.98 | 22.5584
| 40098.1058 | 59.988 | 0 |  |  |  | 16.9215 | 16.9215 |  | -4.1659 | 75.8607 | 0 | 476.8128 | 66.896 | 379.3395 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1058 | 59.988 | 0 | 0 | 261.9062 | 0 | 0 | 0 | 0 | -420 | 7634.31 | 16.9215
| 40098.1058 | 59.987 | 0 |  |  |  | 18.3307 | 18.3307 |  | -4.1659 | 73.104 | 0 | 474.1742 | 62.7301 | 377.2565 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1058 | 59.987 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7634.64 | 18.3307
| 40098.1059 | 59.987 | 0 |  |  |  | 18.3307 | 18.3307 |  | -4.1659 | 68.9381 | 0 | 471.5428 | 58.5642 | 375.1736 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1059 | 59.987 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7634.64 | 18.3307
| 40098.1059 | 59.987 | 0 |  |  |  | 18.3307 | 18.3307 |  | -4.1659 | 64.7721 | 0 | 468.9185 | 54.3983 | 373.0906 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.1059 | 59.987 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7634.97 | 18.3307
| 40098.1059 | 59.993 | 0 |  |  |  | 9.87 | 9.87 |  | -4.1659 | 52.1455 | 0 | 466.2469 | 50.2323 | 371.0076 | 633 | [6 empty] | 0 | 633 | -1298.4636 | [13 empty] | 40098.1059 | 59.993 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7635.3 | 9.87
| 40098.1059 | 59.993 | 0 |  |  |  | 9.87 | 9.87 |  | -4.1659 | 47.9796 | 0 | 463.5827 | 46.0664 | 368.9247 | 633 | [6 empty] | 0 | 633 | -1298.4636 | [13 empty] | 40098.1059 | 59.993 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7635.3 | 9.87
| 40098.106 | 59.992 | 0 |  |  |  | 11.2792 | 11.2792 |  | -4.1659 | 45.2229 | 0 | 460.9349 | 41.9005 | 366.8417 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.106 | 59.992 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7635.63 | 11.2792
| 40098.106 | 59.989 | 0 |  |  |  | 15.5122 | 15.5122 |  | -4.1659 | 45.29 | 0 | 458.3208 | 37.7346 | 364.7588 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.106 | 59.989 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7635.96 | 15.5122
| 40098.106 | 59.989 | 0 |  |  |  | 15.5122 | 15.5122 |  | -4.1659 | 41.1241 | 0 | 455.7133 | 33.5687 | 362.6758 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.106 | 59.989 | 0 | 0 | 256.7478 | 0 | 0 | 0 | 0 | -420 | 7635.96 | 15.5122
| 40098.106 | 59.986 | 0 |  |  |  | 19.7399 | 19.7399 |  | -4.1659 | 41.1859 | 0 | 453.1386 | 29.4028 | 360.5929 | 633 | [6 empty] | 0 | 633 | -1135.4282 | [13 empty] | 40098.106 | 59.986 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7636.29 | 19.7399
| 40098.1061 | 59.983 | 0 |  |  |  | 23.9676 | 23.9676 |  | -4.1659 | 41.2477 | 0 | 450.5961 | 25.2369 | 358.5099 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1061 | 59.983 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7636.62 | 23.9676
| 40098.1061 | 59.983 | 0 |  |  |  | 23.9676 | 23.9676 |  | -4.1659 | 37.0817 | 0 | 448.0592 | 21.0709 | 356.4269 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1061 | 59.983 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7636.62 | 23.9676
| 40098.1061 | 59.988 | 0 |  |  |  | 16.9215 | 16.9215 |  | -4.1659 | 25.8697 | 0 | 445.4848 | 16.905 | 354.344 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1061 | 59.988 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7636.95 | 16.9215
| 40098.1061 | 59.996 | 0 |  |  |  | 5.6423 | 5.6423 |  | -4.1659 | 10.4246 | 0 | 442.8481 | 12.7391 | 352.261 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.1061 | 59.996 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7637.28 | 5.6423
| 40098.1061 | 59.996 | 0 |  |  |  | 5.6423 | 5.6423 |  | -4.1659 | 6.2587 | 0 | 440.218 | 8.5732 | 350.1781 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.1061 | 59.996 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7637.28 | 5.6423
| 40098.1062 | 59.998 | 0 |  |  |  | 2.8185 | 2.8185 |  | -4.1659 | -0.73105 | 0 | 437.5776 | 4.4073 | 348.0951 | 633 | [6 empty] | 0 | 633 | -1446.895 | [13 empty] | 40098.1062 | 59.998 | 0 | 0 | 167.432 | 0 | 0 | 0 | 0 | -420 | 7637.61 | 2.8185
| 40098.1062 | 60.001 | 0 |  |  |  | -1.4092 | -1.4092 |  | 0 | -4.9587 | 0 | 434.9435 | 4.4073 | 346.0371 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1062 | 60.001 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7637.94 | -1.4092
| 40098.1062 | 60.001 | 0 |  |  |  | -1.4092 | -1.4092 |  | 0 | -4.9587 | 0 | 432.3405 | 4.4073 | 344.0036 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1062 | 60.001 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7637.94 | -1.4092
| 40098.1062 | 59.999 | 0 |  |  |  | 1.4092 | 1.4092 |  | 0 | -2.1403 | 0 | 429.7847 | 4.4073 | 341.9942 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1062 | 59.999 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7638.27 | 1.4092
| 40098.1063 | 59.999 | 0 |  |  |  | 1.4092 | 1.4092 |  | 0 | -2.1403 | 0 | 427.2589 | 4.4073 | 340.0084 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1063 | 59.999 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7638.6 | 1.4092
| 40098.1063 | 59.999 | 0 |  |  |  | 1.4092 | 1.4092 |  | 0 | -2.1403 | 0 | 424.7624 | 4.4073 | 338.0458 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1063 | 59.999 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7638.6 | 1.4092
| 40098.1063 | 60.002 | 0 |  |  |  | -2.8185 | -2.8185 |  | 0 | -6.368 | 0 | 422.2703 | 4.4073 | 336.106 | 633 | [6 empty] | 0 | 633 | -1592.4107 | [13 empty] | 40098.1063 | 60.002 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7638.93 | -2.8185
| 40098.1063 | 60.007 | 0 |  |  |  | -9.87 | -9.87 |  | 0 | -13.4195 | 0 | 419.7663 | 4.4073 | 334.1887 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1063 | 60.007 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7639.26 | -9.87
| 40098.1064 | 60.007 | 0 |  |  |  | -9.87 | -9.87 |  | 0 | -13.4195 | 0 | 417.291 | 4.4073 | 332.2934 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1064 | 60.007 | 0 | 0 | 164.9734 | 0 | 0 | 0 | 0 | -420 | 7639.26 | -9.87
| 40098.1064 | 60.008 | 0 |  |  |  | -11.2792 | -11.2792 |  | 0 | -14.8287 | 0 | 414.8357 | 4.4073 | 330.4197 | 633 | [6 empty] | 0 | 633 | -1875.5259 | [13 empty] | 40098.1064 | 60.008 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7639.59 | -11.2792
| 40098.1064 | 60.014 | 0 |  |  |  | -19.7399 | -19.7399 |  | 0 | -23.2894 | 0 | 412.3605 | 4.4073 | 328.5674 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1064 | 60.014 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7639.92 | -19.7399
| 40098.1064 | 60.014 | 0 |  |  |  | -19.7399 | -19.7399 |  | 0 | -23.2894 | 0 | 409.913 | 4.4073 | 326.736 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1064 | 60.014 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7639.92 | -19.7399
| 40098.1064 | 60.017 | 0 |  |  |  | -23.9676 | -23.9676 |  | 0 | -27.5171 | 0 | 407.4692 | 4.4073 | 324.9252 | 633 | [6 empty] | 0 | 633 | -2557.4039 | [13 empty] | 40098.1064 | 60.017 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7640.25 | -23.9676
| 40098.1065 | 60.021 | 0 |  |  |  | -29.6099 | -29.6099 |  | 0 | -33.1594 | 0 | 405.0213 | 4.4073 | 323.1346 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1065 | 60.021 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7640.58 | -29.6099
| 40098.1065 | 60.021 | 0 |  |  |  | -29.6099 | -29.6099 |  | 0 | -33.1594 | 0 | 402.6004 | 4.4073 | 321.3638 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1065 | 60.021 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7640.58 | -29.6099
| 40098.1065 | 60.017 | 0 |  |  |  | -23.9676 | -23.9676 |  | 0 | -27.5171 | 0 | 400.2371 | 4.4073 | 319.6127 | 633 | [6 empty] | 0 | 633 | -2557.4039 | [13 empty] | 40098.1065 | 60.017 | 0 | 0 | 157.6281 | 0 | 0 | 0 | 0 | -420 | 7640.91 | -23.9676
| 40098.1065 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 397.8843 | 4.4073 | 317.8808 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1065 | 60.019 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7641.24 | -26.7914
| 40098.1066 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 395.5569 | 4.4073 | 316.1678 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1066 | 60.019 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7641.24 | -26.7914
| 40098.1066 | 60.023 | 0 |  |  |  | -32.4283 | -32.4283 |  | 0 | -35.9778 | 0 | 393.2243 | 4.4073 | 314.4735 | 633 | [6 empty] | 0 | 633 | -3375.794 | [13 empty] | 40098.1066 | 60.023 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7641.57 | -32.4283
| 40098.1066 | 60.025 | 0 |  |  |  | -35.2522 | -35.2522 |  | 0 | -38.8017 | 0 | 390.9016 | 4.4073 | 312.7975 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1066 | 60.025 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7641.9 | -35.2522
| 40098.1066 | 60.025 | 0 |  |  |  | -35.2522 | -35.2522 |  | 0 | -38.8017 | 0 | 388.6037 | 4.4073 | 311.1394 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1066 | 60.025 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7641.9 | -35.2522
| 40098.1067 | 60.021 | 0 |  |  |  | -29.6099 | -29.6099 |  | 0 | -33.1594 | 0 | 386.3603 | 4.4073 | 309.4992 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.1067 | 60.021 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7642.23 | -29.6099
| 40098.1067 | 60.024 | 0 |  |  |  | -33.8375 | -33.8375 |  | 0 | -37.3871 | 0 | 384.1183 | 4.4073 | 307.8763 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7642.56 | -33.8375
| 40098.1067 | 60.024 | 0 |  |  |  | -33.8375 | -33.8375 |  | 0 | -37.3871 | 0 | 381.8998 | 4.4073 | 306.2707 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 0 | 0 | 155.5317 | 0 | 0 | 0 | 0 | -420 | 7642.56 | -33.8375
| 40098.1067 | 60.024 | 0 |  |  |  | -33.8375 | -33.8375 |  | 0 | -37.3871 | 0 | 379.7046 | 4.4073 | 304.6819 | 633 | [6 empty] | 0 | 633 | -3565.8569 | [13 empty] | 40098.1067 | 60.024 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7642.89 | -33.8375
| 40098.1067 | 60.02 | 0 |  |  |  | -28.2006 | -28.2006 |  | 0 | -31.7502 | 0 | 377.5616 | 4.4073 | 303.1098 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1067 | 60.02 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7643.22 | -28.2006
| 40098.1068 | 60.02 | 0 |  |  |  | -28.2006 | -28.2006 |  | 0 | -31.7502 | 0 | 375.4408 | 4.4073 | 301.5541 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7643.22 | -28.2006
| 40098.1068 | 60.025 | 0 |  |  |  | -35.2522 | -35.2522 |  | 0 | -38.8017 | 0 | 373.3055 | 4.4073 | 300.0144 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1068 | 60.025 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7643.55 | -35.2522
| 40098.1068 | 60.02 | 0 |  |  |  | -28.2006 | -28.2006 |  | 0 | -31.7502 | 0 | 371.2283 | 4.4073 | 298.4907 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7643.88 | -28.2006
| 40098.1068 | 60.02 | 0 |  |  |  | -28.2006 | -28.2006 |  | 0 | -31.7502 | 0 | 369.1723 | 4.4073 | 296.9826 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1068 | 60.02 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7643.88 | -28.2006
| 40098.1069 | 60.02 | 0 |  |  |  | -28.2006 | -28.2006 |  | 0 | -31.7502 | 0 | 367.1372 | 4.4073 | 295.4898 | 633 | [6 empty] | 0 | 633 | -2910.4122 | [13 empty] | 40098.1069 | 60.02 | 0 | 0 | 160.4472 | 0 | 0 | 0 | 0 | -420 | 7644.21 | -28.2006
| 40098.1069 | 60.022 | 0 |  |  |  | -31.0191 | -31.0191 |  | 0 | -34.5686 | 0 | 365.1084 | 4.4073 | 294.0123 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7644.54 | -31.0191
| 40098.1069 | 60.022 | 0 |  |  |  | -31.0191 | -31.0191 |  | 0 | -34.5686 | 0 | 363.0999 | 4.4073 | 292.5496 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7644.54 | -31.0191
| 40098.1069 | 60.022 | 0 |  |  |  | -31.0191 | -31.0191 |  | 0 | -34.5686 | 0 | 361.1116 | 4.4073 | 291.1017 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.1069 | 60.022 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7644.87 | -31.0191
| 40098.107 | 60.021 | 0 |  |  |  | -29.6099 | -29.6099 |  | 0 | -33.1594 | 0 | 359.15 | 4.4073 | 289.6682 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.107 | 60.021 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7645.2 | -29.6099
| 40098.107 | 60.021 | 0 |  |  |  | -29.6099 | -29.6099 |  | 0 | -33.1594 | 0 | 357.2079 | 4.4073 | 288.249 | 633 | [6 empty] | 0 | 633 | -3050.5957 | [13 empty] | 40098.107 | 60.021 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7645.2 | -29.6099
| 40098.107 | 60.023 | 0 |  |  |  | -32.4283 | -32.4283 |  | 0 | -35.9778 | 0 | 355.271 | 4.4073 | 286.8438 | 633 | [6 empty] | 0 | 633 | -3375.794 | [13 empty] | 40098.107 | 60.023 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7645.53 | -32.4283
| 40098.107 | 60.022 | 0 |  |  |  | -31.0191 | -31.0191 |  | 0 | -34.5686 | 0 | 353.3601 | 4.4073 | 285.4525 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.107 | 60.022 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7645.86 | -31.0191
| 40098.107 | 60.022 | 0 |  |  |  | -31.0191 | -31.0191 |  | 0 | -34.5686 | 0 | 351.4677 | 4.4073 | 284.0748 | 633 | [6 empty] | 0 | 633 | -3204.9667 | [13 empty] | 40098.107 | 60.022 | 0 | 0 | 163.9586 | 0 | 0 | 0 | 0 | -420 | 7645.86 | -31.0191
| 40098.1071 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 349.6143 | 4.4073 | 282.7106 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1071 | 60.019 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7646.19 | -26.7914
| 40098.1071 | 60.018 | 0 |  |  |  | -25.3822 | -25.3822 |  | 0 | -28.9317 | 0 | 347.7856 | 4.4073 | 281.3596 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7646.52 | -25.3822
| 40098.1071 | 60.018 | 0 |  |  |  | -25.3822 | -25.3822 |  | 0 | -28.9317 | 0 | 345.9744 | 4.4073 | 280.0217 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7646.52 | -25.3822
| 40098.1071 | 60.018 | 0 |  |  |  | -25.3822 | -25.3822 |  | 0 | -28.9317 | 0 | 344.1806 | 4.4073 | 278.6966 | 633 | [6 empty] | 0 | 633 | -2665.443 | [13 empty] | 40098.1071 | 60.018 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7646.85 | -25.3822
| 40098.1072 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 342.3972 | 4.4073 | 277.3842 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7647.18 | -26.7914
| 40098.1072 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 340.6306 | 4.4073 | 276.0843 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7647.18 | -26.7914
| 40098.1072 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 338.8808 | 4.4073 | 274.7968 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1072 | 60.019 | 0 | 0 | 166.0724 | 0 | 0 | 0 | 0 | -420 | 7647.51 | -26.7914
| 40098.1072 | 60.015 | 0 |  |  |  | -21.1491 | -21.1491 |  | 0 | -24.6986 | 0 | 337.1738 | 4.4073 | 273.5213 | 633 | [6 empty] | 0 | 633 | -2366.3052 | [13 empty] | 40098.1072 | 60.015 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7647.84 | -21.1491
| 40098.1073 | 60.015 | 0 |  |  |  | -21.1491 | -21.1491 |  | 0 | -24.6986 | 0 | 335.4828 | 4.4073 | 272.2579 | 633 | [6 empty] | 0 | 633 | -2366.3052 | [13 empty] | 40098.1073 | 60.015 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7647.84 | -21.1491
| 40098.1073 | 60.016 | 0 |  |  |  | -22.5584 | -22.5584 |  | 0 | -26.1079 | 0 | 333.801 | 4.4073 | 271.0063 | 633 | [6 empty] | 0 | 633 | -2458.1461 | [13 empty] | 40098.1073 | 60.016 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7648.17 | -22.5584
| 40098.1073 | 60.013 | 0 |  |  |  | -18.3307 | -18.3307 |  | 0 | -21.8802 | 0 | 332.1544 | 4.4073 | 269.7663 | 633 | [6 empty] | 0 | 633 | -2201.78 | [13 empty] | 40098.1073 | 60.013 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7648.5 | -18.3307
| 40098.1073 | 60.013 | 0 |  |  |  | -18.3307 | -18.3307 |  | 0 | -21.8802 | 0 | 330.5229 | 4.4073 | 268.5378 | 633 | [6 empty] | 0 | 633 | -2201.78 | [13 empty] | 40098.1073 | 60.013 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7648.5 | -18.3307
| 40098.1073 | 60.012 | 0 |  |  |  | -16.9215 | -16.9215 |  | 0 | -20.471 | 0 | 328.9128 | 4.4073 | 267.3206 | 633 | [6 empty] | 0 | 633 | -2127.8086 | [13 empty] | 40098.1073 | 60.012 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7648.83 | -16.9215
| 40098.1074 | 60.01 | 0 |  |  |  | -14.0976 | -14.0976 |  | 0 | -17.6471 | 0 | 327.3303 | 4.4073 | 266.1145 | 633 | [6 empty] | 0 | 633 | -1993.5983 | [13 empty] | 40098.1074 | 60.01 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7649.16 | -14.0976
| 40098.1074 | 60.01 | 0 |  |  |  | -14.0976 | -14.0976 |  | 0 | -17.6471 | 0 | 325.7622 | 4.4073 | 264.9195 | 633 | [6 empty] | 0 | 633 | -1993.5983 | [13 empty] | 40098.1074 | 60.01 | 0 | 0 | 163.7666 | 0 | 0 | 0 | 0 | -420 | 7649.16 | -14.0976
| 40098.1074 | 60.007 | 0 |  |  |  | -9.87 | -9.87 |  | 0 | -13.4195 | 0 | 324.2275 | 4.4073 | 263.7354 | 633 | [6 empty] | 0 | 633 | -1821.5835 | [13 empty] | 40098.1074 | 60.007 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7649.49 | -9.87
| 40098.1074 | 60.009 | 0 |  |  |  | -12.6884 | -12.6884 |  | 0 | -16.2379 | 0 | 322.6939 | 4.4073 | 262.562 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1074 | 60.009 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7649.82 | -12.6884
| 40098.1075 | 60.009 | 0 |  |  |  | -12.6884 | -12.6884 |  | 0 | -16.2379 | 0 | 321.174 | 4.4073 | 261.3991 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1075 | 60.009 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7649.82 | -12.6884
| 40098.1075 | 60.009 | 0 |  |  |  | -12.6884 | -12.6884 |  | 0 | -16.2379 | 0 | 319.6677 | 4.4073 | 260.2467 | 633 | [6 empty] | 0 | 633 | -1932.7605 | [13 empty] | 40098.1075 | 60.009 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7650.15 | -12.6884
| 40098.1075 | 60.003 | 0 |  |  |  | -4.2277 | -4.2277 |  | 0 | -7.7772 | 0 | 318.2124 | 4.4073 | 259.1045 | 633 | [6 empty] | 0 | 633 | -1633.4808 | [13 empty] | 40098.1075 | 60.003 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7650.48 | -4.2277
| 40098.1075 | 60.003 | 0 |  |  |  | -4.2277 | -4.2277 |  | 0 | -7.7772 | 0 | 316.7699 | 4.4073 | 257.9725 | 633 | [6 empty] | 0 | 633 | -1633.4808 | [13 empty] | 40098.1075 | 60.003 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7650.48 | -4.2277
| 40098.1076 | 59.999 | 0 |  |  |  | 1.4092 | 1.4092 |  | 0 | -2.1403 | 0 | 315.3651 | 4.4073 | 256.8506 | 633 | [6 empty] | 0 | 633 | -1480.7224 | [13 empty] | 40098.1076 | 59.999 | 0 | 0 | 165.1017 | 0 | 0 | 0 | 0 | -420 | 7650.81 | 1.4092
| 40098.1076 | 59.992 | 0 |  |  |  | 11.2792 | 11.2792 |  | 0 | 7.7297 | 0 | 314.0158 | 4.4073 | 255.7385 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1076 | 59.992 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7651.14 | 11.2792
| 40098.1076 | 59.992 | 0 |  |  |  | 11.2792 | 11.2792 |  | 0 | 7.7297 | 0 | 312.6783 | 4.4073 | 254.6362 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1076 | 59.992 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7651.14 | 11.2792
| 40098.1076 | 59.991 | 0 |  |  |  | 12.6884 | 12.6884 |  | 0 | 9.1389 | 0 | 311.3585 | 4.4073 | 253.5435 | 633 | [6 empty] | 0 | 633 | -1247.3195 | [13 empty] | 40098.1076 | 59.991 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7651.47 | 12.6884
| 40098.1077 | 59.992 | 0 |  |  |  | 11.2792 | 11.2792 |  | 0 | 7.7297 | 0 | 310.0441 | 4.4073 | 252.4602 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1077 | 59.992 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7651.8 | 11.2792
| 40098.1077 | 59.992 | 0 |  |  |  | 11.2792 | 11.2792 |  | 0 | 7.7297 | 0 | 308.7411 | 4.4073 | 251.3864 | 633 | [6 empty] | 0 | 633 | -1272.3778 | [13 empty] | 40098.1077 | 59.992 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7651.8 | 11.2792
| 40098.1077 | 59.988 | 0 |  |  |  | 16.9215 | 16.9215 |  | 0 | 13.372 | 0 | 307.4734 | 4.4073 | 250.3219 | 633 | [6 empty] | 0 | 633 | -1177.6527 | [13 empty] | 40098.1077 | 59.988 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7652.13 | 16.9215
| 40098.1077 | 59.985 | 0 |  |  |  | 21.1491 | 21.1491 |  | 0 | 17.5996 | 0 | 306.2346 | 4.4073 | 249.2664 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1077 | 59.985 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7652.46 | 21.1491
| 40098.1077 | 59.985 | 0 |  |  |  | 21.1491 | 21.1491 |  | 0 | 17.5996 | 0 | 305.0064 | 4.4073 | 248.22 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1077 | 59.985 | 0 | 0 | 165.4764 | 0 | 0 | 0 | 0 | -420 | 7652.46 | 21.1491
| 40098.1078 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | 0 | 19.0089 | 0 | 303.7945 | 4.4073 | 247.1825 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7652.79 | 22.5584
| 40098.1078 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | 0 | 19.0089 | 0 | 302.5929 | 4.4073 | 246.1538 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7616 | 22.5584
| 40098.1078 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | 0 | 19.0089 | 0 | 301.4014 | 4.4073 | 245.1338 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1078 | 59.984 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7616 | 22.5584
| 40098.1078 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 300.2316 | 4.4073 | 244.1223 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1078 | 59.982 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7626 | 25.3822
| 40098.1079 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 299.0716 | 4.4073 | 243.1193 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1079 | 59.982 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7632 | 25.3822
| 40098.1079 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 297.9212 | 4.4073 | 242.1247 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1079 | 59.982 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7632 | 25.3822
| 40098.1079 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | 0 | 26.0604 | 0 | 296.7979 | 4.4073 | 241.1383 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1079 | 59.979 | 0 | 0 | 206.4591 | 0 | 0 | 0 | 0 | -420 | 7632 | 29.6099
| 40098.1079 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 295.7011 | 4.4073 | 240.1601 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1079 | 59.976 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.108 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 294.6133 | 4.4073 | 239.1899 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.108 | 59.976 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.108 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 293.5345 | 4.4073 | 238.2277 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.108 | 59.976 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.108 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 292.43 | 4.4073 | 237.2733 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.108 | 59.982 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 25.3822
| 40098.108 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 291.3345 | 4.4073 | 236.3267 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.108 | 59.982 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 25.3822
| 40098.108 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 290.2705 | 4.4073 | 235.3878 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.108 | 59.978 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 31.0191
| 40098.1081 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 289.2377 | 4.4073 | 234.4564 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1081 | 59.974 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 36.6614
| 40098.1081 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 288.2132 | 4.4073 | 233.5325 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1081 | 59.974 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | -420 | 7632 | 36.6614
| 40098.1081 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 287.1856 | 4.4073 | 232.616 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1081 | 59.976 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.1081 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 286.1606 | 4.4073 | 231.7068 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1081 | 59.977 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 32.4283
| 40098.1082 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 285.1437 | 4.4073 | 230.8048 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1082 | 59.977 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 32.4283
| 40098.1082 | 59.975 | 0 |  |  |  | 35.2522 | 35.2522 |  | 0 | 31.7026 | 0 | 284.1459 | 4.4073 | 229.91 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1082 | 59.975 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 35.2522
| 40098.1082 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 283.1891 | 4.4073 | 229.0222 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1082 | 59.969 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1082 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 282.2397 | 4.4073 | 228.1413 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1082 | 59.969 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1083 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 281.2923 | 4.4073 | 227.2674 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1083 | 59.97 | 0 | 0 | 214.3467 | 0 | 0 | 0 | 0 | -420 | 7632 | 42.2983
| 40098.1083 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 280.3358 | 4.4073 | 226.4002 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1083 | 59.973 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 38.0706
| 40098.1083 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 279.3867 | 4.4073 | 225.5398 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1083 | 59.973 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 38.0706
| 40098.1083 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 278.4178 | 4.4073 | 224.686 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1083 | 59.978 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 31.0191
| 40098.1083 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 277.4563 | 4.4073 | 223.8388 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1083 | 59.978 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 31.0191
| 40098.1084 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 276.5022 | 4.4073 | 222.998 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1084 | 59.978 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 31.0191
| 40098.1084 | 59.975 | 0 |  |  |  | 35.2522 | 35.2522 |  | 0 | 31.7026 | 0 | 275.5714 | 4.4073 | 222.1637 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1084 | 59.975 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 35.2522
| 40098.1084 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 274.6423 | 4.4073 | 221.3357 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1084 | 59.976 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.1084 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 273.7202 | 4.4073 | 220.514 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1084 | 59.976 | 0 | 0 | 212.1727 | 0 | 0 | 0 | 0 | -420 | 7632 | 33.8375
| 40098.1085 | 59.975 | 0 |  |  |  | 35.2522 | 35.2522 |  | 0 | 31.7026 | 0 | 272.8103 | 4.4073 | 219.6985 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1085 | 59.975 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 35.2522
| 40098.1085 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 271.939 | 4.4073 | 218.8892 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1085 | 59.969 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1085 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 271.0741 | 4.4073 | 218.0859 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1085 | 59.969 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1085 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 270.2314 | 4.4073 | 217.2886 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1085 | 59.966 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 47.9406
| 40098.1086 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 269.395 | 4.4073 | 216.4972 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1086 | 59.966 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 47.9406
| 40098.1086 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 268.5647 | 4.4073 | 215.7117 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1086 | 59.966 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 47.9406
| 40098.1086 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 267.725 | 4.4073 | 214.9319 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1086 | 59.969 | 0 | 0 | 215.5982 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1086 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 266.8966 | 4.4073 | 214.158 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1086 | 59.968 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 45.1221
| 40098.1086 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 266.0742 | 4.4073 | 213.3896 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1086 | 59.968 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 45.1221
| 40098.1087 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 265.2732 | 4.4073 | 212.6269 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1087 | 59.965 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 49.3498
| 40098.1087 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 264.4525 | 4.4073 | 211.8698 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1087 | 59.97 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 42.2983
| 40098.1087 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 263.6377 | 4.4073 | 211.1181 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1087 | 59.97 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 42.2983
| 40098.1087 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 262.8186 | 4.4073 | 210.3718 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1087 | 59.972 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 39.4798
| 40098.1088 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 262.0306 | 4.4073 | 209.631 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1088 | 59.967 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 46.5313
| 40098.1088 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 261.2483 | 4.4073 | 208.8954 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1088 | 59.967 | 0 | 0 | 218.3273 | 0 | 0 | 0 | 0 | -420 | 7632 | 46.5313
| 40098.1088 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 260.4615 | 4.4073 | 208.1651 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1088 | 59.969 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1088 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 259.6803 | 4.4073 | 207.44 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1088 | 59.969 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1089 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 258.9046 | 4.4073 | 206.72 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1089 | 59.969 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7632 | 43.7075
| 40098.1089 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 258.1443 | 4.4073 | 206.0051 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1089 | 59.967 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7631 | 46.5313
| 40098.1089 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 257.3943 | 4.4073 | 205.2953 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1089 | 59.966 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7625 | 47.9406
| 40098.1089 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 256.6495 | 4.4073 | 204.5904 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1089 | 59.966 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7625 | 47.9406
| 40098.1089 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 255.9149 | 4.4073 | 203.8904 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1089 | 59.965 | 0 | 0 | 217.3794 | 0 | 0 | 0 | 0 | -420 | 7623 | 49.3498
| 40098.109 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 255.1755 | 4.4073 | 203.1954 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.109 | 59.967 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7621 | 46.5313
| 40098.109 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 254.4413 | 4.4073 | 202.5051 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.109 | 59.967 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7621 | 46.5313
| 40098.109 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 253.7218 | 4.4073 | 201.8197 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.109 | 59.965 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7623 | 49.3498
| 40098.109 | 59.964 | 0 |  |  |  | 50.759 | 50.759 |  | 0 | 47.2095 | 0 | 253.0122 | 4.4073 | 201.1389 | 633 | [6 empty] | 0 | 633 | -814.1557 | [13 empty] | 40098.109 | 59.964 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7625 | 50.759
| 40098.1091 | 59.964 | 0 |  |  |  | 50.759 | 50.759 |  | 0 | 47.2095 | 0 | 252.3074 | 4.4073 | 200.4629 | 633 | [6 empty] | 0 | 633 | -814.1557 | [13 empty] | 40098.1091 | 59.964 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7625 | 50.759
| 40098.1091 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 251.5785 | 4.4073 | 199.7915 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1091 | 59.97 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7627 | 42.2983
| 40098.1091 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 250.8594 | 4.4073 | 199.1246 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1091 | 59.969 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7628 | 43.7075
| 40098.1091 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 250.1451 | 4.4073 | 198.4623 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1091 | 59.969 | 0 | 0 | 214.8304 | 0 | 0 | 0 | 0 | -420 | 7628 | 43.7075
| 40098.1092 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 249.4405 | 4.4073 | 197.8045 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1092 | 59.968 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7628 | 45.1221
| 40098.1092 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 248.7549 | 4.4073 | 197.1511 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1092 | 59.965 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7629 | 49.3498
| 40098.1092 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 248.0738 | 4.4073 | 196.5022 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1092 | 59.965 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7629 | 49.3498
| 40098.1092 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 247.3737 | 4.4073 | 195.8576 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1092 | 59.97 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7630 | 42.2983
| 40098.1092 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 246.6877 | 4.4073 | 195.2173 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1092 | 59.968 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7631 | 45.1221
| 40098.1093 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 246.0063 | 4.4073 | 194.5812 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1093 | 59.968 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7631 | 45.1221
| 40098.1093 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 245.3433 | 4.4073 | 193.9494 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1093 | 59.965 | 0 | 0 | 227.6559 | 0 | 0 | 0 | 0 | -420 | 7635 | 49.3498
| 40098.1093 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 244.6662 | 4.4073 | 193.3218 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1093 | 59.969 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7638 | 43.7075
| 40098.1093 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 243.9934 | 4.4073 | 192.6983 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1093 | 59.969 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7638 | 43.7075
| 40098.1094 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 243.3344 | 4.4073 | 192.0789 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1094 | 59.967 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7639 | 46.5313
| 40098.1094 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 242.6842 | 4.4073 | 191.4636 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1094 | 59.966 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7642 | 47.9406
| 40098.1094 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 242.0383 | 4.4073 | 190.8523 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1094 | 59.966 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7642 | 47.9406
| 40098.1094 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | 0 | 26.0604 | 0 | 241.3371 | 4.4073 | 190.245 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1094 | 59.979 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7644 | 29.6099
| 40098.1095 | 59.983 | 0 |  |  |  | 23.9676 | 23.9676 |  | 0 | 20.4181 | 0 | 240.6222 | 4.4073 | 189.6416 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1095 | 59.983 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7645 | 23.9676
| 40098.1095 | 59.983 | 0 |  |  |  | 23.9676 | 23.9676 |  | 0 | 20.4181 | 0 | 239.9118 | 4.4073 | 189.0422 | 633 | [6 empty] | 0 | 633 | -1077.479 | [13 empty] | 40098.1095 | 59.983 | 0 | 0 | 225.0181 | 0 | 0 | 0 | 0 | -420 | 7645 | 23.9676
| 40098.1095 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 239.2469 | 4.4073 | 188.4466 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1095 | 59.974 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7647 | 36.6614
| 40098.1095 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 238.6268 | 4.4073 | 187.8548 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1095 | 59.965 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7648 | 49.3498
| 40098.1095 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 238.0108 | 4.4073 | 187.2668 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1095 | 59.965 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7648 | 49.3498
| 40098.1096 | 59.962 | 0 |  |  |  | 53.5775 | 53.5775 |  | 0 | 50.028 | 0 | 237.4121 | 4.4073 | 186.6826 | 633 | [6 empty] | 0 | 633 | -793.7488 | [13 empty] | 40098.1096 | 59.962 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7649 | 53.5775
| 40098.1096 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | 0 | 51.4426 | 0 | 236.8217 | 4.4073 | 186.1021 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7650 | 54.9921
| 40098.1096 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | 0 | 51.4426 | 0 | 236.2351 | 4.4073 | 185.5253 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7650 | 54.9921
| 40098.1096 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | 0 | 51.4426 | 0 | 235.6521 | 4.4073 | 184.9522 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1096 | 59.961 | 0 | 0 | 228.3652 | 0 | 0 | 0 | 0 | -420 | 7651 | 54.9921
| 40098.1097 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 235.064 | 4.4073 | 184.3826 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1097 | 59.963 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7652 | 52.1682
| 40098.1097 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 234.4795 | 4.4073 | 183.8167 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1097 | 59.963 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7652 | 52.1682
| 40098.1097 | 59.959 | 0 |  |  |  | 57.8105 | 57.8105 |  | 0 | 54.261 | 0 | 233.9163 | 4.4073 | 183.2543 | 633 | [6 empty] | 0 | 633 | -764.9517 | [13 empty] | 40098.1097 | 59.959 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7653 | 57.8105
| 40098.1097 | 59.951 | 0 |  |  |  | 69.0897 | 69.0897 |  | 0 | 65.5402 | 0 | 233.3918 | 4.4073 | 182.6954 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1097 | 59.951 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7654 | 69.0897
| 40098.1098 | 59.951 | 0 |  |  |  | 69.0897 | 69.0897 |  | 0 | 65.5402 | 0 | 232.8705 | 4.4073 | 182.1399 | 633 | [6 empty] | 0 | 633 | -697.5227 | [13 empty] | 40098.1098 | 59.951 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7654 | 69.0897
| 40098.1098 | 59.953 | 0 |  |  |  | 66.2712 | 66.2712 |  | 0 | 62.7217 | 0 | 232.3438 | 4.4073 | 181.588 | 633 | [6 empty] | 0 | 633 | -713.2327 | [13 empty] | 40098.1098 | 59.953 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7655 | 66.2712
| 40098.1098 | 59.957 | 0 |  |  |  | 60.629 | 60.629 |  | 0 | 57.0795 | 0 | 231.8028 | 4.4073 | 181.0394 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1098 | 59.957 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7655 | 60.629
| 40098.1098 | 59.957 | 0 |  |  |  | 60.629 | 60.629 |  | 0 | 57.0795 | 0 | 231.2652 | 4.4073 | 180.4943 | 633 | [6 empty] | 0 | 633 | -746.9095 | [13 empty] | 40098.1098 | 59.957 | 0 | 0 | 234.0753 | 0 | 0 | 0 | 0 | -420 | 7655 | 60.629
| 40098.1098 | 59.956 | 0 |  |  |  | 62.0382 | 62.0382 |  | 0 | 58.4887 | 0 | 230.7352 | 4.4073 | 179.9525 | 633 | [6 empty] | 0 | 633 | -738.2038 | [13 empty] | 40098.1098 | 59.956 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 62.0382
| 40098.1099 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 230.1783 | 4.4073 | 179.414 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 52.1682
| 40098.1099 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 229.6247 | 4.4073 | 178.8788 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7656 | 52.1682
| 40098.1099 | 59.961 | 0 |  |  |  | 54.9921 | 54.9921 |  | 0 | 51.4426 | 0 | 229.0832 | 4.4073 | 178.3469 | 633 | [6 empty] | 0 | 633 | -783.8872 | [13 empty] | 40098.1099 | 59.961 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 54.9921
| 40098.1099 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 228.5363 | 4.4073 | 177.8182 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.1099 | 59.963 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 52.1682
| 40098.11 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 227.9927 | 4.4073 | 177.2927 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.11 | 59.963 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7657 | 52.1682
| 40098.11 | 59.963 | 0 |  |  |  | 52.1682 | 52.1682 |  | 0 | 48.6187 | 0 | 227.4525 | 4.4073 | 176.7704 | 633 | [6 empty] | 0 | 633 | -803.8228 | [13 empty] | 40098.11 | 59.963 | 0 | 0 | 228.7982 | 0 | 0 | 0 | 0 | -420 | 7658 | 52.1682
| 40098.11 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 226.8943 | 4.4073 | 176.2512 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.11 | 59.968 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7658 | 45.1221
| 40098.11 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 226.3394 | 4.4073 | 175.7352 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.11 | 59.968 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7658 | 45.1221
| 40098.1101 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 225.7879 | 4.4073 | 175.2222 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1101 | 59.968 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7659 | 45.1221
| 40098.1101 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 225.2312 | 4.4073 | 174.7123 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1101 | 59.97 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7659 | 42.2983
| 40098.1101 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 224.6778 | 4.4073 | 174.2054 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1101 | 59.97 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7659 | 42.2983
| 40098.1101 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 224.1152 | 4.4073 | 173.7016 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1101 | 59.973 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7659 | 38.0706
| 40098.1102 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 223.5892 | 4.4073 | 173.2007 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1102 | 59.965 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7660 | 49.3498
| 40098.1102 | 59.965 | 0 |  |  |  | 49.3498 | 49.3498 |  | 0 | 45.8003 | 0 | 223.0663 | 4.4073 | 172.7028 | 633 | [6 empty] | 0 | 633 | -824.7578 | [13 empty] | 40098.1102 | 59.965 | 0 | 0 | 229.467 | 0 | 0 | 0 | 0 | -420 | 7660 | 49.3498
| 40098.1102 | 59.967 | 0 |  |  |  | 46.5313 | 46.5313 |  | 0 | 42.9818 | 0 | 222.5382 | 4.4073 | 172.2078 | 633 | [6 empty] | 0 | 633 | -846.8125 | [13 empty] | 40098.1102 | 59.967 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7660 | 46.5313
| 40098.1102 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 221.9926 | 4.4073 | 171.7157 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1102 | 59.972 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7661 | 39.4798
| 40098.1102 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 221.4501 | 4.4073 | 171.2265 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1102 | 59.972 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7661 | 39.4798
| 40098.1103 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 220.8944 | 4.4073 | 170.7402 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1103 | 59.976 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7661 | 33.8375
| 40098.1103 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 220.3706 | 4.4073 | 170.2567 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1103 | 59.969 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7662 | 43.7075
| 40098.1103 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 219.8497 | 4.4073 | 169.7759 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1103 | 59.969 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7662 | 43.7075
| 40098.1103 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 219.3156 | 4.4073 | 169.298 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1103 | 59.973 | 0 | 0 | 228.9802 | 0 | 0 | 0 | 0 | -420 | 7662 | 38.0706
| 40098.1104 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 218.7643 | 4.4073 | 168.8228 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1104 | 59.978 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7663 | 31.0191
| 40098.1104 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 218.2162 | 4.4073 | 168.3503 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1104 | 59.978 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7663 | 31.0191
| 40098.1104 | 59.981 | 0 |  |  |  | 26.7914 | 26.7914 |  | 0 | 23.2419 | 0 | 217.6591 | 4.4073 | 167.8806 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1104 | 59.981 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7663 | 26.7914
| 40098.1104 | 59.981 | 0 |  |  |  | 26.7914 | 26.7914 |  | 0 | 23.2419 | 0 | 217.1053 | 4.4073 | 167.4135 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1104 | 59.981 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7664 | 26.7914
| 40098.1105 | 59.981 | 0 |  |  |  | 26.7914 | 26.7914 |  | 0 | 23.2419 | 0 | 216.5545 | 4.4073 | 166.9491 | 633 | [6 empty] | 0 | 633 | -1041.9588 | [13 empty] | 40098.1105 | 59.981 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7664 | 26.7914
| 40098.1105 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 216.0029 | 4.4073 | 166.4874 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1105 | 59.982 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7664 | 25.3822
| 40098.1105 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | 0 | 19.0089 | 0 | 215.4464 | 4.4073 | 166.0282 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1105 | 59.984 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7665 | 22.5584
| 40098.1105 | 59.984 | 0 |  |  |  | 22.5584 | 22.5584 |  | 0 | 19.0089 | 0 | 214.8931 | 4.4073 | 165.5716 | 633 | [6 empty] | 0 | 633 | -1096.1268 | [13 empty] | 40098.1105 | 59.984 | 0 | 0 | 219.9756 | 0 | 0 | 0 | 0 | -420 | 7665 | 22.5584
| 40098.1105 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 214.3508 | 4.4073 | 165.1177 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1105 | 59.982 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7666 | 25.3822
| 40098.1106 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | 0 | 26.0604 | 0 | 213.8233 | 4.4073 | 164.6662 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1106 | 59.979 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7666 | 29.6099
| 40098.1106 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | 0 | 26.0604 | 0 | 213.2989 | 4.4073 | 164.2173 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1106 | 59.979 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7666 | 29.6099
| 40098.1106 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | 0 | 24.6511 | 0 | 212.7734 | 4.4073 | 163.7709 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1106 | 59.98 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7667 | 28.2006
| 40098.1106 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 212.2586 | 4.4073 | 163.327 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1106 | 59.978 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7668 | 31.0191
| 40098.1107 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 211.7468 | 4.4073 | 162.8856 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1107 | 59.978 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7668 | 31.0191
| 40098.1107 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | 0 | 24.6511 | 0 | 211.2299 | 4.4073 | 162.4466 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 0 | 0 | 229.0892 | 0 | 0 | 0 | 0 | -420 | 7668 | 28.2006
| 40098.1107 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | 0 | 24.6511 | 0 | 210.7159 | 4.4073 | 162.01 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7669 | 28.2006
| 40098.1107 | 59.98 | 0 |  |  |  | 28.2006 | 28.2006 |  | 0 | 24.6511 | 0 | 210.2048 | 4.4073 | 161.5758 | 633 | [6 empty] | 0 | 633 | -1025.0944 | [13 empty] | 40098.1107 | 59.98 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7669 | 28.2006
| 40098.1108 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 209.7041 | 4.4073 | 161.1441 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1108 | 59.978 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7669 | 31.0191
| 40098.1108 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 209.2293 | 4.4073 | 160.7146 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1108 | 59.972 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7670 | 39.4798
| 40098.1108 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 208.7571 | 4.4073 | 160.2876 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1108 | 59.972 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7670 | 39.4798
| 40098.1108 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 208.2913 | 4.4073 | 159.8628 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1108 | 59.971 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7670 | 40.8891
| 40098.1108 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 207.8166 | 4.4073 | 159.4404 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1108 | 59.974 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7671 | 36.6614
| 40098.1109 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 207.3444 | 4.4073 | 159.0202 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1109 | 59.974 | 0 | 0 | 229.6633 | 0 | 0 | 0 | 0 | -420 | 7671 | 36.6614
| 40098.1109 | 59.975 | 0 |  |  |  | 35.2522 | 35.2522 |  | 0 | 31.7026 | 0 | 206.871 | 4.4073 | 158.6024 | 633 | [6 empty] | 0 | 633 | -948.2936 | [13 empty] | 40098.1109 | 59.975 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7671 | 35.2522
| 40098.1109 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 206.4114 | 4.4073 | 158.1868 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1109 | 59.972 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7672 | 39.4798
| 40098.1109 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 205.9544 | 4.4073 | 157.7734 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1109 | 59.972 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7672 | 39.4798
| 40098.111 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 205.5111 | 4.4073 | 157.3622 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.111 | 59.969 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7673 | 43.7075
| 40098.111 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 205.0514 | 4.4073 | 156.9532 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.111 | 59.974 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7673 | 36.6614
| 40098.111 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 204.5941 | 4.4073 | 156.5464 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.111 | 59.974 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7673 | 36.6614
| 40098.111 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 204.1467 | 4.4073 | 156.1418 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.111 | 59.972 | 0 | 0 | 229.2339 | 0 | 0 | 0 | 0 | -420 | 7673 | 39.4798
| 40098.1111 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 203.7017 | 4.4073 | 155.7393 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1111 | 59.972 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 39.4798
| 40098.1111 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 203.259 | 4.4073 | 155.339 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1111 | 59.972 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 39.4798
| 40098.1111 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 202.8001 | 4.4073 | 154.9408 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1111 | 59.977 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 32.4283
| 40098.1111 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 202.3399 | 4.4073 | 154.5446 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1111 | 59.978 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 31.0191
| 40098.1111 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 201.8821 | 4.4073 | 154.1505 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1111 | 59.978 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 31.0191
| 40098.1112 | 59.976 | 0 |  |  |  | 33.8375 | 33.8375 |  | 0 | 30.288 | 0 | 201.4341 | 4.4073 | 153.7586 | 633 | [6 empty] | 0 | 633 | -962.7638 | [13 empty] | 40098.1112 | 59.976 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 33.8375
| 40098.1112 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 200.9958 | 4.4073 | 153.3686 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1112 | 59.974 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 36.6614
| 40098.1112 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 200.5597 | 4.4073 | 152.9807 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1112 | 59.974 | 0 | 0 | 231.4099 | 0 | 0 | 0 | 0 | -420 | 7673 | 36.6614
| 40098.1112 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 200.1149 | 4.4073 | 152.5948 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1112 | 59.977 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 32.4283
| 40098.1113 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 199.6688 | 4.4073 | 152.2109 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1113 | 59.978 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 31.0191
| 40098.1113 | 59.978 | 0 |  |  |  | 31.0191 | 31.0191 |  | 0 | 27.4696 | 0 | 199.225 | 4.4073 | 151.8289 | 633 | [6 empty] | 0 | 633 | -992.9519 | [13 empty] | 40098.1113 | 59.978 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 31.0191
| 40098.1113 | 59.979 | 0 |  |  |  | 29.6099 | 29.6099 |  | 0 | 26.0604 | 0 | 198.7799 | 4.4073 | 151.449 | 633 | [6 empty] | 0 | 633 | -1008.7671 | [13 empty] | 40098.1113 | 59.979 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 29.6099
| 40098.1113 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 198.3442 | 4.4073 | 151.071 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1113 | 59.977 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 32.4283
| 40098.1114 | 59.977 | 0 |  |  |  | 32.4283 | 32.4283 |  | 0 | 28.8788 | 0 | 197.9108 | 4.4073 | 150.6949 | 633 | [6 empty] | 0 | 633 | -977.6248 | [13 empty] | 40098.1114 | 59.977 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 32.4283
| 40098.1114 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 197.4904 | 4.4073 | 150.3208 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1114 | 59.974 | 0 | 0 | 218.6223 | 0 | 0 | 0 | 0 | -420 | 7673 | 36.6614
| 40098.1114 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 197.0829 | 4.4073 | 149.9486 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7673 | 40.8891
| 40098.1114 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 196.6775 | 4.4073 | 149.5782 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7673 | 40.8891
| 40098.1114 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 196.2741 | 4.4073 | 149.2098 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1114 | 59.971 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7673 | 40.8891
| 40098.1115 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 195.8834 | 4.4073 | 148.8432 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1115 | 59.968 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7673 | 45.1221
| 40098.1115 | 59.968 | 0 |  |  |  | 45.1221 | 45.1221 |  | 0 | 41.5726 | 0 | 195.4947 | 4.4073 | 148.4785 | 633 | [6 empty] | 0 | 633 | -858.2882 | [13 empty] | 40098.1115 | 59.968 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7673 | 45.1221
| 40098.1115 | 59.966 | 0 |  |  |  | 47.9406 | 47.9406 |  | 0 | 44.3911 | 0 | 195.1151 | 4.4073 | 148.1156 | 633 | [6 empty] | 0 | 633 | -835.6397 | [13 empty] | 40098.1115 | 59.966 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7674 | 47.9406
| 40098.1115 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 194.7196 | 4.4073 | 147.7545 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1115 | 59.971 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7675 | 40.8891
| 40098.1116 | 59.971 | 0 |  |  |  | 40.8891 | 40.8891 |  | 0 | 37.3395 | 0 | 194.3262 | 4.4073 | 147.3952 | 633 | [6 empty] | 0 | 633 | -894.7087 | [13 empty] | 40098.1116 | 59.971 | 0 | 0 | 213.5359 | 0 | 0 | 0 | 0 | -420 | 7675 | 40.8891
| 40098.1116 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 193.9277 | 4.4073 | 147.0377 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1116 | 59.973 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7676 | 38.0706
| 40098.1116 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 193.5452 | 4.4073 | 146.6821 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1116 | 59.969 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7677 | 43.7075
| 40098.1116 | 59.969 | 0 |  |  |  | 43.7075 | 43.7075 |  | 0 | 40.158 | 0 | 193.1645 | 4.4073 | 146.3281 | 633 | [6 empty] | 0 | 633 | -870.1248 | [13 empty] | 40098.1116 | 59.969 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7677 | 43.7075
| 40098.1117 | 59.972 | 0 |  |  |  | 39.4798 | 39.4798 |  | 0 | 35.9303 | 0 | 192.7753 | 4.4073 | 145.976 | 633 | [6 empty] | 0 | 633 | -907.5291 | [13 empty] | 40098.1117 | 59.972 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7678 | 39.4798
| 40098.1117 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 192.3846 | 4.4073 | 145.6256 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1117 | 59.973 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7679 | 38.0706
| 40098.1117 | 59.973 | 0 |  |  |  | 38.0706 | 38.0706 |  | 0 | 34.5211 | 0 | 191.9958 | 4.4073 | 145.2769 | 633 | [6 empty] | 0 | 633 | -920.7222 | [13 empty] | 40098.1117 | 59.973 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7679 | 38.0706
| 40098.1117 | 59.97 | 0 |  |  |  | 42.2983 | 42.2983 |  | 0 | 38.7488 | 0 | 191.6192 | 4.4073 | 144.9299 | 633 | [6 empty] | 0 | 633 | -882.2455 | [13 empty] | 40098.1117 | 59.97 | 0 | 0 | 225.6519 | 0 | 0 | 0 | 0 | -420 | 7680 | 42.2983
| 40098.1117 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 191.2307 | 4.4073 | 144.5846 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1117 | 59.974 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7681 | 36.6614
| 40098.1118 | 59.974 | 0 |  |  |  | 36.6614 | 36.6614 |  | 0 | 33.1119 | 0 | 190.8441 | 4.4073 | 144.2411 | 633 | [6 empty] | 0 | 633 | -934.3045 | [13 empty] | 40098.1118 | 59.974 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7681 | 36.6614
| 40098.1118 | 59.982 | 0 |  |  |  | 25.3822 | 25.3822 |  | 0 | 21.8327 | 0 | 190.4319 | 4.4073 | 143.8992 | 633 | [6 empty] | 0 | 633 | -1059.3874 | [13 empty] | 40098.1118 | 59.982 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7682 | 25.3822
| 40098.1118 | 59.985 | 0 |  |  |  | 21.1491 | 21.1491 |  | 0 | 17.5996 | 0 | 190.0114 | 4.4073 | 143.559 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1118 | 59.985 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7684 | 21.1491
| 40098.1118 | 59.985 | 0 |  |  |  | 21.1491 | 21.1491 |  | 0 | 17.5996 | 0 | 189.5929 | 4.4073 | 143.2204 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1118 | 59.985 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7684 | 21.1491
| 40098.1119 | 59.985 | 0 |  |  |  | 21.1491 | 21.1491 |  | 0 | 17.5996 | 0 | 189.1765 | 4.4073 | 142.8835 | 633 | [6 empty] | 0 | 633 | -1115.4314 | [13 empty] | 40098.1119 | 59.985 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7685 | 21.1491
| 40098.1119 | 59.989 | 0 |  |  |  | 15.5122 | 15.5122 |  | 0 | 11.9627 | 0 | 188.7484 | 4.4073 | 142.5482 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7687 | 15.5122
| 40098.1119 | 59.989 | 0 |  |  |  | 15.5122 | 15.5122 |  | 0 | 11.9627 | 0 | 188.3224 | 4.4073 | 142.2145 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 0 | 0 | 212.5736 | 0 | 0 | 0 | 0 | -420 | 7687 | 15.5122
| 40098.1119 | 59.989 | 0 |  |  |  | 15.5122 | 15.5122 |  | 0 | 11.9627 | 0 | 187.8985 | 4.4073 | 141.8824 | 633 | [6 empty] | 0 | 633 | -1199.9649 | [13 empty] | 40098.1119 | 59.989 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7689 | 15.5122
| 40098.112 | 59.987 | 0 |  |  |  | 18.3307 | 18.3307 |  | 0 | 14.7812 | 0 | 187.4833 | 4.4073 | 141.552 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.112 | 59.987 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7690 | 18.3307
| 40098.112 | 59.987 | 0 |  |  |  | 18.3307 | 18.3307 |  | 0 | 14.7812 | 0 | 187.0702 | 4.4073 | 141.2231 | 633 | [6 empty] | 0 | 633 | -1156.155 | [13 empty] | 40098.112 | 59.987 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7690 | 18.3307
| 40098.112 | 59.99 | 0 |  |  |  | 14.0976 | 14.0976 |  | 0 | 10.5481 | 0 | 186.6489 | 4.4073 | 140.8958 | 633 | [6 empty] | 0 | 633 | -1223.2292 | [13 empty] | 40098.112 | 59.99 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7692 | 14.0976
| 40098.112 | 59.996 | 0 |  |  |  | 5.6423 | 5.6423 |  | 0 | 2.0928 | 0 | 186.2095 | 4.4073 | 140.57 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.112 | 59.996 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7692 | 5.6423
| 40098.112 | 59.996 | 0 |  |  |  | 5.6423 | 5.6423 |  | 0 | 2.0928 | 0 | 185.7721 | 4.4073 | 140.2458 | 633 | [6 empty] | 0 | 633 | -1383.559 | [13 empty] | 40098.112 | 59.996 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7692 | 5.6423
| 40098.1121 | 60.001 | 0 |  |  |  | -1.4092 | -1.4092 |  | 0 | -4.9587 | 0 | 185.3202 | 4.4073 | 139.9232 | 633 | [6 empty] | 0 | 633 | -1553.355 | [13 empty] | 40098.1121 | 60.001 | 0 | 0 | 219.8973 | 0 | 0 | 0 | 0 | -420 | 7693 | -1.4092
| 40098.1121 | 60.004 | 0 |  |  |  | -5.6423 | -5.6423 |  | 0 | -9.1918 | 0 | 184.8603 | 4.4073 | 139.602 | 633 | [6 empty] | 0 | 633 | -1676.8951 | [13 empty] | 40098.1121 | 60.004 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7693 | -5.6423
| 40098.1121 | 60.004 | 0 |  |  |  | -5.6423 | -5.6423 |  | 0 | -9.1918 | 0 | 184.4027 | 4.4073 | 139.2824 | 633 | [6 empty] | 0 | 633 | -1676.8951 | [13 empty] | 40098.1121 | 60.004 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7693 | -5.6423
| 40098.1121 | 60.006 | 0 |  |  |  | -8.4607 | -8.4607 |  | 0 | -12.0102 | 0 | 183.9405 | 4.4073 | 138.9643 | 633 | [6 empty] | 0 | 633 | -1770.6573 | [13 empty] | 40098.1121 | 60.006 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7694 | -8.4607
| 40098.1122 | 60.014 | 0 |  |  |  | -19.7399 | -19.7399 |  | 0 | -23.2894 | 0 | 183.4541 | 4.4073 | 138.6477 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1122 | 60.014 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7694 | -19.7399
| 40098.1122 | 60.014 | 0 |  |  |  | -19.7399 | -19.7399 |  | 0 | -23.2894 | 0 | 182.9699 | 4.4073 | 138.3326 | 633 | [6 empty] | 0 | 633 | -2281.0798 | [13 empty] | 40098.1122 | 60.014 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7694 | -19.7399
| 40098.1122 | 60.019 | 0 |  |  |  | -26.7914 | -26.7914 |  | 0 | -30.3409 | 0 | 182.4715 | 4.4073 | 138.019 | 633 | [6 empty] | 0 | 633 | -2782.5464 | [13 empty] | 40098.1122 | 60.019 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7695 | -26.7914
| 40098.1122 | 60.025 | 0 |  |  |  | -35.2522 | -35.2522 |  | 0 | -38.8017 | 0 | 181.9557 | 4.4073 | 137.7068 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1122 | 60.025 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7695 | -35.2522
| 40098.1123 | 60.025 | 0 |  |  |  | -35.2522 | -35.2522 |  | 0 | -38.8017 | 0 | 181.4423 | 4.4073 | 137.3961 | 633 | [6 empty] | 0 | 633 | -3779.4591 | [13 empty] | 40098.1123 | 60.025 | 0 | 0 | 231.1754 | 0 | 0 | 0 | 0 | -420 | 7695 | -35.2522
| 40098.1123 | 60.026 | 0 |  |  |  | -36.6614 | -36.6614 |  | 0 | -40.2109 | 0 | 180.928 | 4.4073 | 137.0868 | 633 | [6 empty] | 0 | 633 | -4019.3085 | [13 empty] | 40098.1123 | 60.026 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7695 | -36.6614
| 40098.1123 | 60.029 | 0 |  |  |  | -40.8891 | -40.8891 |  | 0 | -44.4386 | 0 | 180.4064 | 4.4073 | 136.7789 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7696 | -40.8891
| 40098.1123 | 60.029 | 0 |  |  |  | -40.8891 | -40.8891 |  | 0 | -44.4386 | 0 | 179.8871 | 4.4073 | 136.4725 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7696 | -40.8891
| 40098.1123 | 60.029 | 0 |  |  |  | -40.8891 | -40.8891 |  | 0 | -44.4386 | 0 | 179.3702 | 4.4073 | 136.1675 | 633 | [6 empty] | 0 | 633 | -4964.4623 | [13 empty] | 40098.1123 | 60.029 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7696 | -40.8891
| 40098.1124 | 60.036 | 0 |  |  |  | -50.759 | -50.759 |  | 0 | -54.3085 | 0 | 178.833 | 4.4073 | 135.8639 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7697 | -50.759
| 40098.1124 | 60.036 | 0 |  |  |  | -50.759 | -50.759 |  | 0 | -54.3085 | 0 | 178.2983 | 4.4073 | 135.5617 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7697 | -50.759
| 40098.1124 | 60.037 | 0 |  |  |  | -52.1682 | -52.1682 |  | 0 | -55.7177 | 0 | 177.7628 | 4.4073 | 135.2609 | 633 | [6 empty] | 0 | 633 | -13322.9347 | [13 empty] | 40098.1124 | 60.037 | 0 | 0 | 226.6341 | 0 | 0 | 0 | 0 | -420 | 7697 | -52.1682
| 40098.1124 | 60.036 | 0 |  |  |  | -50.759 | -50.759 |  | 0 | -54.3085 | 0 | 177.2329 | 4.4073 | 134.9615 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1124 | 60.036 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7697 | -50.759
| 40098.1125 | 60.036 | 0 |  |  |  | -50.759 | -50.759 |  | 0 | -54.3085 | 0 | 176.7055 | 4.4073 | 134.6634 | 633 | [6 empty] | 0 | 633 | -11007.4396 | [13 empty] | 40098.1125 | 60.036 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7697 | -50.759
| 40098.1125 | 60.041 | 0 |  |  |  | -57.8105 | -57.8105 |  | 0 | -61.36 | 0 | 176.1644 | 4.4073 | 134.3667 | 633 | [6 empty] | 0 | 633 | -84446.3878 | [13 empty] | 40098.1125 | 60.041 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698 | -57.8105
| 40098.1125 | 60.044 | 0 |  |  |  | -62.0382 | -62.0382 |  | 0 | -65.5877 | 0 | 175.6163 | 4.4073 | 134.0713 | 633 | [6 empty] | 0 | 633 | 28148.7959 | [13 empty] | 40098.1125 | 60.044 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698 | -62.0382
| 40098.1125 | 60.044 | 0 |  |  |  | -62.0382 | -62.0382 |  | 0 | -65.5877 | 0 | 175.0705 | 4.4073 | 133.7773 | 633 | [6 empty] | 0 | 633 | 28148.7959 | [13 empty] | 40098.1125 | 60.044 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698 | -62.0382
| 40098.1126 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 174.5305 | 4.4073 | 133.4846 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1126 | 60.043 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698.33 | -60.629
| 40098.1126 | 60.048 | 0 |  |  |  | -67.6805 | -67.6805 |  | 0 | -71.23 | 0 | 173.977 | 4.4073 | 133.1933 | 633 | [6 empty] | 0 | 633 | 10127.3819 | [13 empty] | 40098.1126 | 60.048 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698.66 | -67.6805
| 40098.1126 | 60.048 | 0 |  |  |  | -67.6805 | -67.6805 |  | 0 | -71.23 | 0 | 173.4259 | 4.4073 | 132.9032 | 633 | [6 empty] | 0 | 633 | 10127.3819 | [13 empty] | 40098.1126 | 60.048 | 0 | 0 | 227.2551 | 0 | 0 | 0 | 0 | -420 | 7698.66 | -67.6805
| 40098.1126 | 60.046 | 0 |  |  |  | -64.862 | -64.862 |  | 0 | -68.4115 | 0 | 172.8837 | 4.4073 | 132.6144 | 633 | [6 empty] | 0 | 633 | 14888.9324 | [13 empty] | 40098.1126 | 60.046 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7698.99 | -64.862
| 40098.1127 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 172.3534 | 4.4073 | 132.327 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7699.32 | -60.629
| 40098.1127 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 171.8254 | 4.4073 | 132.0408 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7699.32 | -60.629
| 40098.1127 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 171.2998 | 4.4073 | 131.7559 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7699.65 | -60.629
| 40098.1127 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 170.7765 | 4.4073 | 131.4723 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7699.98 | -60.629
| 40098.1127 | 60.043 | 0 |  |  |  | -60.629 | -60.629 |  | 0 | -64.1785 | 0 | 170.2555 | 4.4073 | 131.1899 | 633 | [6 empty] | 0 | 633 | 50667.8327 | [13 empty] | 40098.1127 | 60.043 | 0 | 0 | 229.2902 | 0 | 0 | 0 | 0 | -420 | 7699.98 | -60.629

## Graph 20 to 52s (hidden)
60.0417

## Form 1 Summary Data
[6 empty] | Interconnection Performance | [9 empty] | Value A Data |  | BA Performance | [8 empty] | Value B |  | 12 to 24 second Average Period Evaluation | [11 empty] | Value B | 18 to 30 second Average Period Evaluation | [12 empty] | Value B | 20 to 40 second Average Period Evaluation | [12 empty] | Value B | 18 to 52 second Average Period Evaluation | [12 empty] | Value B | 20 to 52 second Average Period Evaluation
[18 empty] | JOU | Non- |  |  | Transferred | Contingent | [5 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent | [8 empty] | JOU | Non- |  |  | Transferred | Contingent
Date | A Point | FPointA | A Value | t(0) Time | C Value | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B | Value B | FR B |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias |  | Total | Dynamic | Conforming | Pumped | Ramping | Frequency | BA | Initial | Initial | Sustained | BA | BA | Bias
| Time | Hz | Hz |  | Hz | 12 to 24 sec | 12 to 24 sec | 18 to 30 sec | 18 to 30 sec | 20 to 40 sec | 20 to 40 sec | 18 to 52 sec | 18 to 52 sec | 20 to 52 sec | 20 to 52 sec |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting |  | Generation | Schedules | Load | Hydro | Units | Response | Lost Generation | Performance | Performance | Performance | Bias | Load | Setting
[6 empty] | Average | Average | Average | Average | Average | Average | Average | Average | Average | Average | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR | Frequency | Lost | n/a | Load (-) | Load (-) Gen (+) | n/a | n/a | n/a | Adjusted | Unadjusted |  | Setting |  | EPFR
[6 empty] | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Frequency | MW | Hz | MW |  | MW | MW |  |  |  | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | Hz | MW |  | MW | MW |  |  |  | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW
2009-10-12 02:27 | 40098.1023 | 60.039 | 60.0417 | 40098.1023 | 59.836 | 59.8823 | -397.4363 | 59.8844 | -402.6343 | 59.8887 | -415.1637 | 59.8879 | -411.9588 | 59.8887 | -413.8616 | 60.0417 | 633 | 0 | 165.4296 | 0 | 0 | 0 | 0 | -420 | 7600.1963 | -175.3498 | 59.8823 | 0 | 0 | 209.8855 | 0 | 0 | 0 | 0 | 2.3505 | 2.8153 | No Evaluation | -420 | 7570 | 494.3985 | 59.8844 | 0 | 0 | 211.256 | 0 | 0 | 0 | 0 | 2.365 | 2.8536 | No Evaluation | -420 | 7570 | 485.3989 | 59.8892 | 0 | 0 | 212.6609 | 0 | 0 | 0 | 0 | 2.4128 | 2.9425 | No Evaluation | -420 | 7570 | 465.4341 | 59.8879 | 0 | 0 | 212.6617 | 0 | 0 | 0 | 0 | 2.3968 | 2.9189 | No Evaluation | -420 | 7570 | 470.6329 | 59.8887 | 0 | 0 | 212.7443 | 0 | 0 | 0 | 0 | 2.4059 | 2.9334 | No Evaluation | -420 | 7570 | 467.4349