## Data
|  |  |  | Non- | [6 empty] | Event Detection | Recovery Target Freq: | Max Absolute Delta Hz | Lowest Delta Hz | Highest Delta Hz | Rows of data to shift to align T(0)
|  | Contingent | Load | Conforming | Not | Not | Not | Not | BA | BA | Row | 59.9986 | 0.07819 | -0.07819 | 0.008728 | 1
|  | Resource | Resources | Load | Used | Used | Used | Used | Bias | Load | 805 | 40679.3379 | t(0)
|  | Lost | Tripped | Load (-) |  |  |  |  | Setting |  | 921 | 40679.3406 | t(Recovery) | Delta | Absolute
Time (T) | Hz | MW | MW | MW |  |  |  |  | MW/0.1 Hz | MW | 806 | 0:04 | Event Length mm:ss | Hz | Delta Hz
2011-05-16 07:40 | 60.0097 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8516 |  | 0
2011-05-16 07:40 | 60.0074 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8516 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:40 | 60.0045 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8223 | 0 | 0 | 0 | -0.0029297 | 0.0029297
2011-05-16 07:40 | 60.0026 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8223 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:40 | 60.0003 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8223 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:40 | 59.9987 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8223 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:40 | 59.9971 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.8223 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:40 | 59.9955 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.4629 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:40 | 59.9935 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.4629 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:40 | 59.9906 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.4629 | 0 | 0 | 0 | -0.0028992 | 0.0028992
2011-05-16 07:40 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.4629 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:40 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.4629 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:40 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.373 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:40 | 59.9787 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.373 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:40 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.373 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:41 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.373 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:41 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 29766.373 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:41 | 59.9758 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9824 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:41 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9824 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:41 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9824 | 0 | 0 | 0 | -0.0015869 | 0.0015869
2011-05-16 07:41 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9824 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:41 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9824 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:41 | 59.9735 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9512 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:41 | 59.9742 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9512 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:41 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9512 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:41 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9512 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:41 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.9512 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:41 | 59.9683 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | -0.0045471 | 0.0045471
2011-05-16 07:41 | 59.9677 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:41 | 59.969 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:41 | 59.9703 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:41 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:41 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0015869 | 0.0015869
2011-05-16 07:41 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:41 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:41 | 59.9777 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0015869 | 0.0015869
2011-05-16 07:41 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 29770.3418 | 0 | 0 | 0 | 0.0022888 | 0.0022888
2011-05-16 07:41 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.7285 | 0 | 0 | 0 | 0.0032043 | 0.0032043
2011-05-16 07:41 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.7285 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:41 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.7285 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:41 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.7285 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:41 | 59.99 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.7285 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:41 | 59.9919 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.8184 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:41 | 59.9935 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.8184 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:41 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.8184 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:41 | 59.998 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.8184 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:42 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.8184 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:42 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.1523 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:42 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.1523 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:42 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.1523 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:42 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.1523 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:42 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.1523 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:42 | 59.9971 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.2109 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:42 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.2109 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:42 | 59.9984 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.2109 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:42 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.2109 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:42 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29786.2109 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:42 | 60.0006 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9824 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:42 | 60.0013 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9824 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:42 | 60.0023 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9824 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:42 | 60.0039 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9824 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:42 | 60.0065 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9824 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:42 | 60.0097 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9238 | 0 | 0 | 0 | 0.0032349 | 0.0032349
2011-05-16 07:42 | 60.0136 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9238 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 07:42 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9238 | 0 | 0 | 0 | 0.0025635 | 0.0025635
2011-05-16 07:42 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9238 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:42 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29778.9238 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:42 | 60.0149 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8965 | 0 | 0 | 0 | -0.0028992 | 0.0028992
2011-05-16 07:42 | 60.0116 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8965 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:42 | 60.009 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8965 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:42 | 60.0078 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8965 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:42 | 60.0078 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8965 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:42 | 60.009 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8379 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:42 | 60.009 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8379 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:42 | 60.0132 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8379 | 0 | 0 | 0 | 0.0042114 | 0.0042114
2011-05-16 07:43 | 60.0149 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8379 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:43 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.8379 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:43 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3887 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:43 | 60.0149 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3887 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:43 | 60.0142 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3887 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:43 | 60.0136 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3887 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:43 | 60.0123 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3887 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:43 | 60.011 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3281 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:43 | 60.0087 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3281 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:43 | 60.0065 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3281 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:43 | 60.0049 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3281 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:43 | 60.0035 | 471 |  | 0 | 0 |  |  |  | -653 | 29813.3281 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:43 | 60.002 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.457 | 0 | 0 | 0 | -0.0015869 | 0.0015869
2011-05-16 07:43 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.457 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:43 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.457 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:43 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.457 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:43 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.457 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:43 | 59.9974 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.5156 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:43 | 59.9984 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.5156 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:43 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.5156 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:43 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.5156 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:43 | 59.9987 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.5156 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:43 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.3281 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:43 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.3281 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:43 | 59.9968 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.3281 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:43 | 59.9968 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.3281 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:43 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.3281 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:43 | 59.998 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.2676 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:43 | 59.9977 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.2676 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:43 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.2676 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:44 | 59.9939 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.2676 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:44 | 59.9926 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.2676 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:44 | 59.9913 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.99 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.9897 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:44 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:44 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:44 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:44 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:44 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.6328 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:44 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:44 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:44 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:44 | 59.9851 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:44 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:44 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:44 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:44 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:44 | 59.9777 | 471 |  | 0 | 0 |  |  |  | -653 | 29787.1172 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:44 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.668 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:44 | 59.9764 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.668 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:44 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.668 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:44 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.668 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:44 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.668 | 0 | 0 | 0 | 0.0032043 | 0.0032043
2011-05-16 07:44 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.7578 | 0 | 0 | 0 | 0.0029297 | 0.0029297
2011-05-16 07:44 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.7578 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:44 | 59.9903 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.7578 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:44 | 59.9919 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.7578 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:45 | 59.9935 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.7578 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:45 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:45 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.0042114 | 0.0042114
2011-05-16 07:45 | 60.0035 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.00354 | 0.00354
2011-05-16 07:45 | 60.0065 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.0029297 | 0.0029297
2011-05-16 07:45 | 60.0084 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:45 | 60.009 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:45 | 60.0087 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:45 | 60.0087 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:45 | 60.0094 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:45 | 60.011 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.7012 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:45 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0.00354 | 0.00354
2011-05-16 07:45 | 60.0181 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0.0035706 | 0.0035706
2011-05-16 07:45 | 60.02 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:45 | 60.0204 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:45 | 60.02 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:45 | 60.02 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:45 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:45 | 60.0181 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:45 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:45 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.6309 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:45 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:45 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:45 | 60.0136 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:45 | 60.0123 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:45 | 60.0116 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:45 | 60.0107 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:45 | 60.0097 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:45 | 60.0084 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:46 | 60.0074 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:46 | 60.0078 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.5059 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0084 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.6191 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:46 | 60.0084 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.6191 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:46 | 60.0081 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.6191 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0074 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.6191 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:46 | 60.0071 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.6191 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:46 | 60.0084 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.5605 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:46 | 60.0094 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.5605 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:46 | 60.0097 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.5605 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:46 | 60.01 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.5605 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0107 | 471 |  | 0 | 0 |  |  |  | -653 | 29780.5605 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:46 | 60.012 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9629 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:46 | 60.0132 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9629 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:46 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9629 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:46 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9629 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:46 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9629 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:46 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9336 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:46 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9336 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:46 | 60.0158 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9336 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9336 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0158 | 471 |  | 0 | 0 |  |  |  | -653 | 29784.9336 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:46 | 60.0149 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:46 | 60.0142 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:46 | 60.0123 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:46 | 60.0097 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 07:46 | 60.0071 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:46 | 60.0058 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:46 | 60.0052 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:46 | 60.0052 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:46 | 60.0049 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:47 | 60.0039 | 471 |  | 0 | 0 |  |  |  | -653 | 29760.416 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:47 | 60.0026 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.3496 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:47 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.3496 | 0 | 0 | 0 | -0.0035706 | 0.0035706
2011-05-16 07:47 | 59.9971 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.3496 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:47 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.3496 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:47 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.3496 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:47 | 59.9942 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4395 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:47 | 59.9922 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4395 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:47 | 59.9903 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4395 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:47 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4395 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:47 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4395 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:47 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5234 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:47 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5234 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:47 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5234 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:47 | 59.9829 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5234 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:47 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5234 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:47 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5527 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:47 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5527 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:47 | 59.9825 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5527 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:47 | 59.9839 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5527 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:47 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29785.5527 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:47 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.2129 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:47 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.2129 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:47 | 59.99 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.2129 | 0 | 0 | 0 | 0.0035706 | 0.0035706
2011-05-16 07:47 | 59.9922 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.2129 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:47 | 59.9932 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.2129 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:47 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.0645 | 0 | 0 | 0 | 0.0032349 | 0.0032349
2011-05-16 07:47 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.0645 | 0 | 0 | 0 | 0.0025635 | 0.0025635
2011-05-16 07:47 | 60.0006 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.0645 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:48 | 60.0065 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.0645 | 0 | 0 | 0 | 0.0058289 | 0.0058289
2011-05-16 07:48 | 60.009 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.0645 | 0 | 0 | 0 | 0.0025635 | 0.0025635
2011-05-16 07:48 | 60.011 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1133 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:48 | 60.0113 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1133 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:48 | 60.0129 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1133 | 0 | 0 | 0 | 0.0015869 | 0.0015869
2011-05-16 07:48 | 60.0132 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1133 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:48 | 60.0132 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1133 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:48 | 60.0142 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1738 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:48 | 60.0181 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1738 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 07:48 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1738 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:48 | 60.0213 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1738 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:48 | 60.022 | 471 |  | 0 | 0 |  |  |  | -653 | 29776.1738 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:48 | 60.0216 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6855 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:48 | 60.0197 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6855 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:48 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6855 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:48 | 60.0175 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6855 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:48 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6855 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:48 | 60.0184 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6562 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:48 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6562 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:48 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6562 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 07:48 | 60.0139 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6562 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:48 | 60.0142 | 471 |  | 0 | 0 |  |  |  | -653 | 29794.6562 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:48 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.7754 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:48 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.7754 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:48 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.7754 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:48 | 60.0142 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.7754 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:48 | 60.012 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.7754 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:48 | 60.0103 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.8633 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:48 | 60.0081 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.8633 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:48 | 60.0061 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.8633 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:48 | 60.0052 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.8633 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:49 | 60.0045 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.8633 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:49 | 60.0035 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1191 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:49 | 60.0013 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1191 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:49 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1191 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:49 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1191 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:49 | 59.9984 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1191 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:49 | 59.9974 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1777 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:49 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1777 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:49 | 59.9951 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1777 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:49 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1777 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:49 | 59.9987 | 471 |  | 0 | 0 |  |  |  | -653 | 29800.1777 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:49 | 60.0013 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.8203 | 0 | 0 | 0 | 0.0025635 | 0.0025635
2011-05-16 07:49 | 60.0032 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.8203 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:49 | 60.0042 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.8203 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:49 | 60.0049 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.8203 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:49 | 60.0055 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.8203 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:49 | 60.0058 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.7891 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:49 | 60.0058 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.7891 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:49 | 60.0055 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.7891 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:49 | 60.0039 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.7891 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:49 | 60.0023 | 471 |  | 0 | 0 |  |  |  | -653 | 29799.7891 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:49 | 60.0023 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.6738 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:49 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.6738 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:49 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.6738 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:49 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.6738 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:49 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.6738 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:49 | 60.0045 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.5547 | 0 | 0 | 0 | 0.0045166 | 0.0045166
2011-05-16 07:49 | 60.0058 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.5547 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:49 | 60.0061 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.5547 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:50 | 60.0058 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.5547 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:50 | 60.0052 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.5547 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:50 | 60.0039 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.5293 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:50 | 60.002 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.5293 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:50 | 60.0013 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.5293 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:50 | 60.001 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.5293 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:50 | 60.0003 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.5293 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:50 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.4688 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:50 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.4688 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:50 | 59.9987 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.4688 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:50 | 59.9984 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.4688 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:50 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29783.4688 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:50 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:50 | 59.9951 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:50 | 59.9939 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:50 | 59.9922 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:50 | 59.9922 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:50 | 59.9948 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:50 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:50 | 59.9971 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:50 | 59.9955 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:50 | 59.9929 | 471 |  | 0 | 0 |  |  |  | -653 | 29788.3848 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:50 | 59.99 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.1621 | 0 | 0 | 0 | -0.0028992 | 0.0028992
2011-05-16 07:50 | 59.9877 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.1621 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:50 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.1621 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:50 | 59.9855 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.1621 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:50 | 59.9855 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.1621 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:50 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.0723 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:50 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.0723 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:50 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.0723 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:50 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.0723 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:51 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29790.0723 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:51 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:51 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:51 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:51 | 59.9829 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:51 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4863 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:51 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4941 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4941 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:51 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4941 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:51 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4941 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:51 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4941 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:51 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4629 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:51 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4629 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:51 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4629 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4629 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 29782.4629 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:51 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.125 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:51 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.125 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:51 | 59.9735 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.125 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:51 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.125 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.125 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9719 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.1836 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:51 | 59.9713 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.1836 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:51 | 59.9716 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.1836 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:52 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.1836 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:52 | 59.9742 | 471 |  | 0 | 0 |  |  |  | -653 | 29756.1836 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:52 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.5801 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:52 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.5801 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:52 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.5801 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:52 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.5801 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:52 | 59.9745 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.5801 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:52 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4023 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:52 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4023 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:52 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4023 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:52 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4023 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:52 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 29777.4023 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:52 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2422 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:52 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2422 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:52 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2422 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:52 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2422 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:52 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2422 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:52 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.1836 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:52 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.1836 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:52 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.1836 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 07:52 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.1836 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:52 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.1836 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:52 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2891 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:52 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2891 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:52 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2891 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:52 | 59.9877 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2891 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:52 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.2891 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:52 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.3203 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:52 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.3203 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:52 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.3203 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:52 | 59.9877 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.3203 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:53 | 59.989 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.3203 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9897 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0215 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:53 | 59.9893 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0215 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:53 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0215 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:53 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0215 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:53 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0215 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:53 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0527 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0527 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0527 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:53 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0527 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:53 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29795.0527 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9893 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4238 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:53 | 59.99 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4238 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:53 | 59.9913 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4238 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9926 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4238 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9939 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4238 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:53 | 59.9939 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4531 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:53 | 59.9929 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4531 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:53 | 59.991 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4531 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:53 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4531 | 0 | 0 | 0 | -0.0022888 | 0.0022888
2011-05-16 07:53 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29781.4531 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:53 | 59.9839 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4297 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 07:53 | 59.9816 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4297 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:53 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4297 | 0 | 0 | 0 | -0.0022888 | 0.0022888
2011-05-16 07:53 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4297 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 07:53 | 59.9742 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4297 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:53 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4004 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:53 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4004 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:53 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4004 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:54 | 59.9745 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4004 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:54 | 59.9735 | 471 |  | 0 | 0 |  |  |  | -653 | 29802.4004 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:54 | 59.9725 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:54 | 59.9725 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:54 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:54 | 59.9716 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:54 | 59.9719 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:54 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:54 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:54 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:54 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:54 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 29804.4023 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:54 | 59.9825 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.3242 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:54 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.3242 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:54 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.3242 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:54 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.3242 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:54 | 59.9903 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.3242 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:54 | 59.9916 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.2949 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:54 | 59.9932 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.2949 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:54 | 59.9948 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.2949 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:54 | 59.9958 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.2949 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:54 | 59.9951 | 471 |  | 0 | 0 |  |  |  | -653 | 29797.2949 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:54 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29823.7598 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:54 | 59.998 | 471 |  | 0 | 0 |  |  |  | -653 | 29823.7598 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:54 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29823.7598 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:54 | 60.0006 | 471 |  | 0 | 0 |  |  |  | -653 | 29823.7598 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:54 | 60.001 | 471 |  | 0 | 0 |  |  |  | -653 | 29823.7598 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:54 | 60.0006 | 471 |  | 0 | 0 |  |  |  | -653 | 29818.4062 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:54 | 60 | 471 |  | 0 | 0 |  |  |  | -653 | 29818.4062 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:54 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29818.4062 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:55 | 59.9987 | 471 |  | 0 | 0 |  |  |  | -653 | 29818.4062 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:55 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29818.4062 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:55 | 60.0003 | 471 |  | 0 | 0 |  |  |  | -653 | 29808.8945 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:55 | 60.0016 | 471 |  | 0 | 0 |  |  |  | -653 | 29808.8945 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:55 | 60.0035 | 471 |  | 0 | 0 |  |  |  | -653 | 29808.8945 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:55 | 60.0049 | 471 |  | 0 | 0 |  |  |  | -653 | 29808.8945 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:55 | 60.0042 | 471 |  | 0 | 0 |  |  |  | -653 | 29808.8945 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:55 | 60.002 | 471 |  | 0 | 0 |  |  |  | -653 | 29814.8906 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:55 | 59.999 | 471 |  | 0 | 0 |  |  |  | -653 | 29814.8906 | 0 | 0 | 0 | -0.0029297 | 0.0029297
2011-05-16 07:55 | 59.9965 | 471 |  | 0 | 0 |  |  |  | -653 | 29814.8906 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 07:55 | 59.9942 | 471 |  | 0 | 0 |  |  |  | -653 | 29814.8906 | 0 | 0 | 0 | -0.0022888 | 0.0022888
2011-05-16 07:55 | 59.9932 | 471 |  | 0 | 0 |  |  |  | -653 | 29814.8906 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:55 | 59.9913 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4727 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:55 | 59.9893 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4727 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:55 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4727 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:55 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4727 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:55 | 59.9855 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4727 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:55 | 59.9855 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4141 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:55 | 59.9851 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4141 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:55 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4141 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:55 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4141 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:55 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29826.4141 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:55 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29834.1777 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:55 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 29834.1777 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:55 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 29834.1777 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:55 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29834.1777 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:55 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29834.1777 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:55 | 59.9884 | 471 |  | 0 | 0 |  |  |  | -653 | 29836.1348 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:55 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29836.1348 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:55 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29836.1348 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:55 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29836.1348 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:56 | 59.9855 | 471 |  | 0 | 0 |  |  |  | -653 | 29836.1348 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 07:56 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8379 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 07:56 | 59.9877 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8379 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:56 | 59.9897 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8379 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:56 | 59.9906 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8379 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:56 | 59.9906 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8379 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9906 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8672 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9906 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8672 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8672 | 0 | 0 | 0 | -0.0042114 | 0.0042114
2011-05-16 07:56 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8672 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:56 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 29821.8672 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:56 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:56 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:56 | 59.9764 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:56 | 59.9764 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:56 | 59.9754 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:56 | 59.9758 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:56 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:56 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:56 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29831.3262 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29835.5078 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29835.5078 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:56 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29835.5078 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:56 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29835.5078 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:56 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29835.5078 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:56 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29856.5469 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:56 | 59.9787 | 471 |  | 0 | 0 |  |  |  | -653 | 29856.5469 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:56 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 29856.5469 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:57 | 59.9816 | 471 |  | 0 | 0 |  |  |  | -653 | 29856.5469 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 07:57 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 29856.5469 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 07:57 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29846.7617 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 07:57 | 59.9903 | 471 |  | 0 | 0 |  |  |  | -653 | 29846.7617 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 07:57 | 59.9945 | 471 |  | 0 | 0 |  |  |  | -653 | 29846.7617 | 0 | 0 | 0 | 0.0042114 | 0.0042114
2011-05-16 07:57 | 59.9974 | 471 |  | 0 | 0 |  |  |  | -653 | 29846.7617 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 07:57 | 59.9984 | 471 |  | 0 | 0 |  |  |  | -653 | 29846.7617 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:57 | 59.998 | 471 |  | 0 | 0 |  |  |  | -653 | 29860.0488 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:57 | 59.9968 | 471 |  | 0 | 0 |  |  |  | -653 | 29860.0488 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:57 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29860.0488 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:57 | 59.9955 | 471 |  | 0 | 0 |  |  |  | -653 | 29860.0488 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:57 | 59.9961 | 471 |  | 0 | 0 |  |  |  | -653 | 29860.0488 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:57 | 59.9994 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0032349 | 0.0032349
2011-05-16 07:57 | 60.0032 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 07:57 | 60.0074 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0042114 | 0.0042114
2011-05-16 07:57 | 60.0116 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0041809 | 0.0041809
2011-05-16 07:57 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 07:57 | 60.0175 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0029297 | 0.0029297
2011-05-16 07:57 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:57 | 60.0194 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:57 | 60.0194 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:57 | 60.0194 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.1465 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:57 | 60.0204 | 471 |  | 0 | 0 |  |  |  | -653 | 29889.6699 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:57 | 60.022 | 471 |  | 0 | 0 |  |  |  | -653 | 29889.6699 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:57 | 60.0242 | 471 |  | 0 | 0 |  |  |  | -653 | 29889.6699 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 07:57 | 60.0268 | 471 |  | 0 | 0 |  |  |  | -653 | 29889.6699 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 07:57 | 60.0281 | 471 |  | 0 | 0 |  |  |  | -653 | 29889.6699 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:57 | 60.0294 | 471 |  | 0 | 0 |  |  |  | -653 | 29886.5996 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:57 | 60.0304 | 471 |  | 0 | 0 |  |  |  | -653 | 29886.5996 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 07:57 | 60.0287 | 471 |  | 0 | 0 |  |  |  | -653 | 29886.5996 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:57 | 60.0268 | 471 |  | 0 | 0 |  |  |  | -653 | 29886.5996 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:58 | 60.0246 | 471 |  | 0 | 0 |  |  |  | -653 | 29886.5996 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:58 | 60.0226 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6738 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:58 | 60.0223 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6738 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0229 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6738 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0236 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6738 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0226 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6738 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:58 | 60.0216 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6445 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:58 | 60.0197 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6445 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:58 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6445 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:58 | 60.0175 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6445 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0168 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6445 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0171 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.5137 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0184 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.5137 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 07:58 | 60.0187 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.5137 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:58 | 60.0181 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.5137 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0168 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.5137 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 07:58 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6016 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:58 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6016 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:58 | 60.0155 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6016 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0155 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6016 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:58 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29891.6016 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:58 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29884.5 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:58 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29884.5 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 07:58 | 60.0158 | 471 |  | 0 | 0 |  |  |  | -653 | 29884.5 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29884.5 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0158 | 471 |  | 0 | 0 |  |  |  | -653 | 29884.5 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29881.793 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:58 | 60.0155 | 471 |  | 0 | 0 |  |  |  | -653 | 29881.793 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:58 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29881.793 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:59 | 60.0178 | 471 |  | 0 | 0 |  |  |  | -653 | 29881.793 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:59 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29881.793 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 07:59 | 60.0207 | 471 |  | 0 | 0 |  |  |  | -653 | 29887.1406 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 07:59 | 60.0213 | 471 |  | 0 | 0 |  |  |  | -653 | 29887.1406 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 07:59 | 60.0207 | 471 |  | 0 | 0 |  |  |  | -653 | 29887.1406 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:59 | 60.0191 | 471 |  | 0 | 0 |  |  |  | -653 | 29887.1406 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:59 | 60.0175 | 471 |  | 0 | 0 |  |  |  | -653 | 29887.1406 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:59 | 60.0161 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.0762 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 07:59 | 60.0152 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.0762 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 07:59 | 60.0145 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.0762 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 07:59 | 60.0139 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.0762 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 07:59 | 60.0136 | 471 |  | 0 | 0 |  |  |  | -653 | 29873.0762 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 07:59 | 60.011 | 471 |  | 0 | 0 |  |  |  | -653 | 29862.1016 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:59 | 60.0055 | 471 |  | 0 | 0 |  |  |  | -653 | 29862.1016 | 0 | 0 | 0 | -0.0054932 | 0.0054932
2011-05-16 07:59 | 59.9997 | 471 |  | 0 | 0 |  |  |  | -653 | 29862.1016 | 0 | 0 | 0 | -0.0058289 | 0.0058289
2011-05-16 07:59 | 59.9945 | 471 |  | 0 | 0 |  |  |  | -653 | 29862.1016 | 0 | 0 | 0 | -0.0051575 | 0.0051575
2011-05-16 07:59 | 59.9913 | 471 |  | 0 | 0 |  |  |  | -653 | 29862.1016 | 0 | 0 | 0 | -0.0032349 | 0.0032349
2011-05-16 07:59 | 59.9897 | 471 |  | 0 | 0 |  |  |  | -653 | 29861.9531 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 07:59 | 59.9887 | 471 |  | 0 | 0 |  |  |  | -653 | 29861.9531 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:59 | 59.9868 | 471 |  | 0 | 0 |  |  |  | -653 | 29861.9531 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:59 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 29861.9531 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 07:59 | 59.9829 | 471 |  | 0 | 0 |  |  |  | -653 | 29861.9531 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:59 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 29906.207 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 07:59 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29906.207 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 07:59 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29906.207 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 07:59 | 59.9758 | 471 |  | 0 | 0 |  |  |  | -653 | 29906.207 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 07:59 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29906.207 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 07:59 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29878.6875 | 0 | 0 | 0 | 0 | 0
2011-05-16 07:59 | 59.9764 | 471 |  | 0 | 0 |  |  |  | -653 | 29878.6875 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 07:59 | 59.9754 | 471 |  | 0 | 0 |  |  |  | -653 | 29878.6875 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 07:59 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29878.6875 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:00 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29878.6875 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:00 | 59.9725 | 471 |  | 0 | 0 |  |  |  | -653 | 29900.5625 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:00 | 59.9722 | 471 |  | 0 | 0 |  |  |  | -653 | 29900.5625 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:00 | 59.9725 | 471 |  | 0 | 0 |  |  |  | -653 | 29900.5625 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 08:00 | 59.9735 | 471 |  | 0 | 0 |  |  |  | -653 | 29900.5625 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:00 | 59.9735 | 471 |  | 0 | 0 |  |  |  | -653 | 29900.5625 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9732 | 471 |  | 0 | 0 |  |  |  | -653 | 29896.9863 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:00 | 59.9719 | 471 |  | 0 | 0 |  |  |  | -653 | 29896.9863 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:00 | 59.9709 | 471 |  | 0 | 0 |  |  |  | -653 | 29896.9863 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:00 | 59.9703 | 471 |  | 0 | 0 |  |  |  | -653 | 29896.9863 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:00 | 59.9703 | 471 |  | 0 | 0 |  |  |  | -653 | 29896.9863 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9703 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7988 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9703 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7988 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9706 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7988 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:00 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7988 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 08:00 | 59.9729 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7988 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7676 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 08:00 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7676 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7676 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:00 | 59.9683 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7676 | 0 | 0 | 0 | -0.0054932 | 0.0054932
2011-05-16 08:00 | 59.968 | 471 |  | 0 | 0 |  |  |  | -653 | 29905.7676 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:00 | 59.969 | 471 |  | 0 | 0 |  |  |  | -653 | 29914.8965 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:00 | 59.9699 | 471 |  | 0 | 0 |  |  |  | -653 | 29914.8965 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:00 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29914.8965 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 08:00 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29914.8965 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9738 | 471 |  | 0 | 0 |  |  |  | -653 | 29914.8965 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:00 | 59.9777 | 471 |  | 0 | 0 |  |  |  | -653 | 29925.5801 | 0 | 0 | 0 | 0.0038757 | 0.0038757
2011-05-16 08:00 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29925.5801 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:00 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29925.5801 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:01 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 29925.5801 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:01 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29925.5801 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:01 | 59.9777 | 471 |  | 0 | 0 |  |  |  | -653 | 29938.8711 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:01 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29938.8711 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:01 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29938.8711 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:01 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 29938.8711 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:01 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 29938.8711 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:01 | 59.9764 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:01 | 59.9748 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 08:01 | 59.9745 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:01 | 59.9754 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:01 | 59.9771 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:01 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 29952.5078 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 08:01 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:01 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:01 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:01 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:01 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:01 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:01 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:01 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:01 | 59.9845 | 471 |  | 0 | 0 |  |  |  | -653 | 29948.9492 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 08:01 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29951.0508 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:01 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29951.0508 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:01 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 29951.0508 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:01 | 59.9871 | 471 |  | 0 | 0 |  |  |  | -653 | 29951.0508 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 08:01 | 59.9877 | 471 |  | 0 | 0 |  |  |  | -653 | 29951.0508 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:01 | 59.9897 | 471 |  | 0 | 0 |  |  |  | -653 | 29955.0879 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 08:01 | 59.9916 | 471 |  | 0 | 0 |  |  |  | -653 | 29955.0879 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 08:01 | 59.9926 | 471 |  | 0 | 0 |  |  |  | -653 | 29955.0879 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:02 | 59.9932 | 471 |  | 0 | 0 |  |  |  | -653 | 29955.0879 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 08:02 | 59.9929 | 471 |  | 0 | 0 |  |  |  | -653 | 29955.0879 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:02 | 59.991 | 471 |  | 0 | 0 |  |  |  | -653 | 29967.6875 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 08:02 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 29967.6875 | 0 | 0 | 0 | -0.0029297 | 0.0029297
2011-05-16 08:02 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 29967.6875 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 08:02 | 59.9839 | 471 |  | 0 | 0 |  |  |  | -653 | 29967.6875 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 08:02 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 29967.6875 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 08:02 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 29983.1328 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:02 | 59.9829 | 471 |  | 0 | 0 |  |  |  | -653 | 29983.1328 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:02 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29983.1328 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 08:02 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 29983.1328 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:02 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 29983.1328 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:02 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7539 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:02 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7539 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:02 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7539 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 08:02 | 59.9839 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7539 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:02 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7539 | 0 | 0 | 0 | -0.002594 | 0.002594
2011-05-16 08:02 | 59.9754 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7832 | 0 | 0 | 0 | -0.0058289 | 0.0058289
2011-05-16 08:02 | 59.9683 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7832 | 0 | 0 | 0 | -0.0071106 | 0.0071106
2011-05-16 08:02 | 59.9635 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7832 | 0 | 0 | 0 | -0.0048218 | 0.0048218
2011-05-16 08:02 | 59.9615 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7832 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 08:02 | 59.9609 | 471 |  | 0 | 0 |  |  |  | -653 | 29976.7832 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:02 | 59.9615 | 471 |  | 0 | 0 |  |  |  | -653 | 30008.5137 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:02 | 59.9606 | 471 |  | 0 | 0 |  |  |  | -653 | 30008.5137 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:02 | 59.958 | 471 |  | 0 | 0 |  |  |  | -653 | 30008.5137 | 0 | 0 | 0 | -0.0025635 | 0.0025635
2011-05-16 08:02 | 59.9557 | 471 |  | 0 | 0 |  |  |  | -653 | 30008.5137 | 0 | 0 | 0 | -0.0022583 | 0.0022583
2011-05-16 08:02 | 59.9557 | 471 |  | 0 | 0 |  |  |  | -653 | 30008.5137 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:02 | 59.957 | 471 |  | 0 | 0 |  |  |  | -653 | 30037.2461 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:02 | 59.959 | 471 |  | 0 | 0 |  |  |  | -653 | 30037.2461 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 08:02 | 59.9606 | 471 |  | 0 | 0 |  |  |  | -653 | 30037.2461 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:02 | 59.9615 | 471 |  | 0 | 0 |  |  |  | -653 | 30037.2461 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9625 | 471 |  | 0 | 0 |  |  |  | -653 | 30037.2461 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9641 | 471 |  | 0 | 0 |  |  |  | -653 | 30055.7324 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:03 | 59.9651 | 471 |  | 0 | 0 |  |  |  | -653 | 30055.7324 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9651 | 471 |  | 0 | 0 |  |  |  | -653 | 30055.7324 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:03 | 59.9658 | 471 |  | 0 | 0 |  |  |  | -653 | 30055.7324 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:03 | 59.967 | 471 |  | 0 | 0 |  |  |  | -653 | 30055.7324 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:03 | 59.9699 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.7559 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 08:03 | 59.9725 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.7559 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 08:03 | 59.9742 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.7559 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:03 | 59.9761 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.7559 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 08:03 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.7559 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:03 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.207 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 08:03 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.207 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.207 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:03 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.207 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:03 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.207 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:03 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.2383 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 08:03 | 59.9784 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.2383 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:03 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.2383 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:03 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.2383 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30068.2383 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 08:03 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 30076.1953 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:03 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 30076.1953 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:03 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 30076.1953 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 08:03 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 30076.1953 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:03 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30076.1953 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:03 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 30093.9512 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:03 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30093.9512 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:03 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 30093.9512 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 08:04 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 30093.9512 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 08:04 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30093.9512 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 08:04 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30100.9707 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:04 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30100.9707 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:04 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30100.9707 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:04 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30100.9707 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:04 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 30100.9707 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:04 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.8652 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:04 | 59.9787 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.8652 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:04 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.8652 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:04 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.8652 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 08:04 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.8652 | 0 | 0 | 0 | 0.0025635 | 0.0025635
2011-05-16 08:04 | 59.9851 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7676 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:04 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7676 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:04 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7676 | 0 | 0 | 0 | -0.0019226 | 0.0019226
2011-05-16 08:04 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7676 | 0 | 0 | 0 | -0.0019531 | 0.0019531
2011-05-16 08:04 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7676 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:04 | 59.9787 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7363 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:04 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7363 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:04 | 59.98 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7363 | 0 | 0 | 0 | 0.00067139 | 0.00067139
2011-05-16 08:04 | 59.9793 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7363 | 0 | 0 | 0 | -0.00067139 | 0.00067139
2011-05-16 08:04 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30118.7363 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:04 | 59.978 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.9336 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:04 | 59.9767 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.9336 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:04 | 59.9774 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.9336 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:04 | 59.979 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.9336 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:04 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.9336 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:04 | 59.9809 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.6074 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:04 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.6074 | 0 | 0 | 0 | 0.0013123 | 0.0013123
2011-05-16 08:04 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.6074 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:04 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.6074 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 30106.6074 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 08:05 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 30116.0176 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:05 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 30116.0176 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 30116.0176 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9816 | 471 |  | 0 | 0 |  |  |  | -653 | 30116.0176 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:05 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 30116.0176 | 0 | 0 | 0 | 0.00030518 | 0.00030518
2011-05-16 08:05 | 59.9816 | 471 |  | 0 | 0 |  |  |  | -653 | 30141.5898 | 0 | 0 | 0 | -0.00030518 | 0.00030518
2011-05-16 08:05 | 59.9813 | 471 |  | 0 | 0 |  |  |  | -653 | 30141.5898 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:05 | 59.9816 | 471 |  | 0 | 0 |  |  |  | -653 | 30141.5898 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:05 | 59.9825 | 471 |  | 0 | 0 |  |  |  | -653 | 30141.5898 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:05 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 30141.5898 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:05 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:05 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9842 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9851 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:05 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 08:05 | 59.989 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:05 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:05 | 59.9864 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 08:05 | 59.9829 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | -0.00354 | 0.00354
2011-05-16 08:05 | 59.9825 | 471 |  | 0 | 0 |  |  |  | -653 | 30144.2285 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:05 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 30148.6699 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:05 | 59.9819 | 471 |  | 0 | 0 |  |  |  | -653 | 30148.6699 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:05 | 59.9806 | 471 |  | 0 | 0 |  |  |  | -653 | 30148.6699 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:05 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30148.6699 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:05 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30148.6699 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9796 | 471 |  | 0 | 0 |  |  |  | -653 | 30155.6719 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:05 | 59.9803 | 471 |  | 0 | 0 |  |  |  | -653 | 30155.6719 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:05 | 59.9822 | 471 |  | 0 | 0 |  |  |  | -653 | 30155.6719 | 0 | 0 | 0 | 0.0019531 | 0.0019531
2011-05-16 08:06 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 30155.6719 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:06 | 59.9858 | 471 |  | 0 | 0 |  |  |  | -653 | 30155.6719 | 0 | 0 | 0 | 0.0022583 | 0.0022583
2011-05-16 08:06 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 30142.791 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:06 | 59.988 | 471 |  | 0 | 0 |  |  |  | -653 | 30142.791 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9874 | 471 |  | 0 | 0 |  |  |  | -653 | 30142.791 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9861 | 471 |  | 0 | 0 |  |  |  | -653 | 30142.791 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:06 | 59.9848 | 471 |  | 0 | 0 |  |  |  | -653 | 30142.791 | 0 | 0 | 0 | -0.0013123 | 0.0013123
2011-05-16 08:06 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 30154.666 | 0 | 0 | 0 | -0.0012817 | 0.0012817
2011-05-16 08:06 | 59.9832 | 471 |  | 0 | 0 |  |  |  | -653 | 30154.666 | 0 | 0 | 0 | -0.00033569 | 0.00033569
2011-05-16 08:06 | 59.9835 | 471 |  | 0 | 0 |  |  |  | -653 | 30154.666 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:06 | 59.9842 | 471.3 |  | 0 | 0 |  |  |  | -653 | 30150.3477 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9851 | 471.3 |  | 0 | 0 |  |  |  | -653 | 30150.3477 | 0 | 0 | 0 | 0.00097656 | 0.00097656
2011-05-16 08:06 | 59.9855 | 471.3 |  | 0 | 0 |  |  |  | -653 | 30159.6348 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:06 | 59.9864 | 471.3 |  | 0 | 0 |  |  |  | -653 | 30159.6348 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:06 | 59.9868 | 471.9 |  | 0 | 0 |  |  |  | -653 | 30159.6348 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:06 | 59.9874 | 471.9 |  | 0 | 0 |  |  |  | -653 | 30159.6348 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9877 | 471.9 |  | 0 | 0 |  |  |  | -653 | 30151.416 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:06 | 59.989 | 471.9 |  | 0 | 0 |  |  |  | -653 | 30151.416 | 0 | 0 | 0 | 0.0012817 | 0.0012817
2011-05-16 08:06 | 59.989 | 471.9 |  | 0 | 0 |  |  |  | -653 | 30156.1621 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:06 | 59.988 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30156.1621 | 0 | 0 | 0 | -0.00097656 | 0.00097656
2011-05-16 08:06 | 59.9864 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30156.1621 | 0 | 0 | 0 | -0.0016174 | 0.0016174
2011-05-16 08:06 | 59.9855 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30156.1621 | 0 | 0 | 0 | -0.00094604 | 0.00094604
2011-05-16 08:06 | 59.9864 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30164.1465 | 0 | 0 | 0 | 0.00094604 | 0.00094604
2011-05-16 08:06 | 59.9893 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30164.1465 | 0 | 0 | 0 | 0.0029297 | 0.0029297
2011-05-16 08:06 | 59.9922 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30164.1465 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 08:06 | 59.9951 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30164.1465 | 0 | 0 | 0 | 0.0028992 | 0.0028992
2011-05-16 08:06 | 59.9958 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30203.9062 | 0 | 0 | 0 | 0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9951 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30203.9062 | 0 | 0 | 0 | -0.00064087 | 0.00064087
2011-05-16 08:06 | 59.9955 | 471.4 |  | 0 | 0 |  |  |  | -653 | 30203.7285 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:06 | 59.9974 | 470.9 |  | 0 | 0 |  |  |  | -653 | 30203.7285 | 0 | 0 | 0 | 0.0019226 | 0.0019226
2011-05-16 08:06 | 60 | 470.9 |  | 0 | 0 |  |  |  | -653 | 30203.7285 | 0 | 0 | 0 | 0.002594 | 0.002594
2011-05-16 08:07 | 60.0016 | 470.9 |  | 0 | 0 |  |  |  | -653 | 30203.7285 | 0 | 0 | 0 | 0.0016174 | 0.0016174
2011-05-16 08:07 | 60.0016 | 470.9 |  | 0 | 0 |  |  |  | -653 | 30199.6055 | 0 | 0 | 0 | 0 | 0
2011-05-16 08:07 | 60.002 | 470.9 |  | 0 | 0 |  |  |  | -653 | 30199.6055 | 0 | 0 | 0 | 0.00033569 | 0.00033569
2011-05-16 08:07 | 59.9596 | 0 |  | 0 | 0 |  |  |  | -653 | 30199.6055 | 0 | 0 | 1 | -0.042328 | 0.042328
2011-05-16 08:07 | 59.8814 | 0 |  | 0 | 0 |  |  |  | -653 | 30199.6055 | 1 | 0 | 1 | -0.07819 | 0.07819
2011-05-16 08:07 | 59.8724 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1094 | 1 | 0 | 1 | -0.0090637 | 0.0090637
2011-05-16 08:07 | 59.8701 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1094 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:07 | 59.8743 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1387 | 1 | 0 | 1 | 0.0042114 | 0.0042114
2011-05-16 08:07 | 59.8808 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1387 | 1 | 0 | 1 | 0.0064392 | 0.0064392
2011-05-16 08:07 | 59.8853 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1387 | 1 | 0 | 1 | 0.0045471 | 0.0045471
2011-05-16 08:07 | 59.8879 | 0 |  | 0 | 0 |  |  |  | -653 | 30086.1387 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:07 | 59.8895 | 0 |  | 0 | 0 |  |  |  | -653 | 30094.4258 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:07 | 59.8908 | 0 |  | 0 | 0 |  |  |  | -653 | 30094.4258 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:07 | 59.8918 | 0 |  | 0 | 0 |  |  |  | -653 | 30094.4258 | 1 | 0 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:07 | 59.8924 | 0 |  | 0 | 0 |  |  |  | -653 | 30094.4258 | 1 | 0 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:07 | 59.8931 | 0 |  | 0 | 0 |  |  |  | -653 | 30139.4863 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:07 | 59.8931 | 0 |  | 0 | 0 |  |  |  | -653 | 30139.4863 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:07 | 59.8931 | 0 |  | 0 | 0 |  |  |  | -653 | 30133.375 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:07 | 59.8953 | 0 |  | 0 | 0 |  |  |  | -653 | 30133.375 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:07 | 59.8979 | 0 |  | 0 | 0 |  |  |  | -653 | 30133.375 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:07 | 59.8995 | 0 |  | 0 | 0 |  |  |  | -653 | 30133.375 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:07 | 59.9008 | 0 |  | 0 | 0 |  |  |  | -653 | 30137.2637 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:07 | 59.9021 | 0 |  | 0 | 0 |  |  |  | -653 | 30137.2637 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:07 | 59.9018 | 0 |  | 0 | 0 |  |  |  | -653 | 30137.2637 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:07 | 59.9008 | 0 |  | 0 | 0 |  |  |  | -653 | 30137.2637 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:07 | 59.9008 | 0 |  | 0 | 0 |  |  |  | -653 | 30171.375 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:07 | 59.9005 | 0 |  | 0 | 0 |  |  |  | -653 | 30171.375 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:07 | 59.8992 | 0 |  | 0 | 0 |  |  |  | -653 | 30168.7637 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:07 | 59.8989 | 0 |  | 0 | 0 |  |  |  | -653 | 30168.7637 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:08 | 59.8986 | 0 |  | 0 | 0 |  |  |  | -653 | 30168.7637 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:08 | 59.9002 | 0 |  | 0 | 0 |  |  |  | -653 | 30168.7637 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:08 | 59.9024 | 0 |  | 0 | 0 |  |  |  | -653 | 30208.9941 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9047 | 0 |  | 0 | 0 |  |  |  | -653 | 30208.9941 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9069 | 0 |  | 0 | 0 |  |  |  | -653 | 30208.9941 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9089 | 0 |  | 0 | 0 |  |  |  | -653 | 30208.9941 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:08 | 59.9092 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6641 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:08 | 59.9086 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6641 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:08 | 59.9089 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6582 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:08 | 59.9102 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6582 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:08 | 59.9124 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6582 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9147 | 0 |  | 0 | 0 |  |  |  | -653 | 30205.6582 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9176 | 0 |  | 0 | 0 |  |  |  | -653 | 30211.7539 | 1 | 0 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:08 | 59.9192 | 0 |  | 0 | 0 |  |  |  | -653 | 30211.7539 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:08 | 59.9208 | 0 |  | 0 | 0 |  |  |  | -653 | 30211.7539 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:08 | 59.9221 | 0 |  | 0 | 0 |  |  |  | -653 | 30211.7539 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:08 | 59.9231 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5488 | 1 | 0 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:08 | 59.925 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5488 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:08 | 59.925 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5664 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:08 | 59.9273 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5664 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9325 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5664 | 1 | 0 | 1 | 0.0051575 | 0.0051575
2011-05-16 08:08 | 59.9351 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5664 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:08 | 59.937 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5938 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:08 | 59.9377 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5938 | 1 | 0 | 1 | 0.00064468 | 0.00064468
2011-05-16 08:08 | 59.9393 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5938 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:08 | 59.9418 | 0 |  | 0 | 0 |  |  |  | -653 | 30217.5938 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:08 | 59.9441 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.4863 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9457 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.4863 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:08 | 59.948 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.2559 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:08 | 59.9477 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.2559 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:08 | 59.9454 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.2559 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:09 | 59.9444 | 0 |  | 0 | 0 |  |  |  | -653 | 30210.2559 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9441 | 0 |  | 0 | 0 |  |  |  | -653 | 30234.5859 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:09 | 59.9451 | 0 |  | 0 | 0 |  |  |  | -653 | 30234.5859 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:09 | 59.946 | 0 |  | 0 | 0 |  |  |  | -653 | 30234.5859 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9464 | 0 |  | 0 | 0 |  |  |  | -653 | 30234.5859 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:09 | 59.9473 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.5996 | 1 | 0 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:09 | 59.9483 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.5996 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9489 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.7305 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:09 | 59.9499 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.7305 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9509 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.7305 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9515 | 0 |  | 0 | 0 |  |  |  | -653 | 30223.7305 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:09 | 59.9519 | 0 |  | 0 | 0 |  |  |  | -653 | 30224.3926 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:09 | 59.9535 | 0 |  | 0 | 0 |  |  |  | -653 | 30224.3926 | 1 | 0 | 1 | 0.0015869 | 0.0015869
2011-05-16 08:09 | 59.9551 | 0 |  | 0 | 0 |  |  |  | -653 | 30224.3926 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:09 | 59.9557 | 0 |  | 0 | 0 |  |  |  | -653 | 30224.3926 | 1 | 0 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:09 | 59.9564 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.5293 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:09 | 59.958 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.5293 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:09 | 59.9612 | 0 |  | 0 | 0 |  |  |  | -653 | 30252.8672 | 1 | 0 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:09 | 59.9625 | 0 |  | 0 | 0 |  |  |  | -653 | 30252.8672 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:09 | 59.9619 | 0 |  | 0 | 0 |  |  |  | -653 | 30252.8672 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:09 | 59.9612 | 0 |  | 0 | 0 |  |  |  | -653 | 30252.8672 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:09 | 59.9603 | 0 |  | 0 | 0 |  |  |  | -653 | 30232.4492 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:09 | 59.9606 | 0 |  | 0 | 0 |  |  |  | -653 | 30232.4492 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:09 | 59.9622 | 0 |  | 0 | 0 |  |  |  | -653 | 30232.4492 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:09 | 59.9651 | 0 |  | 0 | 0 |  |  |  | -653 | 30232.4492 | 1 | 0 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:09 | 59.9674 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.9902 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:09 | 59.969 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.9902 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:09 | 59.9706 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.6836 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:09 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.6836 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:10 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.6836 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9729 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.6836 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:10 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30264.9609 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30264.9609 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:10 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30264.9609 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:10 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30264.9609 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:10 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.625 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30263.625 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30279.3887 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:10 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30279.3887 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:10 | 59.9793 | 0 |  | 0 | 0 |  |  |  | -653 | 30279.3887 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:10 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 30279.3887 | 1 | 0 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:10 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.3184 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:10 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.3184 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:10 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.3184 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:10 | 59.9809 | 0 |  | 0 | 0 |  |  |  | -653 | 30255.3184 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:10 | 59.9822 | 0 |  | 0 | 0 |  |  |  | -653 | 30260.6738 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:10 | 59.9839 | 0 |  | 0 | 0 |  |  |  | -653 | 30260.6738 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:10 | 59.9851 | 0 |  | 0 | 0 |  |  |  | -653 | 30259.9922 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:10 | 59.9877 | 0 |  | 0 | 0 |  |  |  | -653 | 30259.9922 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:10 | 59.9903 | 0 |  | 0 | 0 |  |  |  | -653 | 30259.9922 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:10 | 59.9929 | 0 |  | 0 | 0 |  |  |  | -653 | 30259.9922 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:10 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30274.0801 | 1 | 0 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:10 | 59.9965 | 0 |  | 0 | 0 |  |  |  | -653 | 30274.0801 | 1 | 0 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:10 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30274.0801 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:10 | 59.9961 | 0 |  | 0 | 0 |  |  |  | -653 | 30274.0801 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6777 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:10 | 59.9948 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6777 | 1 | 0 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:10 | 59.9948 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6484 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:10 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6484 | 1 | 0 | 1 | 0.0032043 | 0.0032043
2011-05-16 08:10 | 59.9987 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6484 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:11 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30297.6484 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:11 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30300.1035 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:11 | 60.0026 | 0 |  | 0 | 0 |  |  |  | -653 | 30300.1035 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:11 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30300.1035 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:11 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30300.1035 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:11 | 60.0006 | 0 |  | 0 | 0 |  |  |  | -653 | 30314.8379 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:11 | 59.9965 | 0 |  | 0 | 0 |  |  |  | -653 | 30314.8379 | 1 | 0 | 1 | -0.0041809 | 0.0041809
2011-05-16 08:11 | 59.9919 | 0 |  | 0 | 0 |  |  |  | -653 | 30309.709 | 1 | 0 | 1 | -0.0045471 | 0.0045471
2011-05-16 08:11 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 30309.709 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:11 | 59.9877 | 0 |  | 0 | 0 |  |  |  | -653 | 30309.709 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:11 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 30309.709 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:11 | 59.9926 | 0 |  | 0 | 0 |  |  |  | -653 | 30319.4961 | 1 | 0 | 1 | 0.00354 | 0.00354
2011-05-16 08:11 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30319.4961 | 1 | 0 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:11 | 59.999 | 0 |  | 0 | 0 |  |  |  | -653 | 30319.4961 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:11 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30319.4961 | 1 | 1 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:11 | 60.0049 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.2129 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:11 | 60.0081 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.2129 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:11 | 60.0116 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.1836 | 1 | 1 | 1 | 0.00354 | 0.00354
2011-05-16 08:11 | 60.0142 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.1836 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:11 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.1836 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:11 | 60.0155 | 0 |  | 0 | 0 |  |  |  | -653 | 30357.1836 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:11 | 60.0155 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.2578 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:11 | 60.0168 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.2578 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:11 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.2578 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:11 | 60.0229 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.2578 | 1 | 1 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:11 | 60.0262 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.4844 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:11 | 60.0297 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.4844 | 1 | 1 | 1 | 0.00354 | 0.00354
2011-05-16 08:11 | 60.0326 | 0 |  | 0 | 0 |  |  |  | -653 | 30353.832 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:11 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30353.832 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:11 | 60.0352 | 0 |  | 0 | 0 |  |  |  | -653 | 30353.832 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:12 | 60.0342 | 0 |  | 0 | 0 |  |  |  | -653 | 30353.832 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:12 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30370.4141 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:12 | 60.0352 | 0 |  | 0 | 0 |  |  |  | -653 | 30370.4141 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:12 | 60.0381 | 0 |  | 0 | 0 |  |  |  | -653 | 30370.4141 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:12 | 60.0404 | 0 |  | 0 | 0 |  |  |  | -653 | 30370.4141 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:12 | 60.041 | 0 |  | 0 | 0 |  |  |  | -653 | 30374.7871 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:12 | 60.042 | 0 |  | 0 | 0 |  |  |  | -653 | 30374.7871 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:12 | 60.0423 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.1367 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:12 | 60.0433 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.1367 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:12 | 60.0443 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.1367 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:12 | 60.0449 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.1367 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:12 | 60.0456 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.5332 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:12 | 60.0459 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.5332 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:12 | 60.0465 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.5332 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:12 | 60.0488 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.5332 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:12 | 60.0497 | 0 |  | 0 | 0 |  |  |  | -653 | 30343.4648 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:12 | 60.0491 | 0 |  | 0 | 0 |  |  |  | -653 | 30343.4648 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:12 | 60.0491 | 0 |  | 0 | 0 |  |  |  | -653 | 30335.1191 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:12 | 60.0504 | 0 |  | 0 | 0 |  |  |  | -653 | 30335.1191 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:12 | 60.0497 | 0 |  | 0 | 0 |  |  |  | -653 | 30335.1191 | 1 | 1 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:12 | 60.0485 | 0 |  | 0 | 0 |  |  |  | -653 | 30335.1191 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:12 | 60.0472 | 0 |  | 0 | 0 |  |  |  | -653 | 30337.2852 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:12 | 60.0459 | 0 |  | 0 | 0 |  |  |  | -653 | 30337.2852 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:12 | 60.0459 | 0 |  | 0 | 0 |  |  |  | -653 | 30337.2852 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:12 | 60.0456 | 0 |  | 0 | 0 |  |  |  | -653 | 30337.2852 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:12 | 60.0443 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.1973 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:12 | 60.043 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.1973 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:12 | 60.0417 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.0664 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:12 | 60.0423 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.0664 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:13 | 60.0446 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.0664 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:13 | 60.0465 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.0664 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:13 | 60.0472 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.7734 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:13 | 60.0462 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.7734 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:13 | 60.0443 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.7734 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:13 | 60.0449 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.7734 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:13 | 60.0452 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:13 | 60.0452 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:13 | 60.0456 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:13 | 60.0462 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:13 | 60.0465 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:13 | 60.0465 | 0 |  | 0 | 0 |  |  |  | -653 | 30372.3848 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:13 | 60.0452 | 0 |  | 0 | 0 |  |  |  | -653 | 30349.0977 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:13 | 60.0436 | 0 |  | 0 | 0 |  |  |  | -653 | 30349.0977 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:13 | 60.042 | 0 |  | 0 | 0 |  |  |  | -653 | 30349.0977 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:13 | 60.0407 | 0 |  | 0 | 0 |  |  |  | -653 | 30349.0977 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:13 | 60.0388 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.6484 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:13 | 60.0359 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.6484 | 1 | 1 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:13 | 60.0339 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.8789 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:13 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.8789 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:13 | 60.0326 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.8789 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:13 | 60.0301 | 0 |  | 0 | 0 |  |  |  | -653 | 30363.8789 | 1 | 1 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:13 | 60.0275 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.7676 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:13 | 60.0268 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.7676 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:13 | 60.0258 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.7676 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:13 | 60.0236 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.7676 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:13 | 60.022 | 0 |  | 0 | 0 |  |  |  | -653 | 30374.332 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:13 | 60.0216 | 0 |  | 0 | 0 |  |  |  | -653 | 30374.332 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:13 | 60.0223 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.6738 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:13 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.6738 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:13 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.6738 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:14 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 30364.6738 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:14 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.5586 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:14 | 60.0158 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.5586 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:14 | 60.0129 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.5586 | 1 | 1 | 1 | -0.0029297 | 0.0029297
2011-05-16 08:14 | 60.0113 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.5586 | 1 | 1 | 1 | -0.0015869 | 0.0015869
2011-05-16 08:14 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.6875 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:14 | 60.0094 | 0 |  | 0 | 0 |  |  |  | -653 | 30350.6875 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:14 | 60.0078 | 0 |  | 0 | 0 |  |  |  | -653 | 30344.5234 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:14 | 60.0052 | 0 |  | 0 | 0 |  |  |  | -653 | 30344.5234 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:14 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30344.5234 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:14 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30344.5234 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:14 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.3652 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:14 | 60.0055 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.3652 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:14 | 60.0052 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.3652 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:14 | 60.0039 | 0 |  | 0 | 0 |  |  |  | -653 | 30354.3652 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:14 | 60.0026 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.3066 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:14 | 60.0013 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.3066 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:14 | 60.0013 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.7793 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:14 | 60.0006 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.7793 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:14 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.7793 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:14 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.7793 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:14 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.334 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:14 | 60.0068 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.334 | 1 | 1 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:14 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.334 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:14 | 60.0129 | 0 |  | 0 | 0 |  |  |  | -653 | 30366.334 | 1 | 1 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:14 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.8457 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:14 | 60.0145 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.8457 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:14 | 60.0142 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.0469 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:14 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.0469 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:15 | 60.0161 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.0469 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:15 | 60.0168 | 0 |  | 0 | 0 |  |  |  | -653 | 30373.0469 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:15 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30369.7695 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0171 | 0 |  | 0 | 0 |  |  |  | -653 | 30369.7695 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:15 | 60.0168 | 0 |  | 0 | 0 |  |  |  | -653 | 30369.7695 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:15 | 60.0165 | 0 |  | 0 | 0 |  |  |  | -653 | 30369.7695 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:15 | 60.0161 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.9941 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:15 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.9941 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:15 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.1582 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:15 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.1582 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:15 | 60.0165 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.1582 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:15 | 60.0158 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.1582 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0165 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9375 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0158 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9375 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0136 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9375 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:15 | 60.0116 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9375 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:15 | 60.0113 | 0 |  | 0 | 0 |  |  |  | -653 | 30371.8516 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:15 | 60.0113 | 0 |  | 0 | 0 |  |  |  | -653 | 30371.8516 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:15 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30362.6523 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:15 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30362.6523 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:15 | 60.0129 | 0 |  | 0 | 0 |  |  |  | -653 | 30362.6523 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:15 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30362.6523 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:15 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30395.4648 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:15 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30395.4648 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:15 | 60.0184 | 0 |  | 0 | 0 |  |  |  | -653 | 30395.4648 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0181 | 0 |  | 0 | 0 |  |  |  | -653 | 30395.4648 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:15 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30397.0254 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:15 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30397.0254 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:15 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30396.666 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:15 | 60.0139 | 0 |  | 0 | 0 |  |  |  | -653 | 30396.666 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:15 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30396.666 | 1 | 1 | 1 | 0.0035706 | 0.0035706
2011-05-16 08:16 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30396.666 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:16 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.6152 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:16 | 60.0204 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.6152 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:16 | 60.0187 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.6152 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:16 | 60.0187 | 0 |  | 0 | 0 |  |  |  | -653 | 30388.6152 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:16 | 60.0197 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.7754 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:16 | 60.0197 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.7754 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:16 | 60.0197 | 0 |  | 0 | 0 |  |  |  | -653 | 30382.959 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:16 | 60.0184 | 0 |  | 0 | 0 |  |  |  | -653 | 30382.959 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:16 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30382.959 | 1 | 1 | 1 | -0.00354 | 0.00354
2011-05-16 08:16 | 60.0136 | 0 |  | 0 | 0 |  |  |  | -653 | 30382.959 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:16 | 60.0139 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.4824 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:16 | 60.0123 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.4824 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:16 | 60.01 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.4824 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:16 | 60.0058 | 0 |  | 0 | 0 |  |  |  | -653 | 30381.4824 | 1 | 1 | 1 | -0.0041809 | 0.0041809
2011-05-16 08:16 | 60.0016 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0293 | 1 | 1 | 1 | -0.0042114 | 0.0042114
2011-05-16 08:16 | 60.0016 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0293 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:16 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0703 | 1 | 0 | 1 | -0.0035706 | 0.0035706
2011-05-16 08:16 | 59.9935 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0703 | 1 | 0 | 1 | -0.0045166 | 0.0045166
2011-05-16 08:16 | 59.9926 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0703 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:16 | 59.9922 | 0 |  | 0 | 0 |  |  |  | -653 | 30394.0703 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:16 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9102 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:16 | 59.9884 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9102 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:16 | 59.9842 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9102 | 1 | 0 | 1 | -0.0042114 | 0.0042114
2011-05-16 08:16 | 59.9816 | 0 |  | 0 | 0 |  |  |  | -653 | 30376.9102 | 1 | 0 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:16 | 59.9809 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.957 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:16 | 59.9803 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.957 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:16 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.457 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:16 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.457 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:17 | 59.9751 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.457 | 1 | 0 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:17 | 59.9729 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.457 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:17 | 59.9719 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.1777 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:17 | 59.9716 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.1777 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:17 | 59.9738 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.1777 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:17 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30361.1777 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:17 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.5918 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:17 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.5918 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:17 | 59.9745 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.1934 | 1 | 0 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:17 | 59.9713 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.1934 | 1 | 0 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:17 | 59.9709 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.1934 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:17 | 59.9729 | 0 |  | 0 | 0 |  |  |  | -653 | 30365.1934 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:17 | 59.9745 | 0 |  | 0 | 0 |  |  |  | -653 | 30375.9121 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:17 | 59.9738 | 0 |  | 0 | 0 |  |  |  | -653 | 30375.9121 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:17 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30375.9121 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:17 | 59.9745 | 0 |  | 0 | 0 |  |  |  | -653 | 30375.9121 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:17 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.4023 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:17 | 59.9774 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.4023 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:17 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.7207 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:17 | 59.9777 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.7207 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:17 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.7207 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:17 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30367.7207 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:17 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30416.8711 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:17 | 59.9738 | 0 |  | 0 | 0 |  |  |  | -653 | 30416.8711 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:17 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30416.8711 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:17 | 59.9722 | 0 |  | 0 | 0 |  |  |  | -653 | 30416.8711 | 1 | 0 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:17 | 59.9719 | 0 |  | 0 | 0 |  |  |  | -653 | 30413.6465 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:17 | 59.9709 | 0 |  | 0 | 0 |  |  |  | -653 | 30413.6465 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:17 | 59.9699 | 0 |  | 0 | 0 |  |  |  | -653 | 30406.3008 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:17 | 59.9683 | 0 |  | 0 | 0 |  |  |  | -653 | 30406.3008 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:17 | 59.9661 | 0 |  | 0 | 0 |  |  |  | -653 | 30406.3008 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:18 | 59.9654 | 0 |  | 0 | 0 |  |  |  | -653 | 30406.3008 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:18 | 59.9661 | 0 |  | 0 | 0 |  |  |  | -653 | 30418.5879 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:18 | 59.9693 | 0 |  | 0 | 0 |  |  |  | -653 | 30418.5879 | 1 | 0 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:18 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30418.5879 | 1 | 0 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:18 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30418.5879 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:18 | 59.9738 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:18 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:18 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:18 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:18 | 59.9677 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | -0.0048523 | 0.0048523
2011-05-16 08:18 | 59.9713 | 0 |  | 0 | 0 |  |  |  | -653 | 30433.3145 | 1 | 0 | 1 | 0.0035706 | 0.0035706
2011-05-16 08:18 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.2969 | 1 | 0 | 1 | 0.0045166 | 0.0045166
2011-05-16 08:18 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.2969 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:18 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.2969 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:18 | 59.9842 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.2969 | 1 | 0 | 1 | 0.0083923 | 0.0083923
2011-05-16 08:18 | 59.9819 | 0 |  | 0 | 0 |  |  |  | -653 | 30425.7402 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:18 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 30425.7402 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:18 | 59.9777 | 0 |  | 0 | 0 |  |  |  | -653 | 30419.1836 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:18 | 59.9777 | 0 |  | 0 | 0 |  |  |  | -653 | 30419.1836 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:18 | 59.9813 | 0 |  | 0 | 0 |  |  |  | -653 | 30419.1836 | 1 | 0 | 1 | 0.0035706 | 0.0035706
2011-05-16 08:18 | 59.9848 | 0 |  | 0 | 0 |  |  |  | -653 | 30419.1836 | 1 | 0 | 1 | 0.00354 | 0.00354
2011-05-16 08:18 | 59.9887 | 0 |  | 0 | 0 |  |  |  | -653 | 30424.293 | 1 | 0 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:18 | 59.9916 | 0 |  | 0 | 0 |  |  |  | -653 | 30424.293 | 1 | 0 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:18 | 59.9935 | 0 |  | 0 | 0 |  |  |  | -653 | 30424.293 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:18 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30424.293 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:18 | 59.9968 | 0 |  | 0 | 0 |  |  |  | -653 | 30440.8223 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:18 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30440.8223 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:18 | 59.9984 | 0 |  | 0 | 0 |  |  |  | -653 | 30431.5801 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:18 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30431.5801 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:19 | 59.9971 | 0 |  | 0 | 0 |  |  |  | -653 | 30431.5801 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:19 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30431.5801 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:19 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30444.248 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:19 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30444.248 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:19 | 60.0006 | 0 |  | 0 | 0 |  |  |  | -653 | 30444.248 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:19 | 60.0032 | 0 |  | 0 | 0 |  |  |  | -653 | 30444.248 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:19 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.1133 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:19 | 60.0026 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.1133 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:19 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.3027 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:19 | 59.9994 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.3027 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:19 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.3027 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:19 | 59.9968 | 0 |  | 0 | 0 |  |  |  | -653 | 30465.3027 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:19 | 59.9968 | 0 |  | 0 | 0 |  |  |  | -653 | 30478.248 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:19 | 59.9971 | 0 |  | 0 | 0 |  |  |  | -653 | 30478.248 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:19 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30478.248 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:19 | 59.9987 | 0 |  | 0 | 0 |  |  |  | -653 | 30478.248 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:19 | 59.9997 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8574 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:19 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8574 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:19 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30468.8379 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:19 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 30468.8379 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:19 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30468.8379 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:19 | 60.0029 | 0 |  | 0 | 0 |  |  |  | -653 | 30468.8379 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:19 | 60.0026 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.627 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:19 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.627 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:19 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.627 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:19 | 60.0032 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.627 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:19 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30488.4141 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:19 | 60.0049 | 0 |  | 0 | 0 |  |  |  | -653 | 30488.4141 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:19 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2891 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:19 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2891 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2891 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2891 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30477.1328 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30477.1328 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30477.1328 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30477.1328 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30487.8203 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:20 | 60.0049 | 0 |  | 0 | 0 |  |  |  | -653 | 30487.8203 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:20 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30489.7266 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:20 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30489.7266 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30489.7266 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:20 | 60.0029 | 0 |  | 0 | 0 |  |  |  | -653 | 30489.7266 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:20 | 60.0016 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.0918 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:20 | 60.0016 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.0918 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.0918 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:20 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.0918 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:20 | 60.0029 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.9141 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:20 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.9141 | 1 | 1 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:20 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.8359 | 1 | 0 | 1 | -0.0022888 | 0.0022888
2011-05-16 08:20 | 59.9965 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.8359 | 1 | 0 | 1 | -0.0015869 | 0.0015869
2011-05-16 08:20 | 59.9951 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.8359 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:20 | 59.9939 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.8359 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:20 | 59.9929 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.0918 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:20 | 59.9926 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.0918 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:20 | 59.9922 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.0918 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:20 | 59.9897 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.0918 | 1 | 0 | 1 | -0.002594 | 0.002594
2011-05-16 08:20 | 59.9851 | 0 |  | 0 | 0 |  |  |  | -653 | 30456.7559 | 1 | 0 | 1 | -0.0045166 | 0.0045166
2011-05-16 08:20 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30456.7559 | 1 | 0 | 1 | -0.002594 | 0.002594
2011-05-16 08:20 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30457.1152 | 1 | 0 | 1 | -0.0041809 | 0.0041809
2011-05-16 08:20 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30457.1152 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:20 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30457.1152 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:21 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30457.1152 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:21 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.9785 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:21 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.9785 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:21 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.9785 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:21 | 59.9816 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.9785 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:21 | 59.9813 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.0195 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9793 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.0195 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:21 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30460.9434 | 1 | 0 | 1 | -0.0032043 | 0.0032043
2011-05-16 08:21 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30460.9434 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:21 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30460.9434 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30460.9434 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:21 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.2305 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:21 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.2305 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:21 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.2305 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:21 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30469.2305 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:21 | 59.9819 | 0 |  | 0 | 0 |  |  |  | -653 | 30481.4863 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:21 | 59.9822 | 0 |  | 0 | 0 |  |  |  | -653 | 30481.4863 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2852 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:21 | 59.9829 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2852 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2852 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30480.2852 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:21 | 59.9829 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.1465 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:21 | 59.9861 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.1465 | 1 | 0 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:21 | 59.9939 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.1465 | 1 | 0 | 1 | 0.0077515 | 0.0077515
2011-05-16 08:21 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.1465 | 1 | 1 | 1 | 0.0083923 | 0.0083923
2011-05-16 08:21 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.6582 | 1 | 1 | 1 | 0.008728 | 0.008728
2011-05-16 08:21 | 60.0171 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.6582 | 1 | 1 | 1 | 0.006134 | 0.006134
2011-05-16 08:21 | 60.0207 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.5996 | 1 | 1 | 1 | 0.0035706 | 0.0035706
2011-05-16 08:21 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.5996 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.5996 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.5996 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0233 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.2793 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:22 | 60.0255 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.2793 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:22 | 60.0268 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.2793 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:22 | 60.0284 | 0 |  | 0 | 0 |  |  |  | -653 | 30461.2793 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:22 | 60.0297 | 0 |  | 0 | 0 |  |  |  | -653 | 30450.4355 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:22 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30450.4355 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:22 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.9062 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:22 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.9062 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:22 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.9062 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:22 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30451.9062 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:22 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.5176 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0342 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.5176 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.5176 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:22 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30446.5176 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0356 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:22 | 60.0359 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:22 | 60.0368 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:22 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0372 | 0 |  | 0 | 0 |  |  |  | -653 | 30452.4297 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:22 | 60.0378 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.209 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0378 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.209 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.209 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:22 | 60.0365 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.209 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:22 | 60.0368 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.6074 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:22 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.6074 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.5488 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:22 | 60.0381 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.5488 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:22 | 60.0388 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.5488 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:23 | 60.0401 | 0 |  | 0 | 0 |  |  |  | -653 | 30476.5488 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:23 | 60.0417 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8047 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:23 | 60.0436 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8047 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:23 | 60.0452 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8047 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:23 | 60.0449 | 0 |  | 0 | 0 |  |  |  | -653 | 30473.8047 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:23 | 60.0446 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.9961 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:23 | 60.0439 | 0 |  | 0 | 0 |  |  |  | -653 | 30470.9961 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:23 | 60.042 | 0 |  | 0 | 0 |  |  |  | -653 | 30471.9668 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:23 | 60.0372 | 0 |  | 0 | 0 |  |  |  | -653 | 30471.9668 | 1 | 1 | 1 | -0.0048218 | 0.0048218
2011-05-16 08:23 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 30471.9668 | 1 | 1 | 1 | -0.0042114 | 0.0042114
2011-05-16 08:23 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30471.9668 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:23 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30485.4707 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:23 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30485.4707 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:23 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30485.4707 | 1 | 1 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:23 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30485.4707 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:23 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.4902 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:23 | 60.0333 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.4902 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:23 | 60.0333 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2617 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:23 | 60.0339 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2617 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:23 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2617 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:23 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2617 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:23 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30515.5957 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:23 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30515.5957 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:23 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30515.5957 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:23 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30515.5957 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:23 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2773 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:23 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30505.2773 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:23 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30506.1152 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:23 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30506.1152 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:24 | 60.0304 | 0 |  | 0 | 0 |  |  |  | -653 | 30506.1152 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0304 | 0 |  | 0 | 0 |  |  |  | -653 | 30506.1152 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:24 | 60.0297 | 0 |  | 0 | 0 |  |  |  | -653 | 30493.6797 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0287 | 0 |  | 0 | 0 |  |  |  | -653 | 30493.6797 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:24 | 60.0301 | 0 |  | 0 | 0 |  |  |  | -653 | 30493.6797 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:24 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 30493.6797 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:24 | 60.0333 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.2832 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:24 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.2832 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:24 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.084 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:24 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.084 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:24 | 60.0333 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.084 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:24 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.084 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:24 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.5215 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:24 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.5215 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:24 | 60.0333 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.5215 | 1 | 1 | 1 | 0.0015869 | 0.0015869
2011-05-16 08:24 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30529.5215 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:24 | 60.0359 | 0 |  | 0 | 0 |  |  |  | -653 | 30535.5723 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:24 | 60.0365 | 0 |  | 0 | 0 |  |  |  | -653 | 30535.5723 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8887 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:24 | 60.0368 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8887 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0362 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8887 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0352 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8887 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:24 | 60.0342 | 0 |  | 0 | 0 |  |  |  | -653 | 30521.8203 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:24 | 60.033 | 0 |  | 0 | 0 |  |  |  | -653 | 30521.8203 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:24 | 60.032 | 0 |  | 0 | 0 |  |  |  | -653 | 30521.8203 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:24 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30521.8203 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.6445 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:24 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.6445 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:24 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30532.3223 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:24 | 60.0304 | 0 |  | 0 | 0 |  |  |  | -653 | 30532.3223 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:24 | 60.0297 | 0 |  | 0 | 0 |  |  |  | -653 | 30532.3223 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:25 | 60.0301 | 0 |  | 0 | 0 |  |  |  | -653 | 30532.3223 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:25 | 60.0307 | 0 |  | 0 | 0 |  |  |  | -653 | 30551.1973 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:25 | 60.0317 | 0 |  | 0 | 0 |  |  |  | -653 | 30551.1973 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:25 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30551.1973 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:25 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30551.1973 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:25 | 60.0352 | 0 |  | 0 | 0 |  |  |  | -653 | 30548.0586 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:25 | 60.0359 | 0 |  | 0 | 0 |  |  |  | -653 | 30548.0586 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:25 | 60.0372 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.6934 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:25 | 60.0381 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.6934 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:25 | 60.0372 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.6934 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:25 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.6934 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:25 | 60.0385 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.3164 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:25 | 60.0388 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.3164 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:25 | 60.0378 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.3164 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:25 | 60.0362 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.3164 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:25 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.2773 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:25 | 60.0339 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.2773 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:25 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.377 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:25 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.377 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:25 | 60.0346 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.377 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:25 | 60.0365 | 0 |  | 0 | 0 |  |  |  | -653 | 30546.377 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:25 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.8418 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:25 | 60.0378 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.8418 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:25 | 60.0375 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.8418 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:25 | 60.0365 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.8418 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:25 | 60.0349 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4219 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:25 | 60.0336 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4219 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:25 | 60.0323 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4316 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:25 | 60.0313 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4316 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:26 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4316 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:26 | 60.031 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.4316 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0307 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.3945 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:26 | 60.0297 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.3945 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:26 | 60.0291 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.3945 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:26 | 60.0281 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.3945 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:26 | 60.0265 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.2559 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:26 | 60.0252 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.2559 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:26 | 60.0236 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.4297 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:26 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.4297 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:26 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.4297 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:26 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.4297 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0207 | 0 |  | 0 | 0 |  |  |  | -653 | 30573.3203 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:26 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30573.3203 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:26 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 30573.3203 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:26 | 60.0204 | 0 |  | 0 | 0 |  |  |  | -653 | 30573.3203 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:26 | 60.0194 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.998 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:26 | 60.0194 | 0 |  | 0 | 0 |  |  |  | -653 | 30566.998 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0194 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.0391 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0197 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.0391 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:26 | 60.0197 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.0391 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30567.0391 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:26 | 60.0194 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.4902 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:26 | 60.0204 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.4902 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:26 | 60.0204 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.4902 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:26 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.4902 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:26 | 60.0171 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.1875 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:26 | 60.0158 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.1875 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:26 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.043 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:26 | 60.0155 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.043 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:26 | 60.0161 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.043 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30530.043 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:27 | 60.0181 | 0 |  | 0 | 0 |  |  |  | -653 | 30542.2676 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0175 | 0 |  | 0 | 0 |  |  |  | -653 | 30542.2676 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0171 | 0 |  | 0 | 0 |  |  |  | -653 | 30542.2676 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:27 | 60.0165 | 0 |  | 0 | 0 |  |  |  | -653 | 30542.2676 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.6387 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:27 | 60.0123 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.6387 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:27 | 60.0103 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.668 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:27 | 60.0094 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.668 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:27 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.668 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:27 | 60.0094 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.668 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:27 | 60.0107 | 0 |  | 0 | 0 |  |  |  | -653 | 30552.0176 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:27 | 60.0116 | 0 |  | 0 | 0 |  |  |  | -653 | 30552.0176 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:27 | 60.0123 | 0 |  | 0 | 0 |  |  |  | -653 | 30552.0176 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0116 | 0 |  | 0 | 0 |  |  |  | -653 | 30552.0176 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0087 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.7812 | 1 | 1 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:27 | 60.0065 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.7812 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:27 | 60.0058 | 0 |  | 0 | 0 |  |  |  | -653 | 30550.6973 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30550.6973 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:27 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30550.6973 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:27 | 60.0071 | 0 |  | 0 | 0 |  |  |  | -653 | 30550.6973 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:27 | 60.009 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.7598 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:27 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.7598 | 1 | 1 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:27 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.7598 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:27 | 60.0103 | 0 |  | 0 | 0 |  |  |  | -653 | 30559.7598 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0097 | 0 |  | 0 | 0 |  |  |  | -653 | 30563.6094 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:27 | 60.0087 | 0 |  | 0 | 0 |  |  |  | -653 | 30563.6094 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:27 | 60.0071 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.5703 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:27 | 60.0061 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.5703 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:28 | 60.0058 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.5703 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:28 | 60.0071 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.5703 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:28 | 60.0081 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.6953 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:28 | 60.0084 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.6953 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:28 | 60.0081 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.6953 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:28 | 60.0071 | 0 |  | 0 | 0 |  |  |  | -653 | 30556.6953 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:28 | 60.0068 | 0 |  | 0 | 0 |  |  |  | -653 | 30544.5176 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:28 | 60.0078 | 0 |  | 0 | 0 |  |  |  | -653 | 30544.5176 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:28 | 60.0071 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.3418 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:28 | 60.0065 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.3418 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:28 | 60.0039 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.3418 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:28 | 60.0013 | 0 |  | 0 | 0 |  |  |  | -653 | 30543.3418 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:28 | 59.9994 | 0 |  | 0 | 0 |  |  |  | -653 | 30554.416 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:28 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 30554.416 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:28 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30554.416 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:28 | 59.9971 | 0 |  | 0 | 0 |  |  |  | -653 | 30554.416 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:28 | 59.9968 | 0 |  | 0 | 0 |  |  |  | -653 | 30534.334 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:28 | 59.9971 | 0 |  | 0 | 0 |  |  |  | -653 | 30534.334 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:28 | 59.9965 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8379 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:28 | 59.9958 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8379 | 1 | 0 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:28 | 59.9945 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8379 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:28 | 59.9935 | 0 |  | 0 | 0 |  |  |  | -653 | 30533.8379 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:28 | 59.9929 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.2012 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:28 | 59.9919 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.2012 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:28 | 59.989 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.2012 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:28 | 59.9861 | 0 |  | 0 | 0 |  |  |  | -653 | 30557.2012 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:28 | 59.9845 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.9121 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:28 | 59.9832 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.9121 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:28 | 59.9819 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.5566 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:28 | 59.9809 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.5566 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:28 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.5566 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:29 | 59.9787 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.5566 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:29 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.084 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:29 | 59.98 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.084 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:29 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.084 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9803 | 0 |  | 0 | 0 |  |  |  | -653 | 30560.084 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:29 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 30558.7188 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:29 | 59.9774 | 0 |  | 0 | 0 |  |  |  | -653 | 30558.7188 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:29 | 59.9751 | 0 |  | 0 | 0 |  |  |  | -653 | 30553.4551 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:29 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30553.4551 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:29 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30553.4551 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:29 | 59.9719 | 0 |  | 0 | 0 |  |  |  | -653 | 30553.4551 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.6309 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:29 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.6309 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:29 | 59.9745 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.6309 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:29 | 59.9751 | 0 |  | 0 | 0 |  |  |  | -653 | 30562.6309 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30578.0469 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30578.0469 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30570.9668 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30570.9668 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:29 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30570.9668 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:29 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30570.9668 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:29 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30593.1738 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:29 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30593.1738 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:29 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30593.1738 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:29 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30593.1738 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:29 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:29 | 59.9803 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:29 | 59.9832 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:29 | 59.9855 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.0022888 | 0.0022888
2011-05-16 08:29 | 59.9871 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:30 | 59.9897 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.0664 | 1 | 0 | 1 | 0.0025635 | 0.0025635
2011-05-16 08:30 | 59.9922 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.7188 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:30 | 59.9948 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.7188 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:30 | 59.9965 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.7188 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:30 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30575.7188 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:30 | 59.9997 | 0 |  | 0 | 0 |  |  |  | -653 | 30583.8379 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:30 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30583.8379 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:30 | 60.0013 | 0 |  | 0 | 0 |  |  |  | -653 | 30586.4023 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:30 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30586.4023 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:30 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30586.4023 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:30 | 60.0029 | 0 |  | 0 | 0 |  |  |  | -653 | 30586.4023 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:30 | 60.0035 | 0 |  | 0 | 0 |  |  |  | -653 | 30589.7168 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:30 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30589.7168 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:30 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30589.7168 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:30 | 60.0039 | 0 |  | 0 | 0 |  |  |  | -653 | 30589.7168 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:30 | 60.0039 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.3008 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:30 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.3008 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:30 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.2207 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:30 | 60.0039 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.2207 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:30 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.2207 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:30 | 59.9997 | 0 |  | 0 | 0 |  |  |  | -653 | 30590.2207 | 1 | 1 | 1 | -0.0022888 | 0.0022888
2011-05-16 08:30 | 59.9939 | 0 |  | 0 | 0 |  |  |  | -653 | 30600.1211 | 1 | 0 | 1 | -0.0057983 | 0.0057983
2011-05-16 08:30 | 59.9939 | 0 |  | 0 | 0 |  |  |  | -653 | 30600.1211 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:30 | 59.99 | 0 |  | 0 | 0 |  |  |  | -653 | 30600.1211 | 1 | 0 | 1 | -0.0038757 | 0.0038757
2011-05-16 08:30 | 59.9887 | 0 |  | 0 | 0 |  |  |  | -653 | 30600.1211 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:30 | 59.9871 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.3828 | 1 | 0 | 1 | -0.0015869 | 0.0015869
2011-05-16 08:30 | 59.9858 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.3828 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:30 | 59.9858 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:30 | 59.9829 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:31 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:31 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:31 | 59.9748 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.9609 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:31 | 59.9748 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.9609 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:31 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.9609 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:31 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30603.9609 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:31 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:31 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:31 | 59.9732 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:31 | 59.9751 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:31 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:31 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30597.0918 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:31 | 59.9787 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:31 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:31 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:31 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.002594 | 0.002594
2011-05-16 08:31 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30607.9609 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:31 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:31 | 59.9748 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:31 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:31 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:31 | 59.9735 | 0 |  | 0 | 0 |  |  |  | -653 | 30601.9844 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:31 | 59.9754 | 0 |  | 0 | 0 |  |  |  | -653 | 30632.7852 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:31 | 59.9777 | 0 |  | 0 | 0 |  |  |  | -653 | 30632.7852 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:31 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30632.7852 | 1 | 0 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:31 | 59.9851 | 0 |  | 0 | 0 |  |  |  | -653 | 30632.7852 | 1 | 0 | 1 | 0.0045166 | 0.0045166
2011-05-16 08:31 | 59.9877 | 0 |  | 0 | 0 |  |  |  | -653 | 30632.7852 | 1 | 0 | 1 | 0.002594 | 0.002594
2011-05-16 08:31 | 59.9897 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.1777 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:31 | 59.991 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.1777 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:31 | 59.9922 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.1777 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:31 | 59.9932 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.1777 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:32 | 59.9961 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.1777 | 1 | 0 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:32 | 60.0003 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.5977 | 1 | 1 | 1 | 0.0042114 | 0.0042114
2011-05-16 08:32 | 60.0045 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.5977 | 1 | 1 | 1 | 0.0041809 | 0.0041809
2011-05-16 08:32 | 60.0081 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.5977 | 1 | 1 | 1 | 0.0035706 | 0.0035706
2011-05-16 08:32 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.5977 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:32 | 60.0139 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.5977 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:32 | 60.0178 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.9062 | 1 | 1 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:32 | 60.0207 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.9062 | 1 | 1 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:32 | 60.0216 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.9062 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:32 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.9062 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:32 | 60.0191 | 0 |  | 0 | 0 |  |  |  | -653 | 30620.9062 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:32 | 60.0181 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.873 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:32 | 60.0184 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.873 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:32 | 60.0207 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.873 | 1 | 1 | 1 | 0.0022888 | 0.0022888
2011-05-16 08:32 | 60.0239 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.873 | 1 | 1 | 1 | 0.0032043 | 0.0032043
2011-05-16 08:32 | 60.0262 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.873 | 1 | 1 | 1 | 0.0022888 | 0.0022888
2011-05-16 08:32 | 60.0268 | 0 |  | 0 | 0 |  |  |  | -653 | 30663.7324 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:32 | 60.0265 | 0 |  | 0 | 0 |  |  |  | -653 | 30663.7324 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:32 | 60.0258 | 0 |  | 0 | 0 |  |  |  | -653 | 30663.7324 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:32 | 60.0236 | 0 |  | 0 | 0 |  |  |  | -653 | 30663.7324 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:32 | 60.0236 | 0 |  | 0 | 0 |  |  |  | -653 | 30663.7324 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:32 | 60.0216 | 0 |  | 0 | 0 |  |  |  | -653 | 30659.8398 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:32 | 60.0223 | 0 |  | 0 | 0 |  |  |  | -653 | 30659.8398 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:32 | 60.0233 | 0 |  | 0 | 0 |  |  |  | -653 | 30659.8398 | 1 | 1 | 1 | 0.00094604 | 0.00094604
2011-05-16 08:32 | 60.0236 | 0 |  | 0 | 0 |  |  |  | -653 | 30659.8398 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:32 | 60.0229 | 0 |  | 0 | 0 |  |  |  | -653 | 30659.8398 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:32 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30653.4648 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:32 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 30653.4648 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:32 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 30653.4648 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:33 | 60.0213 | 0 |  | 0 | 0 |  |  |  | -653 | 30653.4648 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:33 | 60.021 | 0 |  | 0 | 0 |  |  |  | -653 | 30653.4648 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0204 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.6035 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:33 | 60.02 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.6035 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0194 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.6035 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:33 | 60.0184 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.6035 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:33 | 60.0171 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.6035 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:33 | 60.0158 | 0 |  | 0 | 0 |  |  |  | -653 | 30655.5098 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:33 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30655.5098 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:33 | 60.0145 | 0 |  | 0 | 0 |  |  |  | -653 | 30655.5098 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30655.5098 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0145 | 0 |  | 0 | 0 |  |  |  | -653 | 30655.5098 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.1406 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.1406 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.1406 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.1406 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.1406 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:33 | 60.0165 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.291 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:33 | 60.0161 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.291 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0152 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.291 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:33 | 60.0149 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.291 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0145 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.291 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:33 | 60.0129 | 0 |  | 0 | 0 |  |  |  | -653 | 30652.043 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:33 | 60.011 | 0 |  | 0 | 0 |  |  |  | -653 | 30652.043 | 1 | 1 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:33 | 60.0078 | 0 |  | 0 | 0 |  |  |  | -653 | 30652.043 | 1 | 1 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:33 | 60.0042 | 0 |  | 0 | 0 |  |  |  | -653 | 30652.043 | 1 | 1 | 1 | -0.00354 | 0.00354
2011-05-16 08:33 | 60.0016 | 0 |  | 0 | 0 |  |  |  | -653 | 30652.043 | 1 | 1 | 1 | -0.002594 | 0.002594
2011-05-16 08:33 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 30651.8418 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:33 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30651.8418 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:33 | 59.9951 | 0 |  | 0 | 0 |  |  |  | -653 | 30651.8418 | 1 | 0 | 1 | -0.002594 | 0.002594
2011-05-16 08:33 | 59.9926 | 0 |  | 0 | 0 |  |  |  | -653 | 30651.8418 | 1 | 0 | 1 | -0.002594 | 0.002594
2011-05-16 08:34 | 59.9903 | 0 |  | 0 | 0 |  |  |  | -653 | 30651.8418 | 1 | 0 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:34 | 59.9868 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.8008 | 1 | 0 | 1 | -0.00354 | 0.00354
2011-05-16 08:34 | 59.9835 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.8008 | 1 | 0 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:34 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.8008 | 1 | 0 | 1 | -0.0028992 | 0.0028992
2011-05-16 08:34 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.8008 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:34 | 59.9787 | 0 |  | 0 | 0 |  |  |  | -653 | 30633.8008 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:34 | 59.9771 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.707 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:34 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.707 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:34 | 59.9767 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.707 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:34 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.707 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:34 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.707 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:34 | 59.9748 | 0 |  | 0 | 0 |  |  |  | -653 | 30634.1309 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:34 | 59.9742 | 0 |  | 0 | 0 |  |  |  | -653 | 30634.1309 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:34 | 59.9729 | 0 |  | 0 | 0 |  |  |  | -653 | 30634.1309 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:34 | 59.9713 | 0 |  | 0 | 0 |  |  |  | -653 | 30634.1309 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:34 | 59.9709 | 0 |  | 0 | 0 |  |  |  | -653 | 30634.1309 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:34 | 59.9713 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.0508 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:34 | 59.9706 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.0508 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:34 | 59.9709 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.0508 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:34 | 59.9713 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.0508 | 1 | 0 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:34 | 59.9716 | 0 |  | 0 | 0 |  |  |  | -653 | 30627.0508 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:34 | 59.9725 | 0 |  | 0 | 0 |  |  |  | -653 | 30662.7227 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:34 | 59.9745 | 0 |  | 0 | 0 |  |  |  | -653 | 30662.7227 | 1 | 0 | 1 | 0.0019531 | 0.0019531
2011-05-16 08:34 | 59.9758 | 0 |  | 0 | 0 |  |  |  | -653 | 30662.7227 | 1 | 0 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:34 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30662.7227 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:34 | 59.9764 | 0 |  | 0 | 0 |  |  |  | -653 | 30662.7227 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:34 | 59.9751 | 0 |  | 0 | 0 |  |  |  | -653 | 30656.5176 | 1 | 0 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:34 | 59.9761 | 0 |  | 0 | 0 |  |  |  | -653 | 30656.5176 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:34 | 59.979 | 0 |  | 0 | 0 |  |  |  | -653 | 30656.5176 | 1 | 0 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:35 | 59.9813 | 0 |  | 0 | 0 |  |  |  | -653 | 30656.5176 | 1 | 0 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:35 | 59.9822 | 0 |  | 0 | 0 |  |  |  | -653 | 30656.5176 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.2461 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:35 | 59.9825 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.2461 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:35 | 59.9816 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.2461 | 1 | 0 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:35 | 59.9803 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.2461 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:35 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.2461 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:35 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.4863 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9809 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.4863 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:35 | 59.9803 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.4863 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:35 | 59.9793 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.4863 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9784 | 0 |  | 0 | 0 |  |  |  | -653 | 30642.4863 | 1 | 0 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:35 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30645.7227 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:35 | 59.978 | 0 |  | 0 | 0 |  |  |  | -653 | 30645.7227 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:35 | 59.9787 | 0 |  | 0 | 0 |  |  |  | -653 | 30645.7227 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:35 | 59.9796 | 0 |  | 0 | 0 |  |  |  | -653 | 30645.7227 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9806 | 0 |  | 0 | 0 |  |  |  | -653 | 30645.7227 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9813 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.5547 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:35 | 59.9822 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.5547 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9842 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.5547 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:35 | 59.9855 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.5547 | 1 | 0 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:35 | 59.9858 | 0 |  | 0 | 0 |  |  |  | -653 | 30648.5547 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:35 | 59.9858 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:35 | 59.9868 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:35 | 59.9906 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 0 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:35 | 59.9942 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 0 | 1 | 0.00354 | 0.00354
2011-05-16 08:35 | 59.998 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 0 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:35 | 59.9997 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:35 | 60.0023 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:35 | 60.002 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:35 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:36 | 59.9994 | 0 |  | 0 | 0 |  |  |  | -653 | 30661.0586 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:36 | 59.9987 | 0 |  | 0 | 0 |  |  |  | -653 | 30684.3066 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:36 | 59.9977 | 0 |  | 0 | 0 |  |  |  | -653 | 30684.3066 | 1 | 0 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:36 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30684.3066 | 1 | 0 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:36 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30684.3066 | 1 | 0 | 1 | 0 | 0
2011-05-16 08:36 | 59.9984 | 0 |  | 0 | 0 |  |  |  | -653 | 30684.3066 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:36 | 59.9997 | 0 |  | 0 | 0 |  |  |  | -653 | 30686.8301 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:36 | 60.0006 | 0 |  | 0 | 0 |  |  |  | -653 | 30686.8301 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:36 | 60.001 | 0 |  | 0 | 0 |  |  |  | -653 | 30686.8301 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:36 | 60.0006 | 0 |  | 0 | 0 |  |  |  | -653 | 30686.8301 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:36 | 60 | 0 |  | 0 | 0 |  |  |  | -653 | 30686.8301 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:36 | 59.9994 | 0 |  | 0 | 0 |  |  |  | -653 | 30678.0488 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:36 | 59.9974 | 0 |  | 0 | 0 |  |  |  | -653 | 30678.0488 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:36 | 59.9948 | 0 |  | 0 | 0 |  |  |  |  | 30678.0488 | 1 | 0 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:36 | 59.9929 | 0 |  | 0 | 0 |  |  |  |  | 30678.0488 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:36 | 59.991 | 0 |  | 0 | 0 |  |  |  |  | 30678.0488 | 1 | 0 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:36 | 59.9897 | 0 |  | 0 | 0 |  |  |  |  | 30679.1855 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:36 | 59.988 | 0 |  | 0 | 0 |  |  |  |  | 30679.1855 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:36 | 59.9877 | 0 |  | 0 | 0 |  |  |  |  | 30679.1855 | 1 | 0 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:36 | 59.988 | 0 |  | 0 | 0 |  |  |  |  | 30679.1855 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:36 | 59.989 | 0 |  | 0 | 0 |  |  |  |  | 30679.1855 | 1 | 0 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:36 | 59.9906 | 0 |  | 0 | 0 |  |  |  |  | 30684.8457 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:36 | 59.9926 | 0 |  | 0 | 0 |  |  |  |  | 30684.8457 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:36 | 59.9948 | 0 |  | 0 | 0 |  |  |  |  | 30684.8457 | 1 | 0 | 1 | 0.0022888 | 0.0022888
2011-05-16 08:36 | 59.9968 | 0 |  | 0 | 0 |  |  |  |  | 30684.8457 | 1 | 0 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:36 | 59.9984 | 0 |  | 0 | 0 |  |  |  |  | 30684.8457 | 1 | 0 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:36 | 59.9987 | 0 |  | 0 | 0 |  |  |  |  | 30684.9922 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:36 | 59.9987 | 0 |  | 0 | 0 |  |  |  |  | 30684.9922 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:36 | 59.9994 | 0 |  | 0 | 0 |  |  |  |  | 30684.9922 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:37 | 60.002 | 0 |  | 0 | 0 |  |  |  |  | 30684.9922 | 1 | 1 | 1 | 0.002594 | 0.002594
2011-05-16 08:37 | 60.0049 | 0 |  | 0 | 0 |  |  |  |  | 30684.9922 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:37 | 60.0081 | 0 |  | 0 | 0 |  |  |  |  | 30687.2891 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:37 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 30687.2891 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:37 | 60.0132 | 0 |  | 0 | 0 |  |  |  |  | 30687.2891 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:37 | 60.0142 | 0 |  | 0 | 0 |  |  |  |  | 30687.2891 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:37 | 60.0149 | 0 |  | 0 | 0 |  |  |  |  | 30687.2891 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:37 | 60.0145 | 0 |  | 0 | 0 |  |  |  |  | 30687.5898 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:37 | 60.0123 | 0 |  | 0 | 0 |  |  |  |  | 30687.5898 | 1 | 1 | 1 | -0.0022583 | 0.0022583
2011-05-16 08:37 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 30687.5898 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:37 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 30687.5898 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:37 | 60.0123 | 0 |  | 0 | 0 |  |  |  |  | 30687.5898 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:37 | 60.0123 | 0 |  | 0 | 0 |  |  |  |  | 30726.7617 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:37 | 60.0116 | 0 |  | 0 | 0 |  |  |  |  | 30726.7617 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:37 | 60.0113 | 0 |  | 0 | 0 |  |  |  |  | 30726.7617 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:37 | 60.0113 | 0 |  | 0 | 0 |  |  |  |  | 30726.7617 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:37 | 60.0107 | 0 |  | 0 | 0 |  |  |  |  | 30726.7617 | 1 | 1 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:37 | 60.009 | 0 |  | 0 | 0 |  |  |  |  | 30726.8184 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:37 | 60.0084 | 0 |  | 0 | 0 |  |  |  |  | 30726.8184 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:37 | 60.0081 | 0 |  | 0 | 0 |  |  |  |  | 30726.8184 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:37 | 60.0081 | 0 |  | 0 | 0 |  |  |  |  | 30726.8184 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:37 | 60.0094 | 0 |  | 0 | 0 |  |  |  |  | 30726.8184 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:37 | 60.011 | 0 |  | 0 | 0 |  |  |  |  | 30720.9336 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:37 | 60.0123 | 0 |  | 0 | 0 |  |  |  |  | 30720.9336 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:37 | 60.0129 | 0 |  | 0 | 0 |  |  |  |  | 30720.9336 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:37 | 60.0126 | 0 |  | 0 | 0 |  |  |  |  | 30720.9336 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:37 | 60.0113 | 0 |  | 0 | 0 |  |  |  |  | 30720.9336 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:37 | 60.0097 | 0 |  | 0 | 0 |  |  |  |  | 30720.5332 | 1 | 1 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:37 | 60.0061 | 0 |  | 0 | 0 |  |  |  |  | 30720.5332 | 1 | 1 | 1 | -0.0035706 | 0.0035706
2011-05-16 08:37 | 60.0026 | 0 |  | 0 | 0 |  |  |  |  | 30720.5332 | 1 | 1 | 1 | -0.00354 | 0.00354
2011-05-16 08:38 | 59.9994 | 0 |  | 0 | 0 |  |  |  |  | 30720.5332 | 1 | 1 | 1 | -0.0032349 | 0.0032349
2011-05-16 08:38 | 59.999 | 0 |  | 0 | 0 |  |  |  |  | 30720.5332 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:38 | 60.0003 | 0 |  | 0 | 0 |  |  |  |  | 30720.6172 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:38 | 60.0006 | 0 |  | 0 | 0 |  |  |  |  | 30720.6172 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:38 | 59.9994 | 0 |  | 0 | 0 |  |  |  |  | 30720.6172 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:38 | 59.9974 | 0 |  | 0 | 0 |  |  |  |  | 30720.6172 | 1 | 0 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:38 | 59.9958 | 0 |  | 0 | 0 |  |  |  |  | 30720.6172 | 1 | 0 | 1 | -0.0016174 | 0.0016174
2011-05-16 08:38 | 59.9939 | 0 |  | 0 | 0 |  |  |  |  | 30721.1465 | 1 | 0 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:38 | 59.9926 | 0 |  | 0 | 0 |  |  |  |  | 30721.1465 | 1 | 0 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:38 | 59.9919 | 0 |  | 0 | 0 |  |  |  |  | 30721.1465 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:38 | 59.9926 | 0 |  | 0 | 0 |  |  |  |  | 30721.1465 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:38 | 59.9955 | 0 |  | 0 | 0 |  |  |  |  | 30721.1465 | 1 | 0 | 1 | 0.0029297 | 0.0029297
2011-05-16 08:38 | 60 | 0 |  | 0 | 0 |  |  |  |  | 30726.8652 | 1 | 1 | 1 | 0.0045166 | 0.0045166
2011-05-16 08:38 | 60.0032 | 0 |  | 0 | 0 |  |  |  |  | 30726.8652 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:38 | 60.0052 | 0 |  | 0 | 0 |  |  |  |  | 30726.8652 | 1 | 1 | 1 | 0.0019226 | 0.0019226
2011-05-16 08:38 | 60.0049 | 0 |  | 0 | 0 |  |  |  |  | 30726.8652 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:38 | 60.0035 | 0 |  | 0 | 0 |  |  |  |  | 30726.8652 | 1 | 1 | 1 | -0.0013123 | 0.0013123
2011-05-16 08:38 | 60.0023 | 0 |  | 0 | 0 |  |  |  |  | 30734.8379 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:38 | 60.001 | 0 |  | 0 | 0 |  |  |  |  | 30734.8379 | 1 | 1 | 1 | -0.0012817 | 0.0012817
2011-05-16 08:38 | 60 | 0 |  | 0 | 0 |  |  |  |  | 30734.8379 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:38 | 59.9997 | 0 |  | 0 | 0 |  |  |  |  | 30734.8379 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:38 | 59.9997 | 0 |  | 0 | 0 |  |  |  |  | 30734.8379 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:38 | 59.9977 | 0 |  | 0 | 0 |  |  |  |  | 30757.4531 | 1 | 0 | 1 | -0.0019226 | 0.0019226
2011-05-16 08:38 | 59.9971 | 0 |  | 0 | 0 |  |  |  |  | 30757.4531 | 1 | 0 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:38 | 59.9974 | 0 |  | 0 | 0 |  |  |  |  | 30757.4531 | 1 | 0 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:38 | 59.998 | 0 |  | 0 | 0 |  |  |  |  | 30757.4531 | 1 | 0 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:38 | 59.9987 | 0 |  | 0 | 0 |  |  |  |  | 30757.4531 | 1 | 1 | 1 | 0.00067139 | 0.00067139
2011-05-16 08:38 | 59.9994 | 0 |  | 0 | 0 |  |  |  |  | 30757.9238 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:38 | 60 | 0 |  | 0 | 0 |  |  |  |  | 30757.9238 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:38 | 60.0016 | 0 |  | 0 | 0 |  |  |  |  | 30757.9238 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:39 | 60.0032 | 0 |  | 0 | 0 |  |  |  |  | 30757.9238 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:39 | 60.0039 | 0 |  | 0 | 0 |  |  |  |  | 30757.9238 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0049 | 0 |  | 0 | 0 |  |  |  |  | 30752.2715 | 1 | 1 | 1 | 0.00097656 | 0.00097656
2011-05-16 08:39 | 60.0055 | 0 |  | 0 | 0 |  |  |  |  | 30752.2715 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0061 | 0 |  | 0 | 0 |  |  |  |  | 30752.2715 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0065 | 0 |  | 0 | 0 |  |  |  |  | 30752.2715 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:39 | 60.0068 | 0 |  | 0 | 0 |  |  |  |  | 30752.2715 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:39 | 60.0068 | 0 |  | 0 | 0 |  |  |  |  | 30752.3301 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:39 | 60.0061 | 0 |  | 0 | 0 |  |  |  |  | 30752.3301 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0055 | 0 |  | 0 | 0 |  |  |  |  | 30752.3301 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0049 | 0 |  | 0 | 0 |  |  |  |  | 30752.3301 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0049 | 0 |  | 0 | 0 |  |  |  |  | 30752.3301 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:39 | 60.0061 | 0 |  | 0 | 0 |  |  |  |  | 30755.6289 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:39 | 60.01 | 0 |  | 0 | 0 |  |  |  |  | 30755.6289 | 1 | 1 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:39 | 60.0132 | 0 |  | 0 | 0 |  |  |  |  | 30755.6289 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:39 | 60.0161 | 0 |  | 0 | 0 |  |  |  |  | 30755.6289 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:39 | 60.0184 | 0 |  | 0 | 0 |  |  |  |  | 30755.6289 | 1 | 1 | 1 | 0.0022583 | 0.0022583
2011-05-16 08:39 | 60.0197 | 0 |  | 0 | 0 |  |  |  |  | 30755.6582 | 1 | 1 | 1 | 0.0013123 | 0.0013123
2011-05-16 08:39 | 60.021 | 0 |  | 0 | 0 |  |  |  |  | 30755.6582 | 1 | 1 | 1 | 0.0012817 | 0.0012817
2011-05-16 08:39 | 60.0213 | 0 |  | 0 | 0 |  |  |  |  | 30755.6582 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:39 | 60.022 | 0 |  | 0 | 0 |  |  |  |  | 30755.6582 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0236 | 0 |  | 0 | 0 |  |  |  |  | 30755.6582 | 1 | 1 | 1 | 0.0016174 | 0.0016174
2011-05-16 08:39 | 60.0268 | 0 |  | 0 | 0 |  |  |  |  | 30784.8867 | 1 | 1 | 1 | 0.0032349 | 0.0032349
2011-05-16 08:39 | 60.0307 | 0 |  | 0 | 0 |  |  |  |  | 30784.8867 | 1 | 1 | 1 | 0.0038757 | 0.0038757
2011-05-16 08:39 | 60.0336 | 0 |  | 0 | 0 |  |  |  |  | 30784.8867 | 1 | 1 | 1 | 0.0028992 | 0.0028992
2011-05-16 08:39 | 60.0342 | 0 |  | 0 | 0 |  |  |  |  | 30784.8867 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:39 | 60.0333 | 0 |  | 0 | 0 |  |  |  |  | 30784.8867 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:39 | 60.0307 | 0 |  | 0 | 0 |  |  |  |  | 30786.9824 | 1 | 1 | 1 | -0.0025635 | 0.0025635
2011-05-16 08:39 | 60.0287 | 0 |  | 0 | 0 |  |  |  |  | 30786.9824 | 1 | 1 | 1 | -0.0019531 | 0.0019531
2011-05-16 08:39 | 60.0287 | 0 |  | 0 | 0 |  |  |  |  | 30786.9824 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:40 | 60.0294 | 0 |  | 0 | 0 |  |  |  |  | 30786.9824 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:40 | 60.0291 | 0 |  | 0 | 0 |  |  |  |  | 30786.9824 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:40 | 60.0284 | 0 |  | 0 | 0 |  |  |  |  | 30796.2773 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:40 | 60.0278 | 0 |  | 0 | 0 |  |  |  |  | 30796.2773 | 1 | 1 | 1 | -0.00067139 | 0.00067139
2011-05-16 08:40 | 60.0281 | 0 |  | 0 | 0 |  |  |  |  | 30796.2773 | 1 | 1 | 1 | 0.00033569 | 0.00033569
2011-05-16 08:40 | 60.0278 | 0 |  | 0 | 0 |  |  |  |  | 30796.2773 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:40 | 60.0278 | 0 |  | 0 | 0 |  |  |  |  | 30796.2773 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:40 | 60.0278 | 0 |  | 0 | 0 |  |  |  |  | 30792.9355 | 1 | 1 | 1 | 0 | 0
2011-05-16 08:40 | 60.0275 | 0 |  | 0 | 0 |  |  |  |  | 30792.9355 | 1 | 1 | 1 | -0.00030518 | 0.00030518
2011-05-16 08:40 | 60.0271 | 0 |  | 0 | 0 |  |  |  |  | 30792.9355 | 1 | 1 | 1 | -0.00033569 | 0.00033569
2011-05-16 08:40 | 60.0262 | 0 |  | 0 | 0 |  |  |  |  | 30792.9355 | 1 | 1 | 1 | -0.00094604 | 0.00094604
2011-05-16 08:40 | 60.0252 | 0 |  | 0 | 0 |  |  |  |  | 30792.9355 | 1 | 1 | 1 | -0.00097656 | 0.00097656
2011-05-16 08:40 | 60.0246 | 0 |  | 0 | 0 |  |  |  |  | 30803.5762 | 1 | 1 | 1 | -0.00064087 | 0.00064087
2011-05-16 08:40 | 60.0249 | 0 |  | 0 | 0 |  |  |  |  | 30803.5762 | 1 | 1 | 1 | 0.00030518 | 0.00030518
2011-05-16 08:40 | 60.0255 | 0 |  | 0 | 0 |  |  |  |  | 30803.5762 | 1 | 1 | 1 | 0.00064087 | 0.00064087
2011-05-16 08:40 | 60.0262 | 0 |  | 0 | 0 |  |  |  |  | 30803.5762 | 1 | 1 | 1 | 0.00067139 | 0.00067139

## Copy Results
Balancing Authority Name: | MyBA |  | MyBA_110516_0806_FRS_Form2.9.xlsm
| Interconnection Prevailing UFLS First Step Relay trip point | 59.3 | Hz
| Interconnection High Relay trip point | 60.7 | Hz
Note: See "Instruction" tab for more detailed instructions. |  |  |  | Auto | Event Detection | Auto
|  |  | 40679.3379 | 1245 | Manually selected row number of the Event Starting Time. | Manual
Step 1. | Copy and Paste Event Data into the appropriate cells of the "Data" worksheet. |  | 40679.3406 | 1442 | Manually selected row number of the Event Ending Time.
Maintain date and time format of mm/dd/yy hh:mm:ss.
Step 2. | Data must start at least 2 full minutes before the beginning of the event. | 40679.3379
Collect the same amount of data for each event. Suggest 2 to 3 minutes before to 15 minutes after (up to 60 minutes total). Delete unused rows of data in the Data worksheet below your data, columns A through R. You must also delete any un-used event detection formulas in columns N through R as well.
Step 3. | Enter your BA name in cell B1 of this worksheet.
Step 4. | Verify that the "Auto" Event Detection selected the correct event. Verify time and delta Hz
by comparing time of event and delta Hz on graph to the right to that on Form 1 for this event. If the wrong event was selected, in cell "E4" of this worksheet select "Manual" and manually select the beginning and ending row numbers of the desired event and enter these in cells "E5" and "E6". Only rarely should you have to use the "Manual" process.
Step 5. | Verify that the "Auto" selection of T(0) is correct by observing "Graph 20 to 52s". | 40679.3406
The very first frequency data point of the event on the graph
must not be included in the "A Value" average. This is accomplished when the
first frequency data point of the event is dead center of the graph on the center
vertical grid line. The Auto event detection will select the single largest event in the
data provided. An adjustment for T(0) alignment is provided in Cell Q3 on the Graph 20 to 52s.
Step 6. | When T(0) is properly aligned. Hit the big blue button to copy your data for pasting into FRS Form 1 "BA Event Data" worksheet.
Step 7. | Paste data into "FRS Form 1" in the appropriate row on the "BA Event Data" worksheet.
Be sure to use the latest version of Form 1. This is Form 2.9 so use Form 1.9.
Step 8. | Save this workbook using the following file name in bold below:
| 2011-05-16 08:07 | Date yymmdd
| 40679.3379 | Time hh:ss of T(0)
Where "MyBA" = your BA mnemonic
MyBA_110516_0806_FRS_Form2.9.xlsm
Note on E4: With Auto selected the spreadsheet will find the highest frequency change in the frequency data. On rare occasions this is not the event that you want to evaluate. By selecting manual you can enter the starting and ending event "row" numbers from the "Data" worksheet. The spreadsheet will then evaluate PFR using these manually entered start and end times.
Copy Form 2 data for Pasting into Form 1

## Evaluation
| 2 | seconds |  |  | Date: | 2011-05-16 08:07 |  |  | Balancing Authority | MyBA | [5 empty] | A Point | 40679.3379 | [5 empty] | Non-Conforming Load sign convention | + | (Data is positive for Load then enter "+" else "-" | [11 empty] | Date: | 2011-05-16 08:07 |  |  |  | Frequency Response Initiative - Additional Primary Frequency Response Evaluation Points
[5 empty] | Time of T(0) | 40679.3379 |  |  | Grid Nominal Frequency | 60 | Hz |  |  |  |  | FPointA | 60.002 | 40679.3379 | [18 empty] | Time of T(0) | 40679.3379 |  |  |  | Frequency @ T(+46) | 59.9005 | Hz
[5 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40679.3406 | [9 empty] | A Value | 59.9986 | [19 empty] | Time of Frequency Recovery to 60 Hz or Pre-Perturbation Hz | 40679.3406 |  |  |  | Frequency @ T(+76) | 59.9176 | Hz | Actual |  | Load | Non-
[5 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 59.9986 | Hz |  | Droop Setting | 5% | 3 | Hz |  |  |  | C Value | 59.8701 | [19 empty] | Value A Pre-Perturbation Average Frequency [T(-2 ) to T(-16)] | 59.9986 | Hz |  |  | Frequency @ T(+106) | 59.9457 | Hz | Primary | Un-adjusted | Resources | Conforming |  |  |  | Adjusted
[5 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8976 | Hz |  | Deadband Setting | 0 | Hz |  |  |  |  | Delta FC | [20 empty] | Value B Post-Perturbation Average Frequency [T(+20 to T(+52)] | 59.8976 | Hz |  |  | Frequency @ T(+136) | 59.9519 | Hz | Freq Response | P.U. | Tripped | Load | Spare | Spare | Spare | P.U.
[5 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.10101 | Hz |  | Hz Span | 3 | Hz | [25 empty] | Pre to Post Perturbation Delta Frequency Actual | -0.10101 | Hz |  |  | Frequency @ T(+166) | 59.969 | Hz | MW/0.1 Hz | Performance | Adjustment | Adjustment | Adjustment | Adjustment | Adjustment | Performance
[5 empty] | Value A Pre-Perturbation Average Contingent MW [T(-2 ) to T(-16)] | 471.0875 | MW | [29 empty] | Value A Pre-Perturbation Contingency MW [T(-2 ) to T(-16)] | 471.0875 | MW |  |  | EPFR @ T(+46) | -653 | MW/0.1 Hz | -479.975 | 0.73503 | 0 | 0 | 0 | 0 | 0 | 0.73503
[5 empty] | Value B Post-Perturbation Average Contingent MW [T(+20 to T(+52)] | 0 | MW | [29 empty] | Value B Post-Perturbation Average Contingency MW [T(+20 to T(+52)] | 0 | MW |  |  | EPFR @ T(+76) | -653 | MW/0.1 Hz | -581.3886 | 0.89033 | 0 | 0 | 0 | 0 | 0 | 0.89033
[5 empty] | Pre to Post Perturbation Contingent Delta MW Actual | -471.0875 | MW | [29 empty] | Pre to Post Perturbation Contingency Delta MW Actual | 471.0875 | MW |  |  | EPFR @ T(+106) | -653 | MW/0.1 Hz | -890.2304 | 1.3633 | 0 | 0 | 0 | 0 | 0 | 1.3633
[5 empty] | Initial Performance Ramp Magnitude Adjustment | -0.059004 | MW | [34 empty] | EPFR @ T(+136) | -653 | MW/0.1 Hz | -1007.6106 | 1.543 | 0 | 0 | 0 | 0 | 0 | 1.543
[5 empty] | EPFR Pre-Perturbation Average | 8.9676 | MW | [29 empty] | EPFR Pre-Perturbation Average | 8.9676 | MW |  |  | EPFR @ T(+166) | -653 | MW/0.1 Hz | -1589.7626 | 2.4346 | 0 | 0 | 0 | 0 | 0 | 2.4346
[5 empty] | EPFR Post-Perturbation Average | 668.5617 | MW | [29 empty] | EPFR Post-Perturbation Average | 668.5617 | MW
[5 empty] | EPFR Delta | 659.5941 | MW |  | TC (frequency response filter constant) | 0.35 | Time Constant for delayed delivery of PFR during Sustained Measure | [25 empty] | EPFR Unadjusted | 659.5941 | MW
[37 empty] | EPFR Adjusted | 659.5941 | MW |  |  | T(20) to T(52) Evaluation
[37 empty] | Pre Load Resources MW | 0 | MW |  |  | Pre-Perturbation Bias Setting | -653 | MW/0.1 Hz
[9 empty] | Low Hz | Delta Hz Event | [26 empty] | Pre Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation Bias Setting | -653 | MW/0.1 Hz
[9 empty] | 0 | Actual Interchange MW Average during frequency recovery period | [26 empty] | Spare | 0 | MW |  |  | EPFR for Bias Setting Pre-Perturbation Average | 8.9676 | MW
[9 empty] | 613.5045 | Target Interchange MW Average during frequency recovery period | [31 empty] | EPFR for Bias Setting Post-Perturbation Average | 668.5617 | MW
|  |  | EPFR = Expected Primary Frequency Response |  | EPFR(Final) | 659.5351 | MW |  | 229.5506 | Interchange Average Ramp MW during frequency recovery period | [26 empty] | Spare | 0 | MW |  |  | EPFR for Bias Setting Delta | 659.5941 | MW
[5 empty] | MW Response in right direction for frequency delta | Yes |  |  | 470.9 | Actual MW @ T(-4) | [26 empty] | Spare | 0 | MW |  |  | Primary Frequency Response Delivery % of Bias | 71.42%
[9 empty] | -488.4685 | Starting and Ending Difference in Interchange MW during frequency recovery period (indicates ramp direction during recovery period) | [26 empty] | Sum of Pre Perturbation Adjustments | 0 | MW
[9 empty] | 0:04 | Event Duration (h:mm:ss)
[9 empty] | No | Target MW Average minus MW @ T(-4) less than zero | [26 empty] | Post Load Resources MW | 0 | MW |  |  | Pre-Perturbation BA Load | 30202.7422 | MW
[9 empty] | 631.0731 | Interchange Target Relative Average Change - MW (Low Frequency Event) | [26 empty] | Post Non-Conforming Load MW | 0 | MW |  |  | Post-Perturbation BA Load | 30141.1423 | MW
[9 empty] | 17.5685 | Interchange Actual Relative Average Change - MW (Low Frequency Event) | [26 empty] | Spare | 0 | MW |  |  | Pre to Post Perturbation BA Load Change | -61.5998 | MW
[9 empty] | Yes | Interchange Actual Average minus MW @ T(-4) less than zero | [31 empty] | Load Dampening Frequency Response | -60.984 | MW/0.1 Hz
[9 empty] | No | Interchange Average MW minus MW @ T(-4) greater than zero | [26 empty] | Spare | 0 | MW |  |  | Load Dampening % of Total BA Frequency Response | 13.08%
[9 empty] | Yes | Interchange Target MW Average minus MW @ T(-4) greater than zero | [26 empty] | Spare | 0 | MW
[9 empty] | 142.6046 | Interchange Target Relative Average Change - MW (High Frequency Event) | [26 empty] | Sum of Post Perturbation Adjustments | 0 | MW
[9 empty] | -470.9 | Interchange Actual Relative Average Change - MW (High Frequency Event) | [26 empty] | Net Total Adjustments MW | 0 | MW |  |  | Average Bias Setting when Hz is greater than +/-0.036 Hz | -653 | MW/0.1 Hz
[9 empty] | Down | Ramp Direction during frequency recovery period
[20 empty] | Frequency, Actual Interchange, Adjustment Data, Bias and Load used in the evaluation | [12 empty] | 20 to 52 second Average Period Evaluation
[5 empty] | Initial Response P.U. Performance | 0.71427 | P.U. |  | 0.73503 | P.U. Sustianed Response P.U. Performance | [26 empty] | Initial P.U. Performance for FRO | 0.71421 | P.U.
[37 empty] | Initial P.U. Performance Adjusted for FRO | 0.71421 | P.U.
[9 empty] | Initial | [14 empty] | Non- | [12 empty] | Non- | [8 empty] | Actual | Actual
[7 empty] | Bias |  | Measure |  |  | Average | Average |  | Average | [6 empty] | Contingent | Load | Conforming | Not | Not | Not | Not | BA | BA | Expected Primary |  |  |  | Contingent | Load | Conforming | Not | Not | Not | Not | BA | BA |  | Expected | Average | Primary
[7 empty] | (EPFR) | (TC) | Final |  |  | Output | Target |  | Ramp | [6 empty] | Resource | Resources | Load | Used | Used | Used | Used | Bias | Load | Freq Response |  |  |  | Resource | Resources | Load | Used | Used | Used | Used | Bias | Load |  | MW/0.1 Hz | Primary | Freq Response
|  |  | Contingent | Value B |  |  | Expected | Delayed | Expected |  | Recovery | During | During | Recovery | During | [5 empty] | Frequency | Lost | Tripped | Load (-) |  |  |  |  | Setting |  | Based on Bias Setting |  |  | Frequency | Lost | Tripped | Load (-) |  |  |  |  | Setting |  | EPFR | Response | Freq Response | Beta
|  |  | Resource | 20 to 52 sec |  |  | Primary | Delivery | Primary | Average | Period | Recovery | Recovery | Period | Recovery |  |  |  |  | T | Hz | MW | MW | MW | MW |  | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW |  | T | Hz | MW | MW | MW | MW |  | MW/0.1 Hz | MW | MW/0.1 Hz | MW | MW | MW/0.1 Hz | MW/0.1 Hz | MW/0.1 Hz
|  | Frequency | Lost | Average | Average |  | Frequency | Frequency | Frequency | Ramp | Target | Period | Period | Ramp | Period
| T | Hz | MW | Frequency | MW |  | Response | Response | Response | MW/scan | MW | MW | MW | MW | MW
T-72 sec | 40679.3371 | 59.9803 | 471 |  |  | 19590 | 128.7347 | 45.0572 | [10 empty] | T-72 sec | 40679.3371 | 59.9803 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30155.6719 | 128.7347 | T-72 sec | 40679.3371 | [14 empty] | 0.019714
T-70 sec | 40679.3371 | 59.9822 | 471 |  |  | 19590 | 115.9808 | 69.8804 | [10 empty] | T-70 sec | 40679.3371 | 59.9822 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30155.6719 | 115.9808 | T-70 sec | 40679.3371 | [14 empty] | 0.017761
T-68 sec | 40679.3372 | 59.9835 | 471 |  |  | 19590 | 107.6111 | 83.0862 | [10 empty] | T-68 sec | 40679.3372 | 59.9835 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30155.6719 | 107.6111 | T-68 sec | 40679.3372 | [14 empty] | 0.016479
T-66 sec | 40679.3372 | 59.9858 | 471 |  |  | 19590 | 92.8644 | 86.5085 | [10 empty] | T-66 sec | 40679.3372 | 59.9858 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30155.6719 | 92.8644 | T-66 sec | 40679.3372 | [14 empty] | 0.014221
T-64 sec | 40679.3372 | 59.9874 | 471 |  |  | 19590 | 82.3026 | 85.0364 | [10 empty] | T-64 sec | 40679.3372 | 59.9874 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30142.791 | 82.3026 | T-64 sec | 40679.3372 | [14 empty] | 0.012604
T-62 sec | 40679.3372 | 59.988 | 471 |  |  | 19590 | 78.1177 | 82.6149 | [10 empty] | T-62 sec | 40679.3372 | 59.988 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30142.791 | 78.1177 | T-62 sec | 40679.3372 | [14 empty] | 0.011963
T-60 sec | 40679.3372 | 59.9874 | 471 |  |  | 19590 | 82.3026 | 82.5056 |  | 2.9469 | 471 | [7 empty] | T-60 sec | 40679.3372 | 59.9874 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30142.791 | 82.3026 | T-60 sec | 40679.3372 | [14 empty] | 0.012604
T-58 sec | 40679.3373 | 59.9861 | 471 |  |  | 19590 | 90.6723 | 85.3639 |  | 2.9469 | 476.8052 | [7 empty] | T-58 sec | 40679.3373 | 59.9861 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30142.791 | 90.6723 | T-58 sec | 40679.3373 | [14 empty] | 0.013885
T-56 sec | 40679.3373 | 59.9848 | 471 |  |  | 19590 | 99.2413 | 90.221 |  | 2.9469 | 484.6092 | [7 empty] | T-56 sec | 40679.3373 | 59.9848 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30142.791 | 99.2413 | T-56 sec | 40679.3373 | [14 empty] | 0.015198
T-54 sec | 40679.3373 | 59.9835 | 471 |  |  | 19590 | 107.6111 | 96.3075 |  | 2.9469 | 493.6426 | [7 empty] | T-54 sec | 40679.3373 | 59.9835 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30154.666 | 107.6111 | T-54 sec | 40679.3373 | [14 empty] | 0.016479
T-52 sec | 40679.3373 | 59.9832 | 471 |  |  | 19590 | 109.8032 | 101.031 |  | 2.9469 | 501.313 | [7 empty] | T-52 sec | 40679.3373 | 59.9832 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30154.666 | 109.8032 | T-52 sec | 40679.3373 | [14 empty] | 0.016815
T-50 sec | 40679.3374 | 59.9835 | 471 |  |  | 19590 | 107.6111 | 103.334 |  | 2.9469 | 506.5629 | [7 empty] | T-50 sec | 40679.3374 | 59.9835 | 471 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30154.666 | 107.6111 | T-50 sec | 40679.3374 | [14 empty] | 0.016479
T-48 sec | 40679.3374 | 59.9842 | 471.3 |  |  | 19590 | 103.4262 | 103.3663 |  | 2.9469 | 509.542 | [7 empty] | T-48 sec | 40679.3374 | 59.9842 | 471.3 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30150.3477 | 103.4262 | T-48 sec | 40679.3374 | [14 empty] | 0.015839
T-46 sec | 40679.3374 | 59.9851 | 471.3 |  |  | 19590 | 97.0493 | 101.1553 |  | 2.9469 | 510.2779 | [7 empty] | T-46 sec | 40679.3374 | 59.9851 | 471.3 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30150.3477 | 97.0493 | T-46 sec | 40679.3374 | [14 empty] | 0.014862
T-44 sec | 40679.3374 | 59.9855 | 471.3 |  |  | 19590 | 94.8572 | 98.951 |  | 2.9469 | 511.0205 | [7 empty] | T-44 sec | 40679.3374 | 59.9855 | 471.3 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30159.6348 | 94.8572 | T-44 sec | 40679.3374 | [14 empty] | 0.014526
T-42 sec | 40679.3375 | 59.9864 | 471.3 |  |  | 19590 | 88.6795 | 95.356 |  | 2.9469 | 510.3723 | [7 empty] | T-42 sec | 40679.3375 | 59.9864 | 471.3 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30159.6348 | 88.6795 | T-42 sec | 40679.3375 | [14 empty] | 0.01358
T-40 sec | 40679.3375 | 59.9868 | 471.9 |  |  | 19590 | 86.4874 | 92.252 |  | 2.9469 | 510.2152 | [7 empty] | T-40 sec | 40679.3375 | 59.9868 | 471.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30159.6348 | 86.4874 | T-40 sec | 40679.3375 | [14 empty] | 0.013245
T-38 sec | 40679.3375 | 59.9874 | 471.9 |  |  | 19590 | 82.3026 | 88.7697 |  | 2.9469 | 509.6798 | [7 empty] | T-38 sec | 40679.3375 | 59.9874 | 471.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30159.6348 | 82.3026 | T-38 sec | 40679.3375 | [14 empty] | 0.012604
T-36 sec | 40679.3375 | 59.9877 | 471.9 |  |  | 19590 | 80.1105 | 85.739 |  | 2.9469 | 509.596 | [7 empty] | T-36 sec | 40679.3375 | 59.9877 | 471.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30151.416 | 80.1105 | T-36 sec | 40679.3375 | [14 empty] | 0.012268
T-34 sec | 40679.3375 | 59.989 | 471.9 |  |  | 19590 | 71.7407 | 80.8396 |  | 2.9469 | 507.6435 | [7 empty] | T-34 sec | 40679.3375 | 59.989 | 471.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30151.416 | 71.7407 | T-34 sec | 40679.3375 | [14 empty] | 0.010986
T-32 sec | 40679.3376 | 59.989 | 471.9 |  |  | 19590 | 71.7407 | 77.655 |  | 2.9469 | 507.4058 | [7 empty] | T-32 sec | 40679.3376 | 59.989 | 471.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30156.1621 | 71.7407 | T-32 sec | 40679.3376 | [14 empty] | 0.010986
T-30 sec | 40679.3376 | 59.988 | 471.4 |  |  | 19590 | 78.1177 | 77.8169 |  | 2.9469 | 510.5146 | [7 empty] | T-30 sec | 40679.3376 | 59.988 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30156.1621 | 78.1177 | T-30 sec | 40679.3376 | [14 empty] | 0.011963
T-28 sec | 40679.3376 | 59.9864 | 471.4 |  |  | 19590 | 88.6795 | 81.6188 |  | 2.9469 | 517.2634 | [7 empty] | T-28 sec | 40679.3376 | 59.9864 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30156.1621 | 88.6795 | T-28 sec | 40679.3376 | [14 empty] | 0.01358
T-26 sec | 40679.3376 | 59.9855 | 471.4 |  |  | 19590 | 94.8572 | 86.2522 |  | 2.9469 | 524.8437 | [7 empty] | T-26 sec | 40679.3376 | 59.9855 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30156.1621 | 94.8572 | T-26 sec | 40679.3376 | [14 empty] | 0.014526
T-24 sec | 40679.3377 | 59.9864 | 471.4 |  |  | 19590 | 88.6795 | 87.1018 |  | 2.9469 | 528.6401 | [7 empty] | T-24 sec | 40679.3377 | 59.9864 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30164.1465 | 88.6795 | T-24 sec | 40679.3377 | [14 empty] | 0.01358
T-22 sec | 40679.3377 | 59.9893 | 471.4 |  |  | 19590 | 69.5486 | 80.9582 |  | 2.9469 | 525.4434 | [7 empty] | T-22 sec | 40679.3377 | 59.9893 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30164.1465 | 69.5486 | T-22 sec | 40679.3377 | [14 empty] | 0.010651
T-20 sec | 40679.3377 | 59.9922 | 471.4 |  |  | 19590 | 50.6171 | 70.3388 |  | 2.9469 | 517.7709 | [7 empty] | T-20 sec | 40679.3377 | 59.9922 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30164.1465 | 50.6171 | T-20 sec | 40679.3377 | [14 empty] | 0.0077515
T-18 sec | 40679.3377 | 59.9951 | 471.4 |  |  | 19590 | 31.6855 | 56.8101 |  | 2.9469 | 507.1891 | [7 empty] | T-18 sec | 40679.3377 | 59.9951 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30164.1465 | 31.6855 | T-18 sec | 40679.3377 | [14 empty] | 0.0048523
T-16 sec | 40679.3378 | 59.9958 | 471.4 | 59.9986 | 471.0875 | 19590 | 27.5006 | 46.5518 |  | 2.9469 | 499.8776 | [7 empty] | T-16 sec | 40679.3378 | 59.9958 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.9062 | 27.5006 | T-16 sec | 40679.3378 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0042114
T-14 sec | 40679.3378 | 59.9951 | 471.4 | 59.9986 | 471.0875 | 19590 | 31.6855 | 41.3486 |  | 2.9469 | 497.6213 | [7 empty] | T-14 sec | 40679.3378 | 59.9951 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.9062 | 31.6855 | T-14 sec | 40679.3378 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0048523
T-12 sec | 40679.3378 | 59.9955 | 471.4 | 59.9986 | 471.0875 | 19590 | 29.4934 | 37.1993 |  | 2.9469 | 496.4189 | [7 empty] | T-12 sec | 40679.3378 | 59.9955 | 471.4 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.7285 | 29.4934 | T-12 sec | 40679.3378 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0045166
T-10 sec | 40679.3378 | 59.9974 | 470.9 | 59.9986 | 471.0875 | 19590 | 16.9388 | 30.1081 |  | 2.9469 | 492.2746 | [7 empty] | T-10 sec | 40679.3378 | 59.9974 | 470.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.7285 | 16.9388 | T-10 sec | 40679.3378 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.002594
T-08 sec | 40679.3378 | 60 | 470.9 | 59.9986 | 471.0875 | 19590 | 0 | 19.5703 |  | 2.9469 | 484.6836 | [7 empty] | T-08 sec | 40679.3378 | 60 | 470.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.7285 | 0 | T-08 sec | 40679.3378 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0
T-06 sec | 40679.3379 | 60.0016 | 470.9 | 59.9986 | 471.0875 | 19590 | -10.5618 | 9.024 |  | 2.9469 | 477.0843 | [7 empty] | T-06 sec | 40679.3379 | 60.0016 | 470.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30203.7285 | -10.5618 | T-06 sec | 40679.3379 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0016174
T-04 sec | 40679.3379 | 60.0016 | 470.9 | 59.9986 | 471.0875 | 19590 | -10.5618 | 2.169 |  | 2.9469 | 473.1761 | [7 empty] | T-04 sec | 40679.3379 | 60.0016 | 470.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30199.6055 | -10.5618 | T-04 sec | 40679.3379 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0016174
T-02 sec | 40679.3379 | 60.002 | 470.9 | 59.9986 | 471.0875 | 19590 | -12.7539 | -3.054 |  | 2.9469 | 470.9 | [7 empty] | T-02 sec | 40679.3379 | 60.002 | 470.9 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30199.6055 | -12.7539 | T-02 sec | 40679.3379 | 59.9986 | 471.0875 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30202.7422 | 8.9676 |  |  |  | 0.0019531
T+0 sec | 40679.3379 | 59.9596 | 0 |  |  | 19590 | 263.6472 | 90.2914 |  | 0 | 564.2454 | [7 empty] | T+0 sec | 40679.3379 | 59.9596 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30199.6055 | 263.6472 | T+0 sec | 40679.3379 | [14 empty] | 0.040375 | -653
T+02 sec | 40679.338 | 59.8814 | 0 |  |  | 19590 | 774.2269 | 329.6688 |  | -4.2109 | 799.4119 | 0 | 681.8287 | 471.6779 | 471.6779 |  |  |  | T+02 sec | 40679.338 | 59.8814 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30199.6055 | 774.2269 | T+02 sec | 40679.338 | [13 empty] | 401.9816 | 0.11856 | -653
T+04 sec | 40679.338 | 59.8724 | 0 |  |  | 19590 | 833.413 | 505.9793 |  | -4.2109 | 971.5115 | 0 | 778.3896 | 467.467 | 469.5724 |  |  |  | T+04 sec | 40679.338 | 59.8724 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1094 | 833.413 | T+04 sec | 40679.338 | [13 empty] | 373.1237 | 0.12763 | -653
T+06 sec | 40679.338 | 59.8701 | 0 |  |  | 19590 | 848.1597 | 625.7424 |  | -4.2109 | 1087.0637 | 0 | 855.5581 | 463.2561 | 467.467 |  |  |  | T+06 sec | 40679.338 | 59.8701 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1094 | 848.1597 | T+06 sec | 40679.338 | [13 empty] | 366.567 | 0.12989 | -653
T+08 sec | 40679.338 | 59.8743 | 0 |  |  | 19590 | 820.6591 | 693.9632 |  | -4.2109 | 1151.0736 | 0 | 914.6612 | 459.0452 | 465.3615 |  |  |  | T+08 sec | 40679.338 | 59.8743 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1387 | 820.6591 | T+08 sec | 40679.338 | [13 empty] | 378.9865 | 0.12568 | -653
T+10 sec | 40679.3381 | 59.8808 | 0 |  |  | 19590 | 778.611 | 723.59 |  | -4.2109 | 1176.4894 | 0 | 958.2993 | 454.8343 | 463.2561 |  |  |  | T+10 sec | 40679.3381 | 59.8808 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1387 | 778.611 | T+10 sec | 40679.3381 | [13 empty] | 399.6918 | 0.11924 | -653
T+12 sec | 40679.3381 | 59.8853 | 0 |  |  | 19590 | 748.9183 | 732.4549 |  | -4.2109 | 1181.1435 | 0 | 990.1341 | 450.6234 | 461.1506 |  |  |  | T+12 sec | 40679.3381 | 59.8853 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1387 | 748.9183 | T+12 sec | 40679.3381 | [13 empty] | 415.7306 | 0.11469 | -653
T+14 sec | 40679.3381 | 59.8879 | 0 |  |  | 19590 | 732.1788 | 732.3583 |  | -4.2109 | 1176.8359 | 0 | 1013.4719 | 446.4124 | 459.0452 |  |  |  | T+14 sec | 40679.3381 | 59.8879 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30086.1387 | 732.1788 | T+14 sec | 40679.3381 | [13 empty] | 425.3531 | 0.11213 | -653
T+16 sec | 40679.3381 | 59.8895 | 0 |  |  | 19590 | 721.617 | 728.5988 |  | -4.2109 | 1168.8656 | 0 | 1030.7378 | 442.2015 | 456.9397 |  |  |  | T+16 sec | 40679.3381 | 59.8895 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30094.4258 | 721.617 | T+16 sec | 40679.3381 | [13 empty] | 431.657 | 0.11051 | -653
T+18 sec | 40679.3381 | 59.8908 | 0 |  |  | 19590 | 713.048 | 723.156 |  | -4.2109 | 1159.2119 | 0 | 1043.5852 | 437.9906 | 454.8343 |  |  |  | T+18 sec | 40679.3381 | 59.8908 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30094.4258 | 713.048 | T+18 sec | 40679.3381 | [13 empty] | 436.9105 | 0.1092 | -653
T+20 sec | 40679.3382 | 59.8918 | 0 | 59.8976 | 0 | 19590 | 706.8703 | 717.456 | 653 | -4.2109 | 1149.301 | 0 | 1053.1958 | 433.7797 | 452.7288 |  |  |  | T+20 sec | 40679.3382 | 59.8918 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30094.4258 | 706.8703 | T+20 sec | 40679.3382 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 440.778 | 0.10825 | -653
T+22 sec | 40679.3382 | 59.8924 | 0 | 59.8976 | 0 | 19590 | 702.4862 | 712.2166 | 653 | -4.2109 | 1139.8506 | 0 | 1060.417 | 429.5688 | 450.6234 |  |  |  | T+22 sec | 40679.3382 | 59.8924 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30094.4258 | 702.4862 | T+22 sec | 40679.3382 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 443.5644 | 0.10758 | -653
T+24 sec | 40679.3382 | 59.8931 | 0 | 59.8976 | 0 | 19590 | 698.3013 | 707.3462 | 653 | -4.2109 | 1130.7693 | 0 | 1065.8287 | 425.3579 | 448.5179 |  |  |  | T+24 sec | 40679.3382 | 59.8931 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30139.4863 | 698.3013 | T+24 sec | 40679.3382 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 446.2572 | 0.10694 | -653
T+26 sec | 40679.3382 | 59.8931 | 0 | 59.8976 | 0 | 19590 | 698.3013 | 704.1805 | 653 | -4.2109 | 1123.3927 | 0 | 1069.9404 | 421.147 | 446.4124 |  |  |  | T+26 sec | 40679.3382 | 59.8931 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30139.4863 | 698.3013 | T+26 sec | 40679.3382 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 446.2572 | 0.10694 | -653
T+28 sec | 40679.3383 | 59.8931 | 0 | 59.8976 | 0 | 19590 | 698.3013 | 702.1228 | 653 | -4.2109 | 1117.1241 | 0 | 1073.086 | 416.9361 | 444.307 |  |  |  | T+28 sec | 40679.3383 | 59.8931 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30133.375 | 698.3013 | T+28 sec | 40679.3383 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 446.2572 | 0.10694 | -653
T+30 sec | 40679.3383 | 59.8953 | 0 | 59.8976 | 0 | 19590 | 683.5546 | 695.6239 | 653 | -4.2109 | 1106.4143 | 0 | 1075.169 | 412.7252 | 442.2015 |  |  |  | T+30 sec | 40679.3383 | 59.8953 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30133.375 | 683.5546 | T+30 sec | 40679.3383 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 456.0126 | 0.10468 | -653
T+32 sec | 40679.3383 | 59.8979 | 0 | 59.8976 | 0 | 19590 | 666.8151 | 685.5408 | 653 | -4.2109 | 1092.1203 | 0 | 1076.1662 | 408.5143 | 440.0961 |  |  |  | T+32 sec | 40679.3383 | 59.8979 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30133.375 | 666.8151 | T+32 sec | 40679.3383 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 467.6162 | 0.10212 | -653
T+34 sec | 40679.3383 | 59.8995 | 0 | 59.8976 | 0 | 19590 | 656.2532 | 675.2902 | 653 | -4.2109 | 1077.6587 | 0 | 1076.2491 | 404.3034 | 437.9906 |  |  |  | T+34 sec | 40679.3383 | 59.8995 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30133.375 | 656.2532 | T+34 sec | 40679.3383 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 475.2463 | 0.1005 | -653
T+36 sec | 40679.3384 | 59.9008 | 0 | 59.8976 | 0 | 19590 | 647.6842 | 665.6281 | 653 | -4.2109 | 1063.7857 | 0 | 1075.5931 | 400.0924 | 435.8852 |  |  |  | T+36 sec | 40679.3384 | 59.9008 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30137.2637 | 647.6842 | T+36 sec | 40679.3384 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 481.6222 | 0.099186 | -653
T+38 sec | 40679.3384 | 59.9021 | 0 | 59.8976 | 0 | 19590 | 639.3145 | 656.4183 | 653 | -4.2109 | 1050.3651 | 0 | 1074.3317 | 395.8815 | 433.7797 |  |  |  | T+38 sec | 40679.3384 | 59.9021 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30137.2637 | 639.3145 | T+38 sec | 40679.3384 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 488.0172 | 0.097904 | -653
T+40 sec | 40679.3384 | 59.9018 | 0 | 59.8976 | 0 | 19590 | 641.3073 | 651.1294 | 653 | -4.2109 | 1040.8653 | 0 | 1072.7381 | 391.6706 | 431.6743 |  |  |  | T+40 sec | 40679.3384 | 59.9018 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30137.2637 | 641.3073 | T+40 sec | 40679.3384 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 486.4793 | 0.098209 | -653
T+42 sec | 40679.3384 | 59.9008 | 0 | 59.8976 | 0 | 19590 | 647.6842 | 649.9236 | 653 | -4.2109 | 1035.4486 | 0 | 1071.0431 | 387.4597 | 429.5688 |  |  |  | T+42 sec | 40679.3384 | 59.9008 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30137.2637 | 647.6842 | T+42 sec | 40679.3384 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 481.6222 | 0.099186 | -653
T+44 sec | 40679.3384 | 59.9008 | 0 | 59.8976 | 0 | 19590 | 647.6842 | 649.1398 | 653 | -4.2109 | 1030.4539 | 0 | 1069.2783 | 383.2488 | 427.4634 |  |  |  | T+44 sec | 40679.3384 | 59.9008 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30171.375 | 647.6842 | T+44 sec | 40679.3384 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 481.6222 | 0.099186 | -653
T+46 sec | 40679.3385 | 59.9005 | 0 | 59.8976 | 0 | 19590 | 649.8763 | 649.3976 | 653 | -4.2109 | 1026.5007 | 0 | 1067.4959 | 379.0379 | 425.3579 |  |  |  | T+46 sec | 40679.3385 | 59.9005 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30171.375 | 649.8763 | T+46 sec | 40679.3385 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 479.975 | 0.099522 | -653
T+48 sec | 40679.3385 | 59.8992 | 0 | 59.8976 | 0 | 19590 | 658.246 | 652.4945 | 653 | -4.2109 | 1025.3868 | 0 | 1065.8116 | 374.827 | 423.2524 |  |  |  | T+48 sec | 40679.3385 | 59.8992 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30168.7637 | 658.246 | T+48 sec | 40679.3385 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 473.7877 | 0.1008 | -653
T+50 sec | 40679.3385 | 59.8989 | 0 | 59.8976 | 0 | 19590 | 660.4381 | 655.2748 | 653 | -4.2109 | 1023.9561 | 0 | 1064.2018 | 370.6161 | 421.147 |  |  |  | T+50 sec | 40679.3385 | 59.8989 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30168.7637 | 660.4381 | T+50 sec | 40679.3385 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 472.1935 | 0.10114 | -653
T+52 sec | 40679.3385 | 59.8986 | 0 | 59.8976 | 0 | 19590 | 662.4309 | 657.7794 | 653 | -4.2109 | 1022.2498 | 0 | 1062.648 | 366.4052 | 419.0415 |  |  |  | T+52 sec | 40679.3385 | 59.8986 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30168.7637 | 662.4309 | T+52 sec | 40679.3385 | 59.8976 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30141.1423 | 668.5617 | 653 | 466.9448 | 470.7535 | 0.10144 | -653
T+54 sec | 40679.3386 | 59.9002 | 0 |  |  | 19590 | 651.8691 | 655.7108 |  | -4.2109 | 1015.9703 | 0 | 1060.9809 | 362.1943 | 416.9361 |  |  |  | T+54 sec | 40679.3386 | 59.9002 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30168.7637 | 651.8691 | T+54 sec | 40679.3386 | [13 empty] | 478.4872 | 0.099827 | -653
T+56 sec | 40679.3386 | 59.9024 | 0 |  |  | 19590 | 637.1224 | 649.2049 |  | -4.2109 | 1005.2534 | 0 | 1059.0593 | 357.9834 | 414.8306 |  |  |  | T+56 sec | 40679.3386 | 59.9024 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30208.9941 | 637.1224 | T+56 sec | 40679.3386 | [13 empty] | 489.7203 | 0.097569 | -653
T+58 sec | 40679.3386 | 59.9047 | 0 |  |  | 19590 | 622.3757 | 639.8146 |  | -4.2109 | 991.6523 | 0 | 1056.8124 | 353.7725 | 412.7252 |  |  |  | T+58 sec | 40679.3386 | 59.9047 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30208.9941 | 622.3757 | T+58 sec | 40679.3386 | [13 empty] | 501.4934 | 0.09531 | -653
T+60 sec | 40679.3386 | 59.9069 | 0 |  |  | 19590 | 607.629 | 628.5497 |  | -4.2109 | 976.1764 | 0 | 1054.2112 | 349.5615 | 410.6197 |  |  |  | T+60 sec | 40679.3386 | 59.9069 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30208.9941 | 607.629 | T+60 sec | 40679.3386 | [13 empty] | 513.8466 | 0.093052 | -653
T+62 sec | 40679.3387 | 59.9089 | 0 |  |  | 19590 | 595.0743 | 616.8333 |  | -4.2109 | 960.2492 | 0 | 1051.2749 | 345.3506 | 408.5143 |  |  |  | T+62 sec | 40679.3387 | 59.9089 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30208.9941 | 595.0743 | T+62 sec | 40679.3387 | [13 empty] | 524.8534 | 0.091129 | -653
T+64 sec | 40679.3387 | 59.9092 | 0 |  |  | 19590 | 592.8823 | 608.4504 |  | -4.2109 | 947.6554 | 0 | 1048.1349 | 341.1397 | 406.4088 |  |  |  | T+64 sec | 40679.3387 | 59.9092 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6641 | 592.8823 | T+64 sec | 40679.3387 | [13 empty] | 526.8238 | 0.090794 | -653
T+66 sec | 40679.3387 | 59.9086 | 0 |  |  | 19590 | 597.0671 | 604.4663 |  | -4.2109 | 939.4603 | 0 | 1044.9386 | 336.9288 | 404.3034 |  |  |  | T+66 sec | 40679.3387 | 59.9086 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6641 | 597.0671 | T+66 sec | 40679.3387 | [13 empty] | 523.0749 | 0.091434 | -653
T+68 sec | 40679.3387 | 59.9089 | 0 |  |  | 19590 | 595.0743 | 601.1791 |  | -4.2109 | 931.9622 | 0 | 1041.7107 | 332.7179 | 402.1979 |  |  |  | T+68 sec | 40679.3387 | 59.9089 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6582 | 595.0743 | T+68 sec | 40679.3387 | [13 empty] | 524.8534 | 0.091129 | -653
T+70 sec | 40679.3388 | 59.9102 | 0 |  |  | 19590 | 586.5053 | 596.0433 |  | -4.2109 | 922.6155 | 0 | 1038.4025 | 328.507 | 400.0924 |  |  |  | T+70 sec | 40679.3388 | 59.9102 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6582 | 586.5053 | T+70 sec | 40679.3388 | [13 empty] | 532.6408 | 0.089817 | -653
T+72 sec | 40679.3388 | 59.9124 | 0 |  |  | 19590 | 571.7586 | 587.5436 |  | -4.2109 | 909.905 | 0 | 1034.9296 | 324.2961 | 397.987 |  |  |  | T+72 sec | 40679.3388 | 59.9124 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6582 | 571.7586 | T+72 sec | 40679.3388 | [13 empty] | 546.5974 | 0.087559 | -653
T+74 sec | 40679.3388 | 59.9147 | 0 |  |  | 19590 | 557.0119 | 576.8575 |  | -4.2109 | 895.0079 | 0 | 1031.2475 | 320.0852 | 395.8815 |  |  |  | T+74 sec | 40679.3388 | 59.9147 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30205.6582 | 557.0119 | T+74 sec | 40679.3388 | [13 empty] | 561.3052 | 0.0853 | -653
T+76 sec | 40679.3388 | 59.9176 | 0 |  |  | 19590 | 538.0803 | 563.2855 |  | -4.2109 | 877.225 | 0 | 1027.2982 | 315.8743 | 393.7761 |  |  |  | T+76 sec | 40679.3388 | 59.9176 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30211.7539 | 538.0803 | T+76 sec | 40679.3388 | [13 empty] | 581.3886 | 0.082401 | -653
T+78 sec | 40679.3388 | 59.9192 | 0 |  |  | 19590 | 527.5185 | 550.7671 |  | -4.2109 | 860.4956 | 0 | 1023.1281 | 311.6634 | 391.6706 |  |  |  | T+78 sec | 40679.3388 | 59.9192 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30211.7539 | 527.5185 | T+78 sec | 40679.3388 | [13 empty] | 593.2303 | 0.080784 | -653
T+80 sec | 40679.3389 | 59.9208 | 0 |  |  | 19590 | 516.9567 | 538.9334 |  | -4.2109 | 844.4511 | 0 | 1018.7701 | 307.4525 | 389.5652 |  |  |  | T+80 sec | 40679.3389 | 59.9208 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30211.7539 | 516.9567 | T+80 sec | 40679.3389 | [13 empty] | 605.5645 | 0.079166 | -653
T+82 sec | 40679.3389 | 59.9221 | 0 |  |  | 19590 | 508.3876 | 528.2424 |  | -4.2109 | 829.5492 | 0 | 1014.2649 | 303.2415 | 387.4597 |  |  |  | T+82 sec | 40679.3389 | 59.9221 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30211.7539 | 508.3876 | T+82 sec | 40679.3389 | [13 empty] | 615.9547 | 0.077854 | -653
T+84 sec | 40679.3389 | 59.9231 | 0 |  |  | 19590 | 502.21 | 519.131 |  | -4.2109 | 816.2269 | 0 | 1009.6593 | 299.0306 | 385.3543 |  |  |  | T+84 sec | 40679.3389 | 59.9231 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5488 | 502.21 | T+84 sec | 40679.3389 | [13 empty] | 623.6693 | 0.076908 | -653
T+86 sec | 40679.3389 | 59.925 | 0 |  |  | 19590 | 489.4561 | 508.7448 |  | -4.2109 | 801.6298 | 0 | 1004.9314 | 294.8197 | 383.2488 |  |  |  | T+86 sec | 40679.3389 | 59.925 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5488 | 489.4561 | T+86 sec | 40679.3389 | [13 empty] | 640.2238 | 0.074955 | -653
T+88 sec | 40679.339 | 59.925 | 0 |  |  | 19590 | 489.4561 | 501.9937 |  | -4.2109 | 790.6678 | 0 | 1000.17 | 290.6088 | 381.1434 |  |  |  | T+88 sec | 40679.339 | 59.925 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5664 | 489.4561 | T+88 sec | 40679.339 | [13 empty] | 640.2238 | 0.074955 | -653
T+90 sec | 40679.339 | 59.9273 | 0 |  |  | 19590 | 474.7094 | 492.4442 |  | -4.2109 | 776.9073 | 0 | 995.3164 | 286.3979 | 379.0379 |  |  |  | T+90 sec | 40679.339 | 59.9273 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5664 | 474.7094 | T+90 sec | 40679.339 | [13 empty] | 660.4951 | 0.072697 | -653
T+92 sec | 40679.339 | 59.9325 | 0 |  |  | 19590 | 441.0311 | 474.4496 |  | -4.2109 | 754.7018 | 0 | 990.197 | 282.187 | 376.9324 |  |  |  | T+92 sec | 40679.339 | 59.9325 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5664 | 441.0311 | T+92 sec | 40679.339 | [13 empty] | 711.979 | 0.067539 | -653
T+94 sec | 40679.339 | 59.9351 | 0 |  |  | 19590 | 424.0923 | 456.8246 |  | -4.2109 | 732.8659 | 0 | 984.8359 | 277.9761 | 374.827 |  |  |  | T+94 sec | 40679.339 | 59.9351 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5664 | 424.0923 | T+94 sec | 40679.339 | [13 empty] | 741.0307 | 0.064945 | -653
T+96 sec | 40679.3391 | 59.937 | 0 |  |  | 19590 | 411.3384 | 440.9044 |  | -4.2109 | 712.7348 | 0 | 979.2828 | 273.7652 | 372.7215 |  |  |  | T+96 sec | 40679.3391 | 59.937 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5938 | 411.3384 | T+96 sec | 40679.3391 | [13 empty] | 764.519 | 0.062992 | -653
T+98 sec | 40679.3391 | 59.9377 | 0 |  |  | 19590 | 407.1286 | 429.0829 |  | -4.2109 | 696.7024 | 0 | 973.6312 | 269.5543 | 370.6161 |  |  |  | T+98 sec | 40679.3391 | 59.9377 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5938 | 407.1286 | T+98 sec | 40679.3391 | [13 empty] | 772.6024 | 0.062347 | -653
T+100 sec | 40679.3391 | 59.9393 | 0 |  |  | 19590 | 396.5668 | 417.7022 |  | -4.2109 | 681.1108 | 0 | 967.8955 | 265.3434 | 368.5106 |  |  |  | T+100 sec | 40679.3391 | 59.9393 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5938 | 396.5668 | T+100 sec | 40679.3391 | [13 empty] | 793.6553 | 0.06073 | -653
T+102 sec | 40679.3391 | 59.9418 | 0 |  |  | 19590 | 379.8273 | 404.446 |  | -4.2109 | 663.6437 | 0 | 962.0445 | 261.1325 | 366.4052 |  |  |  | T+102 sec | 40679.3391 | 59.9418 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30217.5938 | 379.8273 | T+102 sec | 40679.3391 | [13 empty] | 829.4785 | 0.058167 | -653
T+104 sec | 40679.3391 | 59.9441 | 0 |  |  | 19590 | 365.0806 | 390.6681 |  | -4.2109 | 645.6549 | 0 | 956.0749 | 256.9216 | 364.2997 |  |  |  | T+104 sec | 40679.3391 | 59.9441 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.4863 | 365.0806 | T+104 sec | 40679.3391 | [13 empty] | 863.8274 | 0.055908 | -653
T+106 sec | 40679.3392 | 59.9457 | 0 |  |  | 19590 | 354.5187 | 378.0158 |  | -4.2109 | 628.7917 | 0 | 950.0141 | 252.7106 | 362.1943 |  |  |  | T+106 sec | 40679.3392 | 59.9457 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.4863 | 354.5187 | T+106 sec | 40679.3392 | [13 empty] | 890.2304 | 0.054291 | -653
T+108 sec | 40679.3392 | 59.948 | 0 |  |  | 19590 | 339.772 | 364.6305 |  | -4.2109 | 611.1955 | 0 | 943.8538 | 248.4997 | 360.0888 |  |  |  | T+108 sec | 40679.3392 | 59.948 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.2559 | 339.772 | T+108 sec | 40679.3392 | [13 empty] | 929.9154 | 0.052032 | -653
T+110 sec | 40679.3392 | 59.9477 | 0 |  |  | 19590 | 341.7648 | 356.6275 |  | -4.2109 | 598.9816 | 0 | 937.6953 | 244.2888 | 357.9834 |  |  |  | T+110 sec | 40679.3392 | 59.9477 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.2559 | 341.7648 | T+110 sec | 40679.3392 | [13 empty] | 924.347 | 0.052338 | -653
T+112 sec | 40679.3392 | 59.9454 | 0 |  |  | 19590 | 356.5115 | 356.5869 |  | -4.2109 | 594.7301 | 0 | 931.6784 | 240.0779 | 355.8779 |  |  |  | T+112 sec | 40679.3392 | 59.9454 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.2559 | 356.5115 | T+112 sec | 40679.3392 | [13 empty] | 885.1259 | 0.054596 | -653
T+114 sec | 40679.3393 | 59.9444 | 0 |  |  | 19590 | 362.8885 | 358.7925 |  | -4.2109 | 592.7247 | 0 | 925.8344 | 235.867 | 353.7725 |  |  |  | T+114 sec | 40679.3393 | 59.9444 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30210.2559 | 362.8885 | T+114 sec | 40679.3393 | [13 empty] | 869.1776 | 0.055573 | -653
T+116 sec | 40679.3393 | 59.9441 | 0 |  |  | 19590 | 365.0806 | 360.9933 |  | -4.2109 | 590.7146 | 0 | 920.1544 | 231.6561 | 351.667 |  |  |  | T+116 sec | 40679.3393 | 59.9441 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30234.5859 | 365.0806 | T+116 sec | 40679.3393 | [13 empty] | 863.8274 | 0.055908 | -653
T+118 sec | 40679.3393 | 59.9451 | 0 |  |  | 19590 | 358.7036 | 360.1919 |  | -4.2109 | 585.7023 | 0 | 914.5802 | 227.4452 | 349.5615 |  |  |  | T+118 sec | 40679.3393 | 59.9451 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30234.5859 | 358.7036 | T+118 sec | 40679.3393 | [13 empty] | 879.5781 | 0.054932 | -653
T+120 sec | 40679.3393 | 59.946 | 0 |  |  | 19590 | 352.3267 | 357.4391 |  | -4.2109 | 578.7386 | 0 | 909.0746 | 223.2343 | 347.4561 |  |  |  | T+120 sec | 40679.3393 | 59.946 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30234.5859 | 352.3267 | T+120 sec | 40679.3393 | [13 empty] | 895.9138 | 0.053955 | -653
T+122 sec | 40679.3394 | 59.9464 | 0 |  |  | 19590 | 350.1346 | 354.8825 |  | -4.2109 | 571.9711 | 0 | 903.6374 | 219.0234 | 345.3506 |  |  |  | T+122 sec | 40679.3394 | 59.9464 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30234.5859 | 350.1346 | T+122 sec | 40679.3394 | [13 empty] | 901.6703 | 0.053619 | -653
T+124 sec | 40679.3394 | 59.9473 | 0 |  |  | 19590 | 343.9569 | 351.0585 |  | -4.2109 | 563.9362 | 0 | 898.2453 | 214.8125 | 343.2452 |  |  |  | T+124 sec | 40679.3394 | 59.9473 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.5996 | 343.9569 | T+124 sec | 40679.3394 | [13 empty] | 918.2983 | 0.052673 | -653
T+126 sec | 40679.3394 | 59.9483 | 0 |  |  | 19590 | 337.58 | 346.341 |  | -4.2109 | 555.0078 | 0 | 892.8823 | 210.6016 | 341.1397 |  |  |  | T+126 sec | 40679.3394 | 59.9483 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.5996 | 337.58 | T+126 sec | 40679.3394 | [13 empty] | 936.1186 | 0.051697 | -653
T+128 sec | 40679.3394 | 59.9489 | 0 |  |  | 19590 | 333.3951 | 341.81 |  | -4.2109 | 546.2658 | 0 | 887.5497 | 206.3906 | 339.0343 |  |  |  | T+128 sec | 40679.3394 | 59.9489 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.7305 | 333.3951 | T+128 sec | 40679.3394 | [13 empty] | 948.1938 | 0.051056 | -653
T+130 sec | 40679.3394 | 59.9499 | 0 |  |  | 19590 | 327.0181 | 336.6328 |  | -4.2109 | 536.8778 | 0 | 882.2365 | 202.1797 | 336.9288 |  |  |  | T+130 sec | 40679.3394 | 59.9499 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.7305 | 327.0181 | T+130 sec | 40679.3394 | [13 empty] | 967.2052 | 0.050079 | -653
T+132 sec | 40679.3395 | 59.9509 | 0 |  |  | 19590 | 320.6412 | 331.0357 |  | -4.2109 | 527.0698 | 0 | 876.9355 | 197.9688 | 334.8234 |  |  |  | T+132 sec | 40679.3395 | 59.9509 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.7305 | 320.6412 | T+132 sec | 40679.3395 | [13 empty] | 986.9946 | 0.049103 | -653
T+134 sec | 40679.3395 | 59.9515 | 0 |  |  | 19590 | 316.4563 | 325.9329 |  | -4.2109 | 517.7561 | 0 | 871.6534 | 193.7579 | 332.7179 |  |  |  | T+134 sec | 40679.3395 | 59.9515 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30223.7305 | 316.4563 | T+134 sec | 40679.3395 | [13 empty] | 1000.4274 | 0.048462 | -653
T+136 sec | 40679.3395 | 59.9519 | 0 |  |  | 19590 | 314.2642 | 321.8489 |  | -4.2109 | 509.4611 | 0 | 866.4043 | 189.547 | 330.6125 |  |  |  | T+136 sec | 40679.3395 | 59.9519 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30224.3926 | 314.2642 | T+136 sec | 40679.3395 | [13 empty] | 1007.6106 | 0.048126 | -653
T+138 sec | 40679.3395 | 59.9535 | 0 |  |  | 19590 | 303.9017 | 315.5674 |  | -4.2109 | 498.9687 | 0 | 861.1552 | 185.3361 | 328.507 |  |  |  | T+138 sec | 40679.3395 | 59.9535 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30224.3926 | 303.9017 | T+138 sec | 40679.3395 | [13 empty] | 1043.0132 | 0.046539 | -653
T+140 sec | 40679.3396 | 59.9551 | 0 |  |  | 19590 | 293.3398 | 307.7877 |  | -4.2109 | 486.9781 | 0 | 855.8851 | 181.1252 | 326.4015 |  |  |  | T+140 sec | 40679.3396 | 59.9551 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30224.3926 | 293.3398 | T+140 sec | 40679.3396 | [13 empty] | 1081.7516 | 0.044922 | -653
T+142 sec | 40679.3396 | 59.9557 | 0 |  |  | 19590 | 288.9557 | 301.1965 |  | -4.2109 | 476.176 | 0 | 850.6114 | 176.9143 | 324.2961 |  |  |  | T+142 sec | 40679.3396 | 59.9557 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30224.3926 | 288.9557 | T+142 sec | 40679.3396 | [13 empty] | 1098.69 | 0.04425 | -653
T+144 sec | 40679.3396 | 59.9564 | 0 |  |  | 19590 | 284.7708 | 295.4475 |  | -4.2109 | 466.2161 | 0 | 845.3457 | 172.7034 | 322.1906 |  |  |  | T+144 sec | 40679.3396 | 59.9564 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.5293 | 284.7708 | T+144 sec | 40679.3396 | [13 empty] | 1115.3609 | 0.04361 | -653
T+146 sec | 40679.3396 | 59.958 | 0 |  |  | 19590 | 274.209 | 288.014 |  | -4.2109 | 454.5717 | 0 | 840.0649 | 168.4925 | 320.0852 |  |  |  | T+146 sec | 40679.3396 | 59.958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.5293 | 274.209 | T+146 sec | 40679.3396 | [13 empty] | 1159.7742 | 0.041992 | -653
T+148 sec | 40679.3397 | 59.9612 | 0 |  |  | 19590 | 253.0853 | 275.789 |  | -4.2109 | 438.1358 | 0 | 834.7059 | 164.2816 | 317.9797 |  |  |  | T+148 sec | 40679.3397 | 59.9612 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30252.8672 | 253.0853 | T+148 sec | 40679.3397 | [13 empty] | 1260.1302 | 0.038757 | -653
T+150 sec | 40679.3397 | 59.9625 | 0 |  |  | 19590 | 244.7156 | 264.9133 |  | -4.2109 | 423.0492 | 0 | 829.2894 | 160.0707 | 315.8743 |  |  |  | T+150 sec | 40679.3397 | 59.9625 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30252.8672 | 244.7156 | T+150 sec | 40679.3397 | [13 empty] | 1304.8686 | 0.037476 | -653
T+152 sec | 40679.3397 | 59.9619 | 0 |  |  | 19590 | 248.9005 | 259.3088 |  | -4.2109 | 413.2338 | 0 | 823.886 | 155.8597 | 313.7688 |  |  |  | T+152 sec | 40679.3397 | 59.9619 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30252.8672 | 248.9005 | T+152 sec | 40679.3397 | [13 empty] | 1282.1092 | 0.038116 | -653
T+154 sec | 40679.3397 | 59.9612 | 0 |  |  | 19590 | 253.0853 | 257.1306 |  | -4.2109 | 406.8446 | 0 | 818.5393 | 151.6488 | 311.6634 |  |  |  | T+154 sec | 40679.3397 | 59.9612 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30252.8672 | 253.0853 | T+154 sec | 40679.3397 | [13 empty] | 1260.1302 | 0.038757 | -653
T+156 sec | 40679.3397 | 59.9603 | 0 |  |  | 19590 | 259.4623 | 257.9467 |  | -4.2109 | 403.4498 | 0 | 813.285 | 147.4379 | 309.5579 |  |  |  | T+156 sec | 40679.3397 | 59.9603 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30232.4492 | 259.4623 | T+156 sec | 40679.3397 | [13 empty] | 1228.0505 | 0.039734 | -653
T+158 sec | 40679.3398 | 59.9606 | 0 |  |  | 19590 | 257.4695 | 257.7797 |  | -4.2109 | 399.0719 | 0 | 808.1074 | 143.227 | 307.4525 |  |  |  | T+158 sec | 40679.3398 | 59.9606 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30232.4492 | 257.4695 | T+158 sec | 40679.3398 | [13 empty] | 1237.8986 | 0.039429 | -653
T+160 sec | 40679.3398 | 59.9622 | 0 |  |  | 19590 | 246.9077 | 253.9745 |  | -4.2109 | 391.0558 | 0 | 802.9586 | 139.0161 | 305.347 |  |  |  | T+160 sec | 40679.3398 | 59.9622 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30232.4492 | 246.9077 | T+160 sec | 40679.3398 | [13 empty] | 1292.8472 | 0.037811 | -653
T+162 sec | 40679.3398 | 59.9651 | 0 |  |  | 19590 | 227.7768 | 244.8053 |  | -4.2109 | 377.6757 | 0 | 797.7722 | 134.8052 | 303.2415 |  |  |  | T+162 sec | 40679.3398 | 59.9651 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30232.4492 | 227.7768 | T+162 sec | 40679.3398 | [13 empty] | 1405.883 | 0.034882
T+164 sec | 40679.3398 | 59.9674 | 0 |  |  | 19590 | 213.0301 | 233.684 |  | -4.2109 | 362.3435 | 0 | 792.5261 | 130.5943 | 301.1361 |  |  |  | T+164 sec | 40679.3398 | 59.9674 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.9902 | 213.0301 | T+164 sec | 40679.3398 | [13 empty] | 1507.48 | 0.032623
T+166 sec | 40679.3399 | 59.969 | 0 |  |  | 19590 | 202.4683 | 222.7585 |  | -4.2109 | 347.2071 | 0 | 787.2247 | 126.3834 | 299.0306 |  |  |  | T+166 sec | 40679.3399 | 59.969 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.9902 | 202.4683 | T+166 sec | 40679.3399 | [13 empty] | 1589.7626 | 0.031006
T+168 sec | 40679.3399 | 59.9706 | 0 |  |  | 19590 | 191.9064 | 211.9603 |  | -4.2109 | 332.1979 | 0 | 781.8714 | 122.1725 | 296.9252 |  |  |  | T+168 sec | 40679.3399 | 59.9706 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.6836 | 191.9064 | T+168 sec | 40679.3399 | [13 empty] | 1681.5463 | 0.029388
T+170 sec | 40679.3399 | 59.9732 | 0 |  |  | 19590 | 175.1669 | 199.0826 |  | -4.2109 | 315.1094 | 0 | 776.444 | 117.9616 | 294.8197 |  |  |  | T+170 sec | 40679.3399 | 59.9732 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.6836 | 175.1669 | T+170 sec | 40679.3399 | [13 empty] | 1850.9107 | 0.026825
T+172 sec | 40679.3399 | 59.9735 | 0 |  |  | 19590 | 172.9749 | 189.9449 |  | -4.2109 | 301.7608 | 0 | 770.9878 | 113.7507 | 292.7143 |  |  |  | T+172 sec | 40679.3399 | 59.9735 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.6836 | 172.9749 | T+172 sec | 40679.3399 | [13 empty] | 1875.6495 | 0.026489
T+174 sec | 40679.34 | 59.9729 | 0 |  |  | 19590 | 177.1597 | 185.4701 |  | -4.2109 | 293.075 | 0 | 765.557 | 109.5397 | 290.6088 |  |  |  | T+174 sec | 40679.34 | 59.9729 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.6836 | 177.1597 | T+174 sec | 40679.34 | [13 empty] | 1828.9805 | 0.02713
T+176 sec | 40679.34 | 59.9725 | 0 |  |  | 19590 | 179.3518 | 183.3287 |  | -4.2109 | 286.7227 | 0 | 760.1768 | 105.3288 | 288.5034 |  |  |  | T+176 sec | 40679.34 | 59.9725 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30264.9609 | 179.3518 | T+176 sec | 40679.34 | [13 empty] | 1805.4497 | 0.027466
T+178 sec | 40679.34 | 59.9732 | 0 |  |  | 19590 | 175.1669 | 180.4721 |  | -4.2109 | 279.6552 | 0 | 754.8377 | 101.1179 | 286.3979 |  |  |  | T+178 sec | 40679.34 | 59.9732 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30264.9609 | 175.1669 | T+178 sec | 40679.34 | [13 empty] | 1850.9107 | 0.026825
T+180 sec | 40679.34 | 59.9742 | 0 |  |  | 19590 | 168.79 | 176.3833 |  | -4.2109 | 271.3556 | 0 | 749.5247 | 96.907 | 284.2925 |  |  |  | T+180 sec | 40679.34 | 59.9742 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30264.9609 | 168.79 | T+180 sec | 40679.34 | [13 empty] | 1924.7625 | 0.025848
| 40679.34 | 59.9754 | 0 |  |  | 19590 | 160.4202 | 170.7962 |  | -4.2109 | 261.5576 | 0 | 744.2207 | 92.6961 | 282.187 |  |  |  |  | 40679.34 | 59.9754 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30264.9609 | 160.4202 | [15 empty] | 2031.1309 | 0.024567
| 40679.3401 | 59.9758 | 0 |  |  | 19590 | 158.2281 | 166.3974 |  | -4.2109 | 252.9478 | 0 | 738.9382 | 88.4852 | 280.0815 |  |  |  |  | 40679.3401 | 59.9758 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.625 | 158.2281 | [15 empty] | 2060.9606 | 0.024231
| 40679.3401 | 59.9761 | 0 |  |  | 19590 | 156.0361 | 162.7709 |  | -4.2109 | 245.1105 | 0 | 733.6847 | 84.2743 | 277.9761 |  |  |  |  | 40679.3401 | 59.9761 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30263.625 | 156.0361 | [15 empty] | 2091.6795 | 0.023895
| 40679.3401 | 59.9767 | 0 |  |  | 19590 | 151.8512 | 158.949 |  | -4.2109 | 237.0776 | 0 | 728.4573 | 80.0634 | 275.8706 |  |  |  |  | 40679.3401 | 59.9767 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30279.3887 | 151.8512 | [15 empty] | 2152.9421 | 0.023254
| 40679.3401 | 59.978 | 0 |  |  | 19590 | 143.4814 | 153.5354 |  | -4.2109 | 227.4531 | 0 | 723.2385 | 75.8525 | 273.7652 |  |  |  |  | 40679.3401 | 59.978 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30279.3887 | 143.4814 | [15 empty] | 2286.903 | 0.021973
| 40679.3402 | 59.9793 | 0 |  |  | 19590 | 135.1117 | 147.0871 |  | -4.2109 | 216.7939 | 0 | 718.0174 | 71.6416 | 271.6597 |  |  |  |  | 40679.3402 | 59.9793 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30279.3887 | 135.1117 | [15 empty] | 2438.6406 | 0.020691
| 40679.3402 | 59.98 | 0 |  |  | 19590 | 130.7275 | 141.3612 |  | -4.2109 | 206.8571 | 0 | 712.8015 | 67.4307 | 269.5543 |  |  |  |  | 40679.3402 | 59.98 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30279.3887 | 130.7275 | [15 empty] | 2526.4476 | 0.02002
| 40679.3402 | 59.9796 | 0 |  |  | 19590 | 132.9196 | 138.4067 |  | -4.2109 | 199.6916 | 0 | 707.6186 | 63.2198 | 267.4488 |  |  |  |  | 40679.3402 | 59.9796 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.3184 | 132.9196 | [15 empty] | 2481.7677 | 0.020355
| 40679.3402 | 59.979 | 0 |  |  | 19590 | 137.1045 | 137.9509 |  | -4.2109 | 195.025 | 0 | 702.4926 | 59.0088 | 265.3434 |  |  |  |  | 40679.3402 | 59.979 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.3184 | 137.1045 | [15 empty] | 2400.7146 | 0.020996
| 40679.3403 | 59.9796 | 0 |  |  | 19590 | 132.9196 | 136.19 |  | -4.2109 | 189.0531 | 0 | 697.4091 | 54.7979 | 263.2379 |  |  |  |  | 40679.3403 | 59.9796 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.3184 | 132.9196 | [15 empty] | 2481.7677 | 0.020355
| 40679.3403 | 59.9809 | 0 |  |  | 19590 | 124.5499 | 132.1159 |  | -4.2109 | 180.7682 | 0 | 692.344 | 50.587 | 261.1325 |  |  |  |  | 40679.3403 | 59.9809 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30255.3184 | 124.5499 | [15 empty] | 2661.4819 | 0.019073
| 40679.3403 | 59.9822 | 0 |  |  | 19590 | 115.9808 | 126.4686 |  | -4.2109 | 170.91 | 0 | 687.2815 | 46.3761 | 259.027 |  |  |  |  | 40679.3403 | 59.9822 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30260.6738 | 115.9808 | [15 empty] | 2874.5987 | 0.017761
| 40679.3403 | 59.9839 | 0 |  |  | 19590 | 105.419 | 119.1013 |  | -4.2109 | 159.3317 | 0 | 682.2051 | 42.1652 | 256.9216 |  |  |  |  | 40679.3403 | 59.9839 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30260.6738 | 105.419 | [15 empty] | 3189.3791 | 0.016144
| 40679.3403 | 59.9851 | 0 |  |  | 19590 | 97.0493 | 111.3831 |  | -4.2109 | 147.4026 | 0 | 677.1117 | 37.9543 | 254.8161 |  |  |  |  | 40679.3403 | 59.9851 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30259.9922 | 97.0493 | [15 empty] | 3492.4423 | 0.014862
| 40679.3404 | 59.9877 | 0 |  |  | 19590 | 80.1105 | 100.4377 |  | -4.2109 | 132.2463 | 0 | 671.9715 | 33.7434 | 252.7106 |  |  |  |  | 40679.3404 | 59.9877 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30259.9922 | 80.1105 | [15 empty] | 4323.9762 | 0.012268
| 40679.3404 | 59.9903 | 0 |  |  | 19590 | 63.371 | 87.4643 |  | -4.2109 | 115.062 | 0 | 666.7667 | 29.5325 | 250.6052 |  |  |  |  | 40679.3404 | 59.9903 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30259.9922 | 63.371 | [15 empty] | 5654.4304 | 0.0097046
| 40679.3404 | 59.9929 | 0 |  |  | 19590 | 46.4322 | 73.1031 |  | -4.2109 | 96.4899 | 0 | 661.4864 | 25.3216 | 248.4997 |  |  |  |  | 40679.3404 | 59.9929 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30259.9922 | 46.4322 | [15 empty] | 8210.9548 | 0.0071106
| 40679.3404 | 59.9958 | 0 |  |  | 19590 | 27.5006 | 57.1422 |  | -4.2109 | 76.3181 | 0 | 656.1178 | 21.1107 | 246.3943 |  |  |  |  | 40679.3404 | 59.9958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30274.0801 | 27.5006 | [15 empty] | 16598.4892 | 0.0042114
| 40679.3405 | 59.9965 | 0 |  |  | 19590 | 23.1165 | 45.2332 |  | -4.2109 | 60.1982 | 0 | 650.7004 | 16.8998 | 244.2888 |  |  |  |  | 40679.3405 | 59.9965 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30274.0801 | 23.1165 | [15 empty] | 21741.6831 | 0.00354
| 40679.3405 | 59.9958 | 0 |  |  | 19590 | 27.5006 | 39.0268 |  | -4.2109 | 49.7809 | 0 | 645.2867 | 12.6888 | 242.1834 |  |  |  |  | 40679.3405 | 59.9958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30274.0801 | 27.5006 | [15 empty] | 16598.4892 | 0.0042114
| 40679.3405 | 59.9961 | 0 |  |  | 19590 | 25.3085 | 34.2254 |  | -4.2109 | 40.7686 | 0 | 639.8892 | 8.4779 | 240.0779 |  |  |  |  | 40679.3405 | 59.9961 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30274.0801 | 25.3085 | [15 empty] | 18825.1159 | 0.0038757
| 40679.3405 | 59.9958 | 0 |  |  | 19590 | 27.5006 | 31.8717 |  | -4.2109 | 34.204 | 0 | 634.5292 | 4.267 | 237.9725 |  |  |  |  | 40679.3405 | 59.9958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6777 | 27.5006 | [15 empty] | 16598.4892 | 0.0042114
| 40679.3406 | 59.9948 | 0 |  |  | 19590 | 33.6783 | 32.504 |  | -4.2109 | 30.6254 | 0 | 629.2318 | 0.056124 | 235.867 |  |  |  |  | 40679.3406 | 59.9948 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6777 | 33.6783 | [15 empty] | 12448.8669 | 0.0051575
| 40679.3406 | 59.9948 | 0 |  |  | 19590 | 33.6783 | 32.915 |  | -4.2109 | 26.8254 | 0 | 623.9935 | -4.1548 | 233.7616 |  |  |  |  | 40679.3406 | 59.9948 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6484 | 33.6783 | [15 empty] | 12448.8669 | 0.0051575
| 40679.3406 | 59.998 | 0 |  |  | 19590 | 12.7539 | 25.8586 |  | -4.2109 | 15.5582 | 0 | 618.7483 | -8.3657 | 231.6561 |  |  |  |  | 40679.3406 | 59.998 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6484 | 12.7539 | [15 empty] | 81245.2368 | 0.0019531
| 40679.3406 | 59.9987 | 0 |  |  | 19590 | 8.3698 | 19.7375 |  | -4.2109 | 5.2261 | 0 | 613.5045 | -12.5766 | 229.5506 |  |  |  |  | 40679.3406 | 59.9987 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6484 | 8.3698 | [16 empty] | 0.0012817
| 40679.3406 | 60.0003 | 0 |  |  | 19590 | -2.1921 | 12.0622 |  | 0 | -2.4492 | 0 | 608.2846 | -12.5766 | 227.4812 |  |  |  |  | 40679.3406 | 60.0003 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30297.6484 | -2.1921 | [16 empty] | 0.00033569
| 40679.3407 | 60.002 | 0 |  |  | 19590 | -12.7539 | 3.3765 |  | 0 | -11.1348 | 0 | 603.0794 | -12.5766 | 225.4468 |  |  |  |  | 40679.3407 | 60.002 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30300.1035 | -12.7539 | [16 empty] | 0.0019531
| 40679.3407 | 60.0026 | 0 |  |  | 19590 | -16.9388 | -3.7338 |  | 0 | -18.2452 | 0 | 597.9017 | -12.5766 | 223.4466 |  |  |  |  | 40679.3407 | 60.0026 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30300.1035 | -16.9388 | [16 empty] | 0.002594
| 40679.3407 | 60.0023 | 0 |  |  | 19590 | -14.7467 | -7.5883 |  | 0 | -22.0997 | 0 | 592.7777 | -12.5766 | 221.4797 |  |  |  |  | 40679.3407 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30300.1035 | -14.7467 | [16 empty] | 0.0022583
| 40679.3407 | 60.002 | 0 |  |  | 19590 | -12.7539 | -9.3963 |  | 0 | -23.9077 | 0 | 587.7229 | -12.5766 | 219.5454 |  |  |  |  | 40679.3407 | 60.002 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30300.1035 | -12.7539 | [16 empty] | 0.0019531
| 40679.3408 | 60.0006 | 0 |  |  | 19590 | -4.1849 | -7.5723 |  | 0 | -22.0837 | 0 | 582.7651 | -12.5766 | 217.6427 |  |  |  |  | 40679.3408 | 60.0006 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30314.8379 | -4.1849 | [16 empty] | 0.00064087
| 40679.3408 | 59.9965 | 0 |  |  | 19590 | 23.1165 | 3.1688 |  | 0 | -11.3426 | 0 | 577.9739 | -12.5766 | 215.771 |  |  |  |  | 40679.3408 | 59.9965 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30314.8379 | 23.1165 | [15 empty] | 21741.6831 | 0.00354
| 40679.3408 | 59.9919 | 0 |  |  | 19590 | 52.8091 | 20.5429 |  | 0 | 6.0315 | 0 | 573.3984 | -12.5766 | 213.9295 |  |  |  |  | 40679.3408 | 59.9919 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30309.709 | 52.8091 | [15 empty] | 7016.6341 | 0.0080872
| 40679.3408 | 59.989 | 0 |  |  | 19590 | 71.7407 | 38.4621 |  | 0 | 23.9508 | 0 | 569.0377 | -12.5766 | 212.1175 |  |  |  |  | 40679.3408 | 59.989 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30309.709 | 71.7407 | [15 empty] | 4900.5063 | 0.010986
| 40679.3409 | 59.9877 | 0 |  |  | 19590 | 80.1105 | 53.0391 |  | 0 | 38.5277 | 0 | 564.8605 | -12.5766 | 210.3342 |  |  |  |  | 40679.3409 | 59.9877 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30309.709 | 80.1105 | [15 empty] | 4323.9762 | 0.012268
| 40679.3409 | 59.989 | 0 |  |  | 19590 | 71.7407 | 59.5846 |  | 0 | 45.0733 | 0 | 560.7996 | -12.5766 | 208.579 |  |  |  |  | 40679.3409 | 59.989 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30309.709 | 71.7407 | [15 empty] | 4900.5063 | 0.010986
| 40679.3409 | 59.9926 | 0 |  |  | 19590 | 48.6243 | 55.7485 |  | 0 | 41.2371 | 0 | 556.772 | -12.5766 | 206.8512 |  |  |  |  | 40679.3409 | 59.9926 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30319.4961 | 48.6243 | [15 empty] | 7757.0829 | 0.0074463
| 40679.3409 | 59.9958 | 0 |  |  | 19590 | 27.5006 | 45.8617 |  | 0 | 31.3504 | 0 | 552.7303 | -12.5766 | 205.1502 |  |  |  |  | 40679.3409 | 59.9958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30319.4961 | 27.5006 | [15 empty] | 16598.4892 | 0.0042114
| 40679.3409 | 59.999 | 0 |  |  | 19590 | 6.377 | 32.0421 |  | 0 | 17.5307 | 0 | 548.6448 | -12.5766 | 203.4754 |  |  |  |  | 40679.3409 | 59.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30319.4961 | 6.377 | [16 empty] | 0.00097656
| 40679.341 | 60.002 | 0 |  |  | 19590 | -12.7539 | 16.3635 |  | 0 | 1.8521 | 0 | 544.5024 | -12.5766 | 201.8262 |  |  |  |  | 40679.341 | 60.002 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30319.4961 | -12.7539 | [16 empty] | 0.0019531
| 40679.341 | 60.0049 | 0 |  |  | 19590 | -31.6855 | -0.45366 |  | 0 | -14.965 | 0 | 540.2959 | -12.5766 | 200.2019 |  |  |  |  | 40679.341 | 60.0049 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.2129 | -31.6855 | [16 empty] | 0.0048523
| 40679.341 | 60.0081 | 0 |  |  | 19590 | -52.8091 | -18.7781 |  | 0 | -33.2895 | 0 | 536.0154 | -12.5766 | 198.6021 |  |  |  |  | 40679.341 | 60.0081 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.2129 | -52.8091 | [16 empty] | 0.0080872
| 40679.341 | 60.0116 | 0 |  |  | 19590 | -75.9256 | -38.7797 |  | 0 | -53.2911 | 0 | 531.6502 | -12.5766 | 197.0261 |  |  |  |  | 40679.341 | 60.0116 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.1836 | -75.9256 | [16 empty] | 0.011627
| 40679.3411 | 60.0142 | 0 |  |  | 19590 | -92.8644 | -57.7093 |  | 0 | -72.2207 | 0 | 527.21 | -12.5766 | 195.4735 |  |  |  |  | 40679.3411 | 60.0142 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.1836 | -92.8644 | [16 empty] | 0.014221
| 40679.3411 | 60.0152 | 0 |  |  | 19590 | -99.2413 | -72.2455 |  | 0 | -86.7569 | 0 | 522.7285 | -12.5766 | 193.9437 |  |  |  |  | 40679.3411 | 60.0152 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.1836 | -99.2413 | [16 empty] | 0.015198
| 40679.3411 | 60.0155 | 0 |  |  | 19590 | -101.2341 | -82.3915 |  | 0 | -96.9029 | 0 | 518.2384 | -12.5766 | 192.4363 |  |  |  |  | 40679.3411 | 60.0155 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30357.1836 | -101.2341 | [16 empty] | 0.015503
| 40679.3411 | 60.0155 | 0 |  |  | 19590 | -101.2341 | -88.9865 |  | 0 | -103.4978 | 0 | 513.7655 | -12.5766 | 190.9506 |  |  |  |  | 40679.3411 | 60.0155 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.2578 | -101.2341 | [16 empty] | 0.015503
| 40679.3412 | 60.0168 | 0 |  |  | 19590 | -109.8032 | -96.2723 |  | 0 | -110.7837 | 0 | 509.3044 | -12.5766 | 189.4864 |  |  |  |  | 40679.3412 | 60.0168 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.2578 | -109.8032 | [16 empty] | 0.016815
| 40679.3412 | 60.0191 | 0 |  |  | 19590 | -124.5499 | -106.1694 |  | 0 | -120.6808 | 0 | 504.8364 | -12.5766 | 188.0431 |  |  |  |  | 40679.3412 | 60.0191 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.2578 | -124.5499 | [16 empty] | 0.019073
| 40679.3412 | 60.0229 | 0 |  |  | 19590 | -149.8584 | -121.4606 |  | 0 | -135.972 | 0 | 500.3237 | -12.5766 | 186.6203 |  |  |  |  | 40679.3412 | 60.0229 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.2578 | -149.8584 | [16 empty] | 0.022949
| 40679.3412 | 60.0262 | 0 |  |  | 19590 | -170.9821 | -138.7931 |  | 0 | -153.3045 | 0 | 495.7529 | -12.5766 | 185.2175 |  |  |  |  | 40679.3412 | 60.0262 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.4844 | -170.9821 | [16 empty] | 0.026184
| 40679.3412 | 60.0297 | 0 |  |  | 19590 | -194.0985 | -158.15 |  | 0 | -172.6614 | 0 | 491.1111 | -12.5766 | 183.8343 |  |  |  |  | 40679.3412 | 60.0297 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.4844 | -194.0985 | [16 empty] | 0.029724
| 40679.3413 | 60.0326 | 0 |  |  | 19590 | -213.0301 | -177.358 |  | 0 | -191.8694 | 0 | 486.4009 | -12.5766 | 182.4703 |  |  |  |  | 40679.3413 | 60.0326 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30353.832 | -213.0301 | [16 empty] | 0.032623
| 40679.3413 | 60.0346 | 0 |  |  | 19590 | -225.784 | -194.3071 |  | 0 | -208.8185 | 0 | 481.6391 | -12.5766 | 181.1252 |  |  |  |  | 40679.3413 | 60.0346 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30353.832 | -225.784 | [16 empty] | 0.034576
| 40679.3413 | 60.0352 | 0 |  |  | 19590 | -229.9689 | -206.7887 |  | 0 | -221.3001 | 0 | 476.8572 | -12.5766 | 179.7985 |  |  |  |  | 40679.3413 | 60.0352 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30353.832 | -229.9689 | [16 empty] | 0.035217
| 40679.3413 | 60.0342 | 0 |  |  | 19590 | -223.5919 | -212.6698 |  | 0 | -227.1812 | 0 | 472.1002 | -12.5766 | 178.4898 |  |  |  |  | 40679.3413 | 60.0342 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30353.832 | -223.5919 | [16 empty] | 0.034241
| 40679.3414 | 60.0336 | 0 |  |  | 19590 | -219.407 | -215.0279 |  | 0 | -229.5392 | 0 | 467.3912 | -12.5766 | 177.1988 |  |  |  |  | 40679.3414 | 60.0336 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30370.4141 | -219.407 | [16 empty] | 0.0336
| 40679.3414 | 60.0352 | 0 |  |  | 19590 | -229.9689 | -220.2572 |  | 0 | -234.7686 | 0 | 462.7101 | -12.5766 | 175.9251 |  |  |  |  | 40679.3414 | 60.0352 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30370.4141 | -229.9689 | [16 empty] | 0.035217
| 40679.3414 | 60.0381 | 0 |  |  | 19590 | -248.9005 | -230.2823 |  | 0 | -244.7937 | 0 | 458.0247 | -12.5766 | 174.6685 |  |  |  |  | 40679.3414 | 60.0381 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30370.4141 | -248.9005 | [16 empty] | 0.038116 | -653
| 40679.3414 | 60.0404 | 0 |  |  | 19590 | -263.6472 | -241.96 |  | 0 | -256.4714 | 0 | 453.324 | -12.5766 | 173.4284 |  |  |  |  | 40679.3414 | 60.0404 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30370.4141 | -263.6472 | [16 empty] | 0.040375 | -653
| 40679.3415 | 60.041 | 0 |  |  | 19590 | -268.0313 | -251.085 |  | 0 | -265.5964 | 0 | 448.6252 | -12.5766 | 172.2047 |  |  |  |  | 40679.3415 | 60.041 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30374.7871 | -268.0313 | [16 empty] | 0.041046 | -653
| 40679.3415 | 60.042 | 0 |  |  | 19590 | -274.209 | -259.1784 |  | 0 | -273.6898 | 0 | 443.9349 | -12.5766 | 170.997 |  |  |  |  | 40679.3415 | 60.042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30374.7871 | -274.209 | [16 empty] | 0.041992 | -653
| 40679.3415 | 60.0423 | 0 |  |  | 19590 | -276.4011 | -265.2063 |  | 0 | -279.7177 | 0 | 439.2661 | -12.5766 | 169.805 |  |  |  |  | 40679.3415 | 60.0423 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.1367 | -276.4011 | [16 empty] | 0.042328 | -653
| 40679.3415 | 60.0433 | 0 |  |  | 19590 | -282.778 | -271.3564 |  | 0 | -285.8678 | 0 | 434.6178 | -12.5766 | 168.6283 |  |  |  |  | 40679.3415 | 60.0433 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.1367 | -282.778 | [16 empty] | 0.043304 | -653
| 40679.3416 | 60.0443 | 0 |  |  | 19590 | -288.9557 | -277.5162 |  | 0 | -292.0275 | 0 | 429.9895 | -12.5766 | 167.4667 |  |  |  |  | 40679.3416 | 60.0443 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.1367 | -288.9557 | [16 empty] | 0.04425 | -653
| 40679.3416 | 60.0449 | 0 |  |  | 19590 | -293.3398 | -283.0544 |  | 0 | -297.5658 | 0 | 425.3847 | -12.5766 | 166.32 |  |  |  |  | 40679.3416 | 60.0449 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.1367 | -293.3398 | [16 empty] | 0.044922 | -653
| 40679.3416 | 60.0456 | 0 |  |  | 19590 | -297.5247 | -288.119 |  | 0 | -302.6304 | 0 | 420.806 | -12.5766 | 165.1877 |  |  |  |  | 40679.3416 | 60.0456 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.5332 | -297.5247 | [16 empty] | 0.045563 | -653
| 40679.3416 | 60.0459 | 0 |  |  | 19590 | -299.5175 | -292.1085 |  | 0 | -306.6199 | 0 | 416.2596 | -12.5766 | 164.0697 |  |  |  |  | 40679.3416 | 60.0459 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.5332 | -299.5175 | [16 empty] | 0.045868 | -653
| 40679.3416 | 60.0465 | 0 |  |  | 19590 | -303.9017 | -296.2361 |  | 0 | -310.7475 | 0 | 411.744 | -12.5766 | 162.9657 |  |  |  |  | 40679.3416 | 60.0465 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.5332 | -303.9017 | [16 empty] | 0.046539 | -653
| 40679.3417 | 60.0488 | 0 |  |  | 19590 | -318.6484 | -304.0804 |  | 0 | -318.5918 | 0 | 407.2358 | -12.5766 | 161.8753 |  |  |  |  | 40679.3417 | 60.0488 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.5332 | -318.6484 | [16 empty] | 0.048798 | -653
| 40679.3417 | 60.0497 | 0 |  |  | 19590 | -324.826 | -311.3414 |  | 0 | -325.8528 | 0 | 402.7383 | -12.5766 | 160.7985 |  |  |  |  | 40679.3417 | 60.0497 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30343.4648 | -324.826 | [16 empty] | 0.049744 | -653
| 40679.3417 | 60.0491 | 0 |  |  | 19590 | -320.6412 | -314.5963 |  | 0 | -329.1077 | 0 | 398.2758 | -12.5766 | 159.7348 |  |  |  |  | 40679.3417 | 60.0491 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30343.4648 | -320.6412 | [16 empty] | 0.049103 | -653
| 40679.3417 | 60.0491 | 0 |  |  | 19590 | -320.6412 | -316.712 |  | 0 | -331.2234 | 0 | 393.8546 | -12.5766 | 158.6841 |  |  |  |  | 40679.3417 | 60.0491 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30335.1191 | -320.6412 | [16 empty] | 0.049103 | -653
| 40679.3418 | 60.0504 | 0 |  |  | 19590 | -329.2102 | -321.0864 |  | 0 | -335.5978 | 0 | 389.4603 | -12.5766 | 157.6462 |  |  |  |  | 40679.3418 | 60.0504 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30335.1191 | -329.2102 | [16 empty] | 0.050415 | -653
| 40679.3418 | 60.0497 | 0 |  |  | 19590 | -324.826 | -322.3953 |  | 0 | -336.9066 | 0 | 385.1108 | -12.5766 | 156.6208 |  |  |  |  | 40679.3418 | 60.0497 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30335.1191 | -324.826 | [16 empty] | 0.049744 | -653
| 40679.3418 | 60.0485 | 0 |  |  | 19590 | -316.4563 | -320.3166 |  | 0 | -334.828 | 0 | 380.8255 | -12.5766 | 155.6076 |  |  |  |  | 40679.3418 | 60.0485 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30335.1191 | -316.4563 | [16 empty] | 0.048462 | -653
| 40679.3418 | 60.0472 | 0 |  |  | 19590 | -308.0865 | -316.0361 |  | 0 | -330.5475 | 0 | 376.6162 | -12.5766 | 154.6065 |  |  |  |  | 40679.3418 | 60.0472 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30337.2852 | -308.0865 | [16 empty] | 0.04718 | -653
| 40679.3419 | 60.0459 | 0 |  |  | 19590 | -299.5175 | -310.2546 |  | 0 | -324.766 | 0 | 372.4904 | -12.5766 | 153.6172 |  |  |  |  | 40679.3419 | 60.0459 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30337.2852 | -299.5175 | [16 empty] | 0.045868 | -653
| 40679.3419 | 60.0459 | 0 |  |  | 19590 | -299.5175 | -306.4966 |  | 0 | -321.008 | 0 | 368.4349 | -12.5766 | 152.6396 |  |  |  |  | 40679.3419 | 60.0459 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30337.2852 | -299.5175 | [16 empty] | 0.045868 | -653
| 40679.3419 | 60.0456 | 0 |  |  | 19590 | -297.5247 | -303.3565 |  | 0 | -317.8678 | 0 | 364.4447 | -12.5766 | 151.6735 |  |  |  |  | 40679.3419 | 60.0456 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30337.2852 | -297.5247 | [16 empty] | 0.045563 | -653
| 40679.3419 | 60.0443 | 0 |  |  | 19590 | -288.9557 | -298.3162 |  | 0 | -312.8276 | 0 | 360.5299 | -12.5766 | 150.7185 |  |  |  |  | 40679.3419 | 60.0443 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.1973 | -288.9557 | [16 empty] | 0.04425 | -653
| 40679.3419 | 60.043 | 0 |  |  | 19590 | -280.5859 | -292.1106 |  | 0 | -306.622 | 0 | 356.6957 | -12.5766 | 149.7746 |  |  |  |  | 40679.3419 | 60.043 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.1973 | -280.5859 | [16 empty] | 0.042969 | -653
| 40679.342 | 60.0417 | 0 |  |  | 19590 | -272.2162 | -285.1476 |  | 0 | -299.6589 | 0 | 352.9451 | -12.5766 | 148.8416 |  |  |  |  | 40679.342 | 60.0417 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.0664 | -272.2162 | [16 empty] | 0.041687 | -653
| 40679.342 | 60.0423 | 0 |  |  | 19590 | -276.4011 | -282.0863 |  | 0 | -296.5977 | 0 | 349.2545 | -12.5766 | 147.9192 |  |  |  |  | 40679.342 | 60.0423 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.0664 | -276.4011 | [16 empty] | 0.042328 | -653
| 40679.342 | 60.0446 | 0 |  |  | 19590 | -291.1478 | -285.2578 |  | 0 | -299.7692 | 0 | 345.5877 | -12.5766 | 147.0073 |  |  |  |  | 40679.342 | 60.0446 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.0664 | -291.1478 | [16 empty] | 0.044586 | -653
| 40679.342 | 60.0465 | 0 |  |  | 19590 | -303.9017 | -291.7832 |  | 0 | -306.2945 | 0 | 341.9254 | -12.5766 | 146.1057 |  |  |  |  | 40679.342 | 60.0465 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.0664 | -303.9017 | [16 empty] | 0.046539 | -653
| 40679.3421 | 60.0472 | 0 |  |  | 19590 | -308.0865 | -297.4893 |  | 0 | -312.0007 | 0 | 338.2722 | -12.5766 | 145.2142 |  |  |  |  | 40679.3421 | 60.0472 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.7734 | -308.0865 | [16 empty] | 0.04718 | -653
| 40679.3421 | 60.0462 | 0 |  |  | 19590 | -301.7096 | -298.9664 |  | 0 | -313.4778 | 0 | 334.6514 | -12.5766 | 144.3327 |  |  |  |  | 40679.3421 | 60.0462 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.7734 | -301.7096 | [16 empty] | 0.046204 | -653
| 40679.3421 | 60.0443 | 0 |  |  | 19590 | -288.9557 | -295.4627 |  | 0 | -309.9741 | 0 | 331.0899 | -12.5766 | 143.461 |  |  |  |  | 40679.3421 | 60.0443 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.7734 | -288.9557 | [16 empty] | 0.04425 | -653
| 40679.3421 | 60.0449 | 0 |  |  | 19590 | -293.3398 | -294.7197 |  | 0 | -309.2311 | 0 | 327.5717 | -12.5766 | 142.5989 |  |  |  |  | 40679.3421 | 60.0449 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.7734 | -293.3398 | [16 empty] | 0.044922 | -653
| 40679.3422 | 60.0452 | 0 |  |  | 19590 | -295.3326 | -294.9342 |  | 0 | -309.4456 | 0 | 324.0907 | -12.5766 | 141.7463 |  |  |  |  | 40679.3422 | 60.0452 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -295.3326 | [16 empty] | 0.045227 | -653
| 40679.3422 | 60.0452 | 0 |  |  | 19590 | -295.3326 | -295.0737 |  | 0 | -309.585 | 0 | 320.6468 | -12.5766 | 140.903 |  |  |  |  | 40679.3422 | 60.0452 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -295.3326 | [16 empty] | 0.045227 | -653
| 40679.3422 | 60.0456 | 0 |  |  | 19590 | -297.5247 | -295.9315 |  | 0 | -310.4429 | 0 | 317.2355 | -12.5766 | 140.0688 |  |  |  |  | 40679.3422 | 60.0456 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -297.5247 | [16 empty] | 0.045563 | -653
| 40679.3422 | 60.0462 | 0 |  |  | 19590 | -301.7096 | -297.9539 |  | 0 | -312.4652 | 0 | 313.85 | -12.5766 | 139.2437 |  |  |  |  | 40679.3422 | 60.0462 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -301.7096 | [16 empty] | 0.046204 | -653
| 40679.3422 | 60.0465 | 0 |  |  | 19590 | -303.9017 | -300.0356 |  | 0 | -314.547 | 0 | 310.4896 | -12.5766 | 138.4275 |  |  |  |  | 40679.3422 | 60.0465 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -303.9017 | [16 empty] | 0.046539 | -653
| 40679.3423 | 60.0465 | 0 |  |  | 19590 | -303.9017 | -301.3887 |  | 0 | -315.9001 | 0 | 307.1577 | -12.5766 | 137.62 |  |  |  |  | 40679.3423 | 60.0465 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30372.3848 | -303.9017 | [16 empty] | 0.046539 | -653
| 40679.3423 | 60.0452 | 0 |  |  | 19590 | -295.3326 | -299.2691 |  | 0 | -313.7805 | 0 | 303.8723 | -12.5766 | 136.8211 |  |  |  |  | 40679.3423 | 60.0452 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30349.0977 | -295.3326 | [16 empty] | 0.045227 | -653
| 40679.3423 | 60.0436 | 0 |  |  | 19590 | -284.7708 | -294.1947 |  | 0 | -308.7061 | 0 | 300.6483 | -12.5766 | 136.0306 |  |  |  |  | 40679.3423 | 60.0436 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30349.0977 | -284.7708 | [16 empty] | 0.04361 | -653
| 40679.3423 | 60.042 | 0 |  |  | 19590 | -274.209 | -287.1997 |  | 0 | -301.7111 | 0 | 297.4945 | -12.5766 | 135.2485 |  |  |  |  | 40679.3423 | 60.042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30349.0977 | -274.209 | [16 empty] | 0.041992 | -653
| 40679.3424 | 60.0407 | 0 |  |  | 19590 | -265.8392 | -279.7235 |  | 0 | -294.2349 | 0 | 294.4126 | -12.5766 | 134.4745 |  |  |  |  | 40679.3424 | 60.0407 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30349.0977 | -265.8392 | [16 empty] | 0.04071 | -653
| 40679.3424 | 60.0388 | 0 |  |  | 19590 | -253.0853 | -270.4002 |  | 0 | -284.9115 | 0 | 291.4109 | -12.5766 | 133.7086 |  |  |  |  | 40679.3424 | 60.0388 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.6484 | -253.0853 | [16 empty] | 0.038757 | -653
| 40679.3424 | 60.0359 | 0 |  |  | 19590 | -234.1537 | -257.7139 |  | 0 | -272.2253 | 0 | 288.5056 | -12.5766 | 132.9507 |  |  |  |  | 40679.3424 | 60.0359 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.6484 | -234.1537 | [16 empty] | 0.035858
| 40679.3424 | 60.0339 | 0 |  |  | 19590 | -221.5991 | -245.0737 |  | 0 | -259.5851 | 0 | 285.6949 | -12.5766 | 132.2005 |  |  |  |  | 40679.3424 | 60.0339 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.8789 | -221.5991 | [16 empty] | 0.033936
| 40679.3425 | 60.0336 | 0 |  |  | 19590 | -219.407 | -236.0904 |  | 0 | -250.6018 | 0 | 282.9587 | -12.5766 | 131.4581 |  |  |  |  | 40679.3425 | 60.0336 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.8789 | -219.407 | [16 empty] | 0.0336
| 40679.3425 | 60.0326 | 0 |  |  | 19590 | -213.0301 | -228.0193 |  | 0 | -242.5307 | 0 | 280.2912 | -12.5766 | 130.7232 |  |  |  |  | 40679.3425 | 60.0326 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.8789 | -213.0301 | [16 empty] | 0.032623
| 40679.3425 | 60.0301 | 0 |  |  | 19590 | -196.2906 | -216.9142 |  | 0 | -231.4256 | 0 | 277.7068 | -12.5766 | 129.9958 |  |  |  |  | 40679.3425 | 60.0301 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30363.8789 | -196.2906 | [16 empty] | 0.03006
| 40679.3425 | 60.0275 | 0 |  |  | 19590 | -179.3518 | -203.7674 |  | 0 | -218.2788 | 0 | 275.2144 | -12.5766 | 129.2757 |  |  |  |  | 40679.3425 | 60.0275 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.7676 | -179.3518 | [16 empty] | 0.027466
| 40679.3425 | 60.0268 | 0 |  |  | 19590 | -175.1669 | -193.7572 |  | 0 | -208.2686 | 0 | 272.797 | -12.5766 | 128.5629 |  |  |  |  | 40679.3425 | 60.0268 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.7676 | -175.1669 | [16 empty] | 0.026825
| 40679.3426 | 60.0258 | 0 |  |  | 19590 | -168.79 | -185.0187 |  | 0 | -199.5301 | 0 | 270.4471 | -12.5766 | 127.8572 |  |  |  |  | 40679.3426 | 60.0258 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.7676 | -168.79 | [16 empty] | 0.025848
| 40679.3426 | 60.0236 | 0 |  |  | 19590 | -154.0433 | -174.1773 |  | 0 | -188.6887 | 0 | 268.1741 | -12.5766 | 127.1585 |  |  |  |  | 40679.3426 | 60.0236 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.7676 | -154.0433 | [16 empty] | 0.02359
| 40679.3426 | 60.022 | 0 |  |  | 19590 | -143.4814 | -163.4337 |  | 0 | -177.9451 | 0 | 265.9765 | -12.5766 | 126.4668 |  |  |  |  | 40679.3426 | 60.022 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30374.332 | -143.4814 | [16 empty] | 0.021973
| 40679.3426 | 60.0216 | 0 |  |  | 19590 | -141.2894 | -155.6832 |  | 0 | -170.1946 | 0 | 263.8384 | -12.5766 | 125.7818 |  |  |  |  | 40679.3426 | 60.0216 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30374.332 | -141.2894 | [16 empty] | 0.021637
| 40679.3427 | 60.0223 | 0 |  |  | 19590 | -145.6735 | -152.1798 |  | 0 | -166.6912 | 0 | 261.7383 | -12.5766 | 125.1036 |  |  |  |  | 40679.3427 | 60.0223 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.6738 | -145.6735 | [16 empty] | 0.022308
| 40679.3427 | 60.0213 | 0 |  |  | 19590 | -139.2966 | -147.6707 |  | 0 | -162.1821 | 0 | 259.6804 | -12.5766 | 124.432 |  |  |  |  | 40679.3427 | 60.0213 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.6738 | -139.2966 | [16 empty] | 0.021332
| 40679.3427 | 60.0213 | 0 |  |  | 19590 | -139.2966 | -144.7397 |  | 0 | -159.2511 | 0 | 257.6566 | -12.5766 | 123.7669 |  |  |  |  | 40679.3427 | 60.0213 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.6738 | -139.2966 | [16 empty] | 0.021332
| 40679.3427 | 60.02 | 0 |  |  | 19590 | -130.7275 | -139.8355 |  | 0 | -154.3469 | 0 | 255.6758 | -12.5766 | 123.1082 |  |  |  |  | 40679.3427 | 60.02 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30364.6738 | -130.7275 | [16 empty] | 0.02002
| 40679.3428 | 60.0178 | 0 |  |  | 19590 | -115.9808 | -131.4863 |  | 0 | -145.9977 | 0 | 253.7539 | -12.5766 | 122.4559 |  |  |  |  | 40679.3428 | 60.0178 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.5586 | -115.9808 | [16 empty] | 0.017761
| 40679.3428 | 60.0158 | 0 |  |  | 19590 | -103.4262 | -121.6653 |  | 0 | -136.1767 | 0 | 251.8971 | -12.5766 | 121.8098 |  |  |  |  | 40679.3428 | 60.0158 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.5586 | -103.4262 | [16 empty] | 0.015839
| 40679.3428 | 60.0129 | 0 |  |  | 19590 | -84.2953 | -108.5858 |  | 0 | -123.0972 | 0 | 250.1199 | -12.5766 | 121.1699 |  |  |  |  | 40679.3428 | 60.0129 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.5586 | -84.2953 | [16 empty] | 0.012909
| 40679.3428 | 60.0113 | 0 |  |  | 19590 | -73.9328 | -96.4573 |  | 0 | -110.9686 | 0 | 248.4166 | -12.5766 | 120.536 |  |  |  |  | 40679.3428 | 60.0113 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.5586 | -73.9328 | [16 empty] | 0.011322
| 40679.3428 | 60.01 | 0 |  |  | 19590 | -65.3638 | -85.5745 |  | 0 | -100.0859 | 0 | 246.7805 | -12.5766 | 119.9081 |  |  |  |  | 40679.3428 | 60.01 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.6875 | -65.3638 | [16 empty] | 0.01001
| 40679.3429 | 60.0094 | 0 |  |  | 19590 | -61.1789 | -77.0361 |  | 0 | -91.5474 | 0 | 245.1995 | -12.5766 | 119.2861 |  |  |  |  | 40679.3429 | 60.0094 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30350.6875 | -61.1789 | [16 empty] | 0.0093689
| 40679.3429 | 60.0078 | 0 |  |  | 19590 | -50.6171 | -67.7894 |  | 0 | -82.3008 | 0 | 243.6762 | -12.5766 | 118.6699 |  |  |  |  | 40679.3429 | 60.0078 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30344.5234 | -50.6171 | [16 empty] | 0.0077515
| 40679.3429 | 60.0052 | 0 |  |  | 19590 | -33.6783 | -55.8505 |  | 0 | -70.3619 | 0 | 242.2224 | -12.5766 | 118.0595 |  |  |  |  | 40679.3429 | 60.0052 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30344.5234 | -33.6783 | [16 empty] | 0.0051575
| 40679.3429 | 60.0045 | 0 |  |  | 19590 | -29.4934 | -46.6255 |  | 0 | -61.1369 | 0 | 240.8244 | -12.5766 | 117.4547 |  |  |  |  | 40679.3429 | 60.0045 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30344.5234 | -29.4934 | [16 empty] | 0.0045166
| 40679.343 | 60.0061 | 0 |  |  | 19590 | -40.0552 | -44.3259 |  | 0 | -58.8373 | 0 | 239.4498 | -12.5766 | 116.8555 |  |  |  |  | 40679.343 | 60.0061 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30344.5234 | -40.0552 | [16 empty] | 0.006134
| 40679.343 | 60.0061 | 0 |  |  | 19590 | -40.0552 | -42.8312 |  | 0 | -57.3426 | 0 | 238.0946 | -12.5766 | 116.2618 |  |  |  |  | 40679.343 | 60.0061 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.3652 | -40.0552 | [16 empty] | 0.006134
| 40679.343 | 60.0055 | 0 |  |  | 19590 | -35.8704 | -40.3949 |  | 0 | -54.9063 | 0 | 236.7628 | -12.5766 | 115.6734 |  |  |  |  | 40679.343 | 60.0055 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.3652 | -35.8704 | [16 empty] | 0.0054932
| 40679.343 | 60.0052 | 0 |  |  | 19590 | -33.6783 | -38.0441 |  | 0 | -52.5555 | 0 | 235.4536 | -12.5766 | 115.0905 |  |  |  |  | 40679.343 | 60.0052 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.3652 | -33.6783 | [16 empty] | 0.0051575
| 40679.3431 | 60.0039 | 0 |  |  | 19590 | -25.3085 | -33.5866 |  | 0 | -48.098 | 0 | 234.1764 | -12.5766 | 114.5128 |  |  |  |  | 40679.3431 | 60.0039 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30354.3652 | -25.3085 | [16 empty] | 0.0038757
| 40679.3431 | 60.0026 | 0 |  |  | 19590 | -16.9388 | -27.7599 |  | 0 | -42.2713 | 0 | 232.9367 | -12.5766 | 113.9403 |  |  |  |  | 40679.3431 | 60.0026 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.3066 | -16.9388 | [16 empty] | 0.002594
| 40679.3431 | 60.0013 | 0 |  |  | 19590 | -8.3698 | -20.9733 |  | 0 | -35.4847 | 0 | 231.7384 | -12.5766 | 113.373 |  |  |  |  | 40679.3431 | 60.0013 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.3066 | -8.3698 | [16 empty] | 0.0012817
| 40679.3431 | 60.0013 | 0 |  |  | 19590 | -8.3698 | -16.5621 |  | 0 | -31.0735 | 0 | 230.5703 | -12.5766 | 112.8107 |  |  |  |  | 40679.3431 | 60.0013 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.7793 | -8.3698 | [16 empty] | 0.0012817
| 40679.3431 | 60.0006 | 0 |  |  | 19590 | -4.1849 | -12.2301 |  | 0 | -26.7414 | 0 | 229.4318 | -12.5766 | 112.2534 |  |  |  |  | 40679.3431 | 60.0006 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.7793 | -4.1849 | [16 empty] | 0.00064087
| 40679.3432 | 60.0003 | 0 |  |  | 19590 | -2.1921 | -8.7168 |  | 0 | -23.2281 | 0 | 228.3187 | -12.5766 | 111.7011 |  |  |  |  | 40679.3432 | 60.0003 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.7793 | -2.1921 | [16 empty] | 0.00033569
| 40679.3432 | 60.0023 | 0 |  |  | 19590 | -14.7467 | -10.8272 |  | 0 | -25.3386 | 0 | 227.2062 | -12.5766 | 111.1536 |  |  |  |  | 40679.3432 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.7793 | -14.7467 | [16 empty] | 0.0022583
| 40679.3432 | 60.0042 | 0 |  |  | 19590 | -27.5006 | -16.6629 |  | 0 | -31.1743 | 0 | 226.0779 | -12.5766 | 110.6109 |  |  |  |  | 40679.3432 | 60.0042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.334 | -27.5006 | [16 empty] | 0.0042114
| 40679.3432 | 60.0068 | 0 |  |  | 19590 | -44.2401 | -26.3149 |  | 0 | -40.8263 | 0 | 224.9175 | -12.5766 | 110.073 |  |  |  |  | 40679.3432 | 60.0068 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.334 | -44.2401 | [16 empty] | 0.0067749
| 40679.3433 | 60.009 | 0 |  |  | 19590 | -58.9868 | -37.7501 |  | 0 | -52.2615 | 0 | 223.7175 | -12.5766 | 109.5397 |  |  |  |  | 40679.3433 | 60.009 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.334 | -58.9868 | [16 empty] | 0.0090332
| 40679.3433 | 60.0129 | 0 |  |  | 19590 | -84.2953 | -54.0409 |  | 0 | -68.5523 | 0 | 222.4578 | -12.5766 | 109.0111 |  |  |  |  | 40679.3433 | 60.0129 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30366.334 | -84.2953 | [16 empty] | 0.012909
| 40679.3433 | 60.0149 | 0 |  |  | 19590 | -97.0493 | -69.0938 |  | 0 | -83.6052 | 0 | 221.1442 | -12.5766 | 108.487 |  |  |  |  | 40679.3433 | 60.0149 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.8457 | -97.0493 | [16 empty] | 0.014862
| 40679.3433 | 60.0145 | 0 |  |  | 19590 | -94.8572 | -78.111 |  | 0 | -92.6224 | 0 | 219.8033 | -12.5766 | 107.9674 |  |  |  |  | 40679.3433 | 60.0145 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.8457 | -94.8572 | [16 empty] | 0.014526
| 40679.3434 | 60.0142 | 0 |  |  | 19590 | -92.8644 | -83.2747 |  | 0 | -97.7861 | 0 | 218.4519 | -12.5766 | 107.4523 |  |  |  |  | 40679.3434 | 60.0142 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.0469 | -92.8644 | [16 empty] | 0.014221
| 40679.3434 | 60.0152 | 0 |  |  | 19590 | -99.2413 | -88.863 |  | 0 | -103.3744 | 0 | 217.0882 | -12.5766 | 106.9415 |  |  |  |  | 40679.3434 | 60.0152 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.0469 | -99.2413 | [16 empty] | 0.015198
| 40679.3434 | 60.0161 | 0 |  |  | 19590 | -105.419 | -94.6576 |  | 0 | -109.169 | 0 | 215.7116 | -12.5766 | 106.4351 |  |  |  |  | 40679.3434 | 60.0161 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.0469 | -105.419 | [16 empty] | 0.016144
| 40679.3434 | 60.0168 | 0 |  |  | 19590 | -109.8032 | -99.9586 |  | 0 | -114.4699 | 0 | 214.3243 | -12.5766 | 105.9329 |  |  |  |  | 40679.3434 | 60.0168 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30373.0469 | -109.8032 | [16 empty] | 0.016815
| 40679.3434 | 60.0175 | 0 |  |  | 19590 | -113.988 | -104.8689 |  | 0 | -119.3803 | 0 | 212.928 | -12.5766 | 105.435 |  |  |  |  | 40679.3434 | 60.0175 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30369.7695 | -113.988 | [16 empty] | 0.017456
| 40679.3435 | 60.0171 | 0 |  |  | 19590 | -111.796 | -107.2934 |  | 0 | -121.8047 | 0 | 211.5333 | -12.5766 | 104.9412 |  |  |  |  | 40679.3435 | 60.0171 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30369.7695 | -111.796 | [16 empty] | 0.01712
| 40679.3435 | 60.0168 | 0 |  |  | 19590 | -109.8032 | -108.1718 |  | 0 | -122.6832 | 0 | 210.1465 | -12.5766 | 104.4516 |  |  |  |  | 40679.3435 | 60.0168 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30369.7695 | -109.8032 | [16 empty] | 0.016815
| 40679.3435 | 60.0165 | 0 |  |  | 19590 | -107.6111 | -107.9755 |  | 0 | -122.4869 | 0 | 208.772 | -12.5766 | 103.966 |  |  |  |  | 40679.3435 | 60.0165 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30369.7695 | -107.6111 | [16 empty] | 0.016479
| 40679.3435 | 60.0161 | 0 |  |  | 19590 | -105.419 | -107.0808 |  | 0 | -121.5921 | 0 | 207.4125 | -12.5766 | 103.4844 |  |  |  |  | 40679.3435 | 60.0161 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.9941 | -105.419 | [16 empty] | 0.016144
| 40679.3436 | 60.0175 | 0 |  |  | 19590 | -113.988 | -109.4983 |  | 0 | -124.0097 | 0 | 206.0542 | -12.5766 | 103.0068 |  |  |  |  | 40679.3436 | 60.0175 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.9941 | -113.988 | [16 empty] | 0.017456
| 40679.3436 | 60.0178 | 0 |  |  | 19590 | -115.9808 | -111.7672 |  | 0 | -126.2786 | 0 | 204.6977 | -12.5766 | 102.5331 |  |  |  |  | 40679.3436 | 60.0178 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.1582 | -115.9808 | [16 empty] | 0.017761
| 40679.3436 | 60.0178 | 0 |  |  | 19590 | -115.9808 | -113.242 |  | 0 | -127.7533 | 0 | 203.3463 | -12.5766 | 102.0632 |  |  |  |  | 40679.3436 | 60.0178 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.1582 | -115.9808 | [16 empty] | 0.017761
| 40679.3436 | 60.0165 | 0 |  |  | 19590 | -107.6111 | -111.2712 |  | 0 | -125.7825 | 0 | 202.0138 | -12.5766 | 101.5972 |  |  |  |  | 40679.3436 | 60.0165 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.1582 | -107.6111 | [16 empty] | 0.016479
| 40679.3437 | 60.0158 | 0 |  |  | 19590 | -103.4262 | -108.5254 |  | 0 | -123.0368 | 0 | 200.7031 | -12.5766 | 101.135 |  |  |  |  | 40679.3437 | 60.0158 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.1582 | -103.4262 | [16 empty] | 0.015839
| 40679.3437 | 60.0165 | 0 |  |  | 19590 | -107.6111 | -108.2054 |  | 0 | -122.7168 | 0 | 199.4042 | -12.5766 | 100.6765 |  |  |  |  | 40679.3437 | 60.0165 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9375 | -107.6111 | [16 empty] | 0.016479
| 40679.3437 | 60.0158 | 0 |  |  | 19590 | -103.4262 | -106.5327 |  | 0 | -121.0441 | 0 | 198.1224 | -12.5766 | 100.2216 |  |  |  |  | 40679.3437 | 60.0158 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9375 | -103.4262 | [16 empty] | 0.015839
| 40679.3437 | 60.0136 | 0 |  |  | 19590 | -88.6795 | -100.2841 |  | 0 | -114.7955 | 0 | 196.8757 | -12.5766 | 99.7704 |  |  |  |  | 40679.3437 | 60.0136 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9375 | -88.6795 | [16 empty] | 0.01358
| 40679.3438 | 60.0116 | 0 |  |  | 19590 | -75.9256 | -91.7586 |  | 0 | -106.27 | 0 | 195.6728 | -12.5766 | 99.3228 |  |  |  |  | 40679.3438 | 60.0116 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9375 | -75.9256 | [16 empty] | 0.011627
| 40679.3438 | 60.0113 | 0 |  |  | 19590 | -73.9328 | -85.5196 |  | 0 | -100.031 | 0 | 194.504 | -12.5766 | 98.8788 |  |  |  |  | 40679.3438 | 60.0113 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30371.8516 | -73.9328 | [16 empty] | 0.011322
| 40679.3438 | 60.0113 | 0 |  |  | 19590 | -73.9328 | -81.4642 |  | 0 | -95.9756 | 0 | 193.3604 | -12.5766 | 98.4383 |  |  |  |  | 40679.3438 | 60.0113 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30371.8516 | -73.9328 | [16 empty] | 0.011322
| 40679.3438 | 60.011 | 0 |  |  | 19590 | -71.7407 | -78.061 |  | 0 | -92.5724 | 0 | 192.2391 | -12.5766 | 98.0012 |  |  |  |  | 40679.3438 | 60.011 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30362.6523 | -71.7407 | [16 empty] | 0.010986
| 40679.3438 | 60.011 | 0 |  |  | 19590 | -71.7407 | -75.8489 |  | 0 | -90.3603 | 0 | 191.1352 | -12.5766 | 97.5676 |  |  |  |  | 40679.3438 | 60.011 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30362.6523 | -71.7407 | [16 empty] | 0.010986
| 40679.3439 | 60.0129 | 0 |  |  | 19590 | -84.2953 | -78.8052 |  | 0 | -93.3165 | 0 | 190.0283 | -12.5766 | 97.1373 |  |  |  |  | 40679.3439 | 60.0129 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30362.6523 | -84.2953 | [16 empty] | 0.012909
| 40679.3439 | 60.0149 | 0 |  |  | 19590 | -97.0493 | -85.1906 |  | 0 | -99.702 | 0 | 188.9054 | -12.5766 | 96.7104 |  |  |  |  | 40679.3439 | 60.0149 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30362.6523 | -97.0493 | [16 empty] | 0.014862
| 40679.3439 | 60.0178 | 0 |  |  | 19590 | -115.9808 | -95.9672 |  | 0 | -110.4786 | 0 | 187.7494 | -12.5766 | 96.2868 |  |  |  |  | 40679.3439 | 60.0178 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30395.4648 | -115.9808 | [16 empty] | 0.017761
| 40679.3439 | 60.0178 | 0 |  |  | 19590 | -115.9808 | -102.972 |  | 0 | -117.4833 | 0 | 186.5755 | -12.5766 | 95.8665 |  |  |  |  | 40679.3439 | 60.0178 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30395.4648 | -115.9808 | [16 empty] | 0.017761
| 40679.344 | 60.0184 | 0 |  |  | 19590 | -120.1657 | -108.9898 |  | 0 | -123.5012 | 0 | 185.3874 | -12.5766 | 95.4494 |  |  |  |  | 40679.344 | 60.0184 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30395.4648 | -120.1657 | [16 empty] | 0.018402
| 40679.344 | 60.0181 | 0 |  |  | 19590 | -118.1729 | -112.2039 |  | 0 | -126.7153 | 0 | 184.1962 | -12.5766 | 95.0355 |  |  |  |  | 40679.344 | 60.0181 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30395.4648 | -118.1729 | [16 empty] | 0.018097
| 40679.344 | 60.0175 | 0 |  |  | 19590 | -113.988 | -112.8283 |  | 0 | -127.3397 | 0 | 183.0116 | -12.5766 | 94.6248 |  |  |  |  | 40679.344 | 60.0175 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30397.0254 | -113.988 | [16 empty] | 0.017456
| 40679.344 | 60.0152 | 0 |  |  | 19590 | -99.2413 | -108.0729 |  | 0 | -122.5843 | 0 | 181.8541 | -12.5766 | 94.2172 |  |  |  |  | 40679.344 | 60.0152 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30397.0254 | -99.2413 | [16 empty] | 0.015198
| 40679.3441 | 60.0152 | 0 |  |  | 19590 | -99.2413 | -104.9818 |  | 0 | -119.4932 | 0 | 180.7169 | -12.5766 | 93.8126 |  |  |  |  | 40679.3441 | 60.0152 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30396.666 | -99.2413 | [16 empty] | 0.015198
| 40679.3441 | 60.0139 | 0 |  |  | 19590 | -90.6723 | -99.9735 |  | 0 | -114.4849 | 0 | 179.6071 | -12.5766 | 93.4112 |  |  |  |  | 40679.3441 | 60.0139 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30396.666 | -90.6723 | [16 empty] | 0.013885
| 40679.3441 | 60.0175 | 0 |  |  | 19590 | -113.988 | -104.8786 |  | 0 | -119.39 | 0 | 178.4873 | -12.5766 | 93.0127 |  |  |  |  | 40679.3441 | 60.0175 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30396.666 | -113.988 | [16 empty] | 0.017456
| 40679.3441 | 60.0191 | 0 |  |  | 19590 | -124.5499 | -111.7635 |  | 0 | -126.2749 | 0 | 177.3501 | -12.5766 | 92.6173 |  |  |  |  | 40679.3441 | 60.0191 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30396.666 | -124.5499 | [16 empty] | 0.019073
| 40679.3441 | 60.0191 | 0 |  |  | 19590 | -124.5499 | -116.2388 |  | 0 | -130.7501 | 0 | 176.2048 | -12.5766 | 92.2247 |  |  |  |  | 40679.3441 | 60.0191 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.6152 | -124.5499 | [16 empty] | 0.019073
| 40679.3442 | 60.0204 | 0 |  |  | 19590 | -132.9196 | -122.0771 |  | 0 | -136.5884 | 0 | 175.0463 | -12.5766 | 91.8351 |  |  |  |  | 40679.3442 | 60.0204 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.6152 | -132.9196 | [16 empty] | 0.020355
| 40679.3442 | 60.0187 | 0 |  |  | 19590 | -122.3578 | -122.1753 |  | 0 | -136.6867 | 0 | 173.896 | -12.5766 | 91.4484 |  |  |  |  | 40679.3442 | 60.0187 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.6152 | -122.3578 | [16 empty] | 0.018738
| 40679.3442 | 60.0187 | 0 |  |  | 19590 | -122.3578 | -122.2392 |  | 0 | -136.7506 | 0 | 172.7539 | -12.5766 | 91.0646 |  |  |  |  | 40679.3442 | 60.0187 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30388.6152 | -122.3578 | [16 empty] | 0.018738
| 40679.3442 | 60.0197 | 0 |  |  | 19590 | -128.7347 | -124.5126 |  | 0 | -139.024 | 0 | 171.6119 | -12.5766 | 90.6835 |  |  |  |  | 40679.3442 | 60.0197 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.7754 | -128.7347 | [16 empty] | 0.019714
| 40679.3443 | 60.0197 | 0 |  |  | 19590 | -128.7347 | -125.9904 |  | 0 | -140.5017 | 0 | 170.4728 | -12.5766 | 90.3053 |  |  |  |  | 40679.3443 | 60.0197 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.7754 | -128.7347 | [16 empty] | 0.019714
| 40679.3443 | 60.0197 | 0 |  |  | 19590 | -128.7347 | -126.9509 |  | 0 | -141.4623 | 0 | 169.3384 | -12.5766 | 89.9298 |  |  |  |  | 40679.3443 | 60.0197 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30382.959 | -128.7347 | [16 empty] | 0.019714
| 40679.3443 | 60.0184 | 0 |  |  | 19590 | -120.1657 | -124.5761 |  | 0 | -139.0875 | 0 | 168.221 | -12.5766 | 89.5571 |  |  |  |  | 40679.3443 | 60.0184 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30382.959 | -120.1657 | [16 empty] | 0.018402
| 40679.3443 | 60.0149 | 0 |  |  | 19590 | -97.0493 | -114.9417 |  | 0 | -129.4531 | 0 | 167.1463 | -12.5766 | 89.187 |  |  |  |  | 40679.3443 | 60.0149 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30382.959 | -97.0493 | [16 empty] | 0.014862
| 40679.3444 | 60.0136 | 0 |  |  | 19590 | -88.6795 | -105.7499 |  | 0 | -120.2613 | 0 | 166.1125 | -12.5766 | 88.8196 |  |  |  |  | 40679.3444 | 60.0136 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30382.959 | -88.6795 | [16 empty] | 0.01358
| 40679.3444 | 60.0139 | 0 |  |  | 19590 | -90.6723 | -100.4728 |  | 0 | -114.9841 | 0 | 165.105 | -12.5766 | 88.4549 |  |  |  |  | 40679.3444 | 60.0139 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.4824 | -90.6723 | [16 empty] | 0.013885
| 40679.3444 | 60.0123 | 0 |  |  | 19590 | -80.1105 | -93.346 |  | 0 | -107.8573 | 0 | 164.1301 | -12.5766 | 88.0928 |  |  |  |  | 40679.3444 | 60.0123 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.4824 | -80.1105 | [16 empty] | 0.012268
| 40679.3444 | 60.01 | 0 |  |  | 19590 | -65.3638 | -83.5522 |  | 0 | -98.0636 | 0 | 163.197 | -12.5766 | 87.7333 |  |  |  |  | 40679.3444 | 60.01 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.4824 | -65.3638 | [16 empty] | 0.01001
| 40679.3444 | 60.0058 | 0 |  |  | 19590 | -38.0624 | -67.6308 |  | 0 | -82.1422 | 0 | 162.327 | -12.5766 | 87.3763 |  |  |  |  | 40679.3444 | 60.0058 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30381.4824 | -38.0624 | [16 empty] | 0.0058289
| 40679.3445 | 60.0016 | 0 |  |  | 19590 | -10.5618 | -47.6566 |  | 0 | -62.168 | 0 | 161.5338 | -12.5766 | 87.0218 |  |  |  |  | 40679.3445 | 60.0016 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0293 | -10.5618 | [16 empty] | 0.0016174
| 40679.3445 | 60.0016 | 0 |  |  | 19590 | -10.5618 | -34.6735 |  | 0 | -49.1848 | 0 | 160.7918 | -12.5766 | 86.6699 |  |  |  |  | 40679.3445 | 60.0016 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0293 | -10.5618 | [16 empty] | 0.0016174
| 40679.3445 | 59.998 | 0 |  |  | 19590 | 12.7539 | -18.0739 |  | 0 | -32.5853 | 0 | 160.1133 | -12.5766 | 86.3204 |  |  |  |  | 40679.3445 | 59.998 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0703 | 12.7539 | [15 empty] | 81245.2368 | 0.0019531
| 40679.3445 | 59.9935 | 0 |  |  | 19590 | 42.2473 | 3.0385 |  | 0 | -11.4728 | 0 | 159.5133 | -12.5766 | 85.9734 |  |  |  |  | 40679.3445 | 59.9935 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0703 | 42.2473 | [15 empty] | 9243.4701 | 0.0064697
| 40679.3446 | 59.9926 | 0 |  |  | 19590 | 48.6243 | 18.9935 |  | 0 | 4.4822 | 0 | 158.9731 | -12.5766 | 85.6289 |  |  |  |  | 40679.3446 | 59.9926 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0703 | 48.6243 | [15 empty] | 7757.0829 | 0.0074463
| 40679.3446 | 59.9922 | 0 |  |  | 19590 | 50.6171 | 30.0618 |  | 0 | 15.5504 | 0 | 158.4752 | -12.5766 | 85.2867 |  |  |  |  | 40679.3446 | 59.9922 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30394.0703 | 50.6171 | [15 empty] | 7385.9306 | 0.0077515
| 40679.3446 | 59.99 | 0 |  |  | 19590 | 65.3638 | 42.4175 |  | 0 | 27.9061 | 0 | 158.0234 | -12.5766 | 84.9469 |  |  |  |  | 40679.3446 | 59.99 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9102 | 65.3638 | [15 empty] | 5454.6272 | 0.01001
| 40679.3446 | 59.9884 | 0 |  |  | 19590 | 75.9256 | 54.1453 |  | 0 | 39.6339 | 0 | 157.6151 | -12.5766 | 84.6094 |  |  |  |  | 40679.3446 | 59.9884 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9102 | 75.9256 | [15 empty] | 4594.2247 | 0.011627
| 40679.3447 | 59.9842 | 0 |  |  | 19590 | 103.4262 | 71.3936 |  | 0 | 56.8822 | 0 | 157.269 | -12.5766 | 84.2743 |  |  |  |  | 40679.3447 | 59.9842 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9102 | 103.4262 | [15 empty] | 3256.6656 | 0.015839
| 40679.3447 | 59.9816 | 0 |  |  | 19590 | 120.1657 | 88.4639 |  | 0 | 73.9525 | 0 | 156.9836 | -12.5766 | 83.9415 |  |  |  |  | 40679.3447 | 59.9816 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30376.9102 | 120.1657 | [15 empty] | 2766.4149 | 0.018402
| 40679.3447 | 59.9809 | 0 |  |  | 19590 | 124.5499 | 101.094 |  | 0 | 86.5826 | 0 | 156.7433 | -12.5766 | 83.6109 |  |  |  |  | 40679.3447 | 59.9809 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.957 | 124.5499 | [15 empty] | 2661.4819 | 0.019073
| 40679.3447 | 59.9803 | 0 |  |  | 19590 | 128.7347 | 110.7682 |  | 0 | 96.2569 | 0 | 156.5376 | -12.5766 | 83.2826 |  |  |  |  | 40679.3447 | 59.9803 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.957 | 128.7347 | [15 empty] | 2568.485 | 0.019714
| 40679.3447 | 59.98 | 0 |  |  | 19590 | 130.7275 | 117.754 |  | 0 | 103.2426 | 0 | 156.357 | -12.5766 | 82.9566 |  |  |  |  | 40679.3447 | 59.98 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.457 | 130.7275 | [15 empty] | 2526.4476 | 0.02002
| 40679.3448 | 59.9784 | 0 |  |  | 19590 | 141.2894 | 125.9914 |  | 0 | 111.48 | 0 | 156.2053 | -12.5766 | 82.6328 |  |  |  |  | 40679.3448 | 59.9784 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.457 | 141.2894 | [15 empty] | 2324.7884 | 0.021637
| 40679.3448 | 59.9751 | 0 |  |  | 19590 | 162.413 | 138.739 |  | 0 | 124.2276 | 0 | 156.0977 | -12.5766 | 82.3111 |  |  |  |  | 40679.3448 | 59.9751 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.457 | 162.413 | [15 empty] | 2004.7526 | 0.024872
| 40679.3448 | 59.9729 | 0 |  |  | 19590 | 177.1597 | 152.1862 |  | 0 | 137.6748 | 0 | 156.0359 | -12.5766 | 81.9916 |  |  |  |  | 40679.3448 | 59.9729 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.457 | 177.1597 | [15 empty] | 1828.9805 | 0.02713
| 40679.3448 | 59.9719 | 0 |  |  | 19590 | 183.5367 | 163.1589 |  | 0 | 148.6475 | 0 | 156.0111 | -12.5766 | 81.6743 |  |  |  |  | 40679.3448 | 59.9719 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.1777 | 183.5367 | [15 empty] | 1762.1684 | 0.028107
| 40679.3449 | 59.9716 | 0 |  |  | 19590 | 185.7288 | 171.0583 |  | 0 | 156.547 | 0 | 156.0129 | -12.5766 | 81.3591 |  |  |  |  | 40679.3449 | 59.9716 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.1777 | 185.7288 | [15 empty] | 1740.3151 | 0.028442
| 40679.3449 | 59.9738 | 0 |  |  | 19590 | 170.9821 | 171.0316 |  | 0 | 156.5203 | 0 | 156.0146 | -12.5766 | 81.0459 |  |  |  |  | 40679.3449 | 59.9738 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.1777 | 170.9821 | [15 empty] | 1898.7202 | 0.026184
| 40679.3449 | 59.9764 | 0 |  |  | 19590 | 154.0433 | 165.0857 |  | 0 | 150.5743 | 0 | 155.9966 | -12.5766 | 80.7349 |  |  |  |  | 40679.3449 | 59.9764 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30361.1777 | 154.0433 | [15 empty] | 2120.4114 | 0.02359
| 40679.3449 | 59.9784 | 0 |  |  | 19590 | 141.2894 | 156.757 |  | 0 | 142.2456 | 0 | 155.9512 | -12.5766 | 80.4259 |  |  |  |  | 40679.3449 | 59.9784 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.5918 | 141.2894 | [15 empty] | 2324.7884 | 0.021637
| 40679.345 | 59.9771 | 0 |  |  | 19590 | 149.8584 | 154.3425 |  | 0 | 139.8311 | 0 | 155.8982 | -12.5766 | 80.119 |  |  |  |  | 40679.345 | 59.9771 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.5918 | 149.8584 | [15 empty] | 2183.3939 | 0.022949
| 40679.345 | 59.9745 | 0 |  |  | 19590 | 166.5979 | 158.6319 |  | 0 | 144.1205 | 0 | 155.8596 | -12.5766 | 79.8141 |  |  |  |  | 40679.345 | 59.9745 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.1934 | 166.5979 | [15 empty] | 1951.5291 | 0.025513
| 40679.345 | 59.9713 | 0 |  |  | 19590 | 187.7216 | 168.8133 |  | 0 | 154.3019 | 0 | 155.8545 | -12.5766 | 79.5111 |  |  |  |  | 40679.345 | 59.9713 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.1934 | 187.7216 | [15 empty] | 1720.9136 | 0.028748
| 40679.345 | 59.9709 | 0 |  |  | 19590 | 189.9136 | 176.1984 |  | 0 | 161.687 | 0 | 155.8735 | -12.5766 | 79.2102 |  |  |  |  | 40679.345 | 59.9709 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.1934 | 189.9136 | [15 empty] | 1700.0655 | 0.029083
| 40679.345 | 59.9729 | 0 |  |  | 19590 | 177.1597 | 176.5349 |  | 0 | 162.0235 | 0 | 155.8934 | -12.5766 | 78.9112 |  |  |  |  | 40679.345 | 59.9729 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30365.1934 | 177.1597 | [15 empty] | 1828.9805 | 0.02713
| 40679.3451 | 59.9745 | 0 |  |  | 19590 | 166.5979 | 173.0569 |  | 0 | 158.5455 | 0 | 155.902 | -12.5766 | 78.6142 |  |  |  |  | 40679.3451 | 59.9745 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30375.9121 | 166.5979 | [15 empty] | 1951.5291 | 0.025513
| 40679.3451 | 59.9738 | 0 |  |  | 19590 | 170.9821 | 172.3307 |  | 0 | 157.8193 | 0 | 155.9082 | -12.5766 | 78.3191 |  |  |  |  | 40679.3451 | 59.9738 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30375.9121 | 170.9821 | [15 empty] | 1898.7202 | 0.026184
| 40679.3451 | 59.9732 | 0 |  |  | 19590 | 175.1669 | 173.3234 |  | 0 | 158.812 | 0 | 155.9176 | -12.5766 | 78.0259 |  |  |  |  | 40679.3451 | 59.9732 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30375.9121 | 175.1669 | [15 empty] | 1850.9107 | 0.026825
| 40679.3451 | 59.9745 | 0 |  |  | 19590 | 166.5979 | 170.9695 |  | 0 | 156.4581 | 0 | 155.9193 | -12.5766 | 77.7345 |  |  |  |  | 40679.3451 | 59.9745 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30375.9121 | 166.5979 | [15 empty] | 1951.5291 | 0.025513
| 40679.3452 | 59.9761 | 0 |  |  | 19590 | 156.0361 | 165.7428 |  | 0 | 151.2314 | 0 | 155.9043 | -12.5766 | 77.4451 |  |  |  |  | 40679.3452 | 59.9761 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.4023 | 156.0361 | [15 empty] | 2091.6795 | 0.023895
| 40679.3452 | 59.9774 | 0 |  |  | 19590 | 147.6663 | 159.416 |  | 0 | 144.9046 | 0 | 155.8693 | -12.5766 | 77.1575 |  |  |  |  | 40679.3452 | 59.9774 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.4023 | 147.6663 | [15 empty] | 2217.9016 | 0.022614
| 40679.3452 | 59.9784 | 0 |  |  | 19590 | 141.2894 | 153.0717 |  | 0 | 138.5603 | 0 | 155.8143 | -12.5766 | 76.8717 |  |  |  |  | 40679.3452 | 59.9784 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.7207 | 141.2894 | [15 empty] | 2324.7884 | 0.021637
| 40679.3452 | 59.9777 | 0 |  |  | 19590 | 145.6735 | 150.4823 |  | 0 | 135.971 | 0 | 155.7515 | -12.5766 | 76.5877 |  |  |  |  | 40679.3452 | 59.9777 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.7207 | 145.6735 | [15 empty] | 2250.2325 | 0.022308
| 40679.3453 | 59.9771 | 0 |  |  | 19590 | 149.8584 | 150.264 |  | 0 | 135.7526 | 0 | 155.6884 | -12.5766 | 76.3056 |  |  |  |  | 40679.3453 | 59.9771 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.7207 | 149.8584 | [15 empty] | 2183.3939 | 0.022949
| 40679.3453 | 59.9764 | 0 |  |  | 19590 | 154.0433 | 151.5867 |  | 0 | 137.0753 | 0 | 155.6299 | -12.5766 | 76.0252 |  |  |  |  | 40679.3453 | 59.9764 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30367.7207 | 154.0433 | [15 empty] | 2120.4114 | 0.02359
| 40679.3453 | 59.9754 | 0 |  |  | 19590 | 160.4202 | 154.6784 |  | 0 | 140.1671 | 0 | 155.5814 | -12.5766 | 75.7465 |  |  |  |  | 40679.3453 | 59.9754 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30416.8711 | 160.4202 | [15 empty] | 2031.1309 | 0.024567
| 40679.3453 | 59.9738 | 0 |  |  | 19590 | 170.9821 | 160.3847 |  | 0 | 145.8733 | 0 | 155.5511 | -12.5766 | 75.4697 |  |  |  |  | 40679.3453 | 59.9738 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30416.8711 | 170.9821 | [15 empty] | 1898.7202 | 0.026184
| 40679.3453 | 59.9732 | 0 |  |  | 19590 | 175.1669 | 165.5585 |  | 0 | 151.0471 | 0 | 155.5371 | -12.5766 | 75.1945 |  |  |  |  | 40679.3453 | 59.9732 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30416.8711 | 175.1669 | [15 empty] | 1850.9107 | 0.026825
| 40679.3454 | 59.9722 | 0 |  |  | 19590 | 181.3446 | 171.0836 |  | 0 | 156.5722 | 0 | 155.5403 | -12.5766 | 74.9211 |  |  |  |  | 40679.3454 | 59.9722 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30416.8711 | 181.3446 | [15 empty] | 1784.5775 | 0.027771
| 40679.3454 | 59.9719 | 0 |  |  | 19590 | 183.5367 | 175.4422 |  | 0 | 160.9308 | 0 | 155.557 | -12.5766 | 74.6494 |  |  |  |  | 40679.3454 | 59.9719 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30413.6465 | 183.5367 | [15 empty] | 1762.1684 | 0.028107
| 40679.3454 | 59.9709 | 0 |  |  | 19590 | 189.9136 | 180.5072 |  | 0 | 165.9958 | 0 | 155.5892 | -12.5766 | 74.3793 |  |  |  |  | 40679.3454 | 59.9709 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30413.6465 | 189.9136 | [15 empty] | 1700.0655 | 0.029083
| 40679.3454 | 59.9699 | 0 |  |  | 19590 | 196.2906 | 186.0314 |  | 0 | 171.52 | 0 | 155.6382 | -12.5766 | 74.1109 |  |  |  |  | 40679.3454 | 59.9699 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30406.3008 | 196.2906 | [15 empty] | 1642.191 | 0.03006
| 40679.3455 | 59.9683 | 0 |  |  | 19590 | 206.8524 | 193.3187 |  | 0 | 178.8074 | 0 | 155.7093 | -12.5766 | 73.8442 |  |  |  |  | 40679.3455 | 59.9683 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30406.3008 | 206.8524 | [15 empty] | 1554.5413 | 0.031677
| 40679.3455 | 59.9661 | 0 |  |  | 19590 | 221.5991 | 203.2169 |  | 0 | 188.7055 | 0 | 155.8102 | -12.5766 | 73.5791 |  |  |  |  | 40679.3455 | 59.9661 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30406.3008 | 221.5991 | [15 empty] | 1446.7287 | 0.033936
| 40679.3455 | 59.9654 | 0 |  |  | 19590 | 225.784 | 211.1154 |  | 0 | 196.604 | 0 | 155.9346 | -12.5766 | 73.3156 |  |  |  |  | 40679.3455 | 59.9654 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30406.3008 | 225.784 | [15 empty] | 1418.8047 | 0.034576
| 40679.3455 | 59.9661 | 0 |  |  | 19590 | 221.5991 | 214.7847 |  | 0 | 200.2733 | 0 | 156.0693 | -12.5766 | 73.0538 |  |  |  |  | 40679.3455 | 59.9661 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30418.5879 | 221.5991 | [15 empty] | 1446.7287 | 0.033936
| 40679.3456 | 59.9693 | 0 |  |  | 19590 | 200.4755 | 209.7765 |  | 0 | 195.2651 | 0 | 156.1881 | -12.5766 | 72.7935 |  |  |  |  | 40679.3456 | 59.9693 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30418.5879 | 200.4755 | [15 empty] | 1606.3054 | 0.030701
| 40679.3456 | 59.9725 | 0 |  |  | 19590 | 179.3518 | 199.1278 |  | 0 | 184.6164 | 0 | 156.274 | -12.5766 | 72.5348 |  |  |  |  | 40679.3456 | 59.9725 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30418.5879 | 179.3518 | [15 empty] | 1805.4497 | 0.027466
| 40679.3456 | 59.9735 | 0 |  |  | 19590 | 172.9749 | 189.9743 |  | 0 | 175.4629 | 0 | 156.3318 | -12.5766 | 72.2777 |  |  |  |  | 40679.3456 | 59.9735 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30418.5879 | 172.9749 | [15 empty] | 1875.6495 | 0.026489
| 40679.3456 | 59.9738 | 0 |  |  | 19590 | 170.9821 | 183.327 |  | 0 | 168.8156 | 0 | 156.3693 | -12.5766 | 72.0221 |  |  |  |  | 40679.3456 | 59.9738 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 170.9821 | [15 empty] | 1898.7202 | 0.026184
| 40679.3456 | 59.9725 | 0 |  |  | 19590 | 179.3518 | 181.9357 |  | 0 | 167.4243 | 0 | 156.4024 | -12.5766 | 71.768 |  |  |  |  | 40679.3456 | 59.9725 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 179.3518 | [15 empty] | 1805.4497 | 0.027466
| 40679.3457 | 59.9725 | 0 |  |  | 19590 | 179.3518 | 181.0313 |  | 0 | 166.5199 | 0 | 156.4326 | -12.5766 | 71.5155 |  |  |  |  | 40679.3457 | 59.9725 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 179.3518 | [15 empty] | 1805.4497 | 0.027466
| 40679.3457 | 59.9725 | 0 |  |  | 19590 | 179.3518 | 180.4435 |  | 0 | 165.9321 | 0 | 156.4608 | -12.5766 | 71.2645 |  |  |  |  | 40679.3457 | 59.9725 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 179.3518 | [15 empty] | 1805.4497 | 0.027466
| 40679.3457 | 59.9677 | 0 |  |  | 19590 | 211.0373 | 191.1513 |  | 0 | 176.6399 | 0 | 156.5207 | -12.5766 | 71.0149 |  |  |  |  | 40679.3457 | 59.9677 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 211.0373 | [15 empty] | 1522.3466 | 0.032318
| 40679.3457 | 59.9713 | 0 |  |  | 19590 | 187.7216 | 189.9509 |  | 0 | 175.4395 | 0 | 156.5767 | -12.5766 | 70.7669 |  |  |  |  | 40679.3457 | 59.9713 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30433.3145 | 187.7216 | [15 empty] | 1720.9136 | 0.028748
| 40679.3458 | 59.9758 | 0 |  |  | 19590 | 158.2281 | 178.8479 |  | 0 | 164.3366 | 0 | 156.5996 | -12.5766 | 70.5203 |  |  |  |  | 40679.3458 | 59.9758 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30451.2969 | 158.2281 | [15 empty] | 2060.9606 | 0.024231
| 40679.3458 | 59.9758 | 0 |  |  | 19590 | 158.2281 | 171.631 |  | 0 | 157.1196 | 0 | 156.6011 | -12.5766 | 70.2752 |  |  |  |  | 40679.3458 | 59.9758 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30451.2969 | 158.2281 | [15 empty] | 2060.9606 | 0.024231
| 40679.3458 | 59.9758 | 0 |  |  | 19590 | 158.2281 | 166.94 |  | 0 | 152.4286 | 0 | 156.5889 | -12.5766 | 70.0315 |  |  |  |  | 40679.3458 | 59.9758 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30451.2969 | 158.2281 | [15 empty] | 2060.9606 | 0.024231
| 40679.3458 | 59.9842 | 0 |  |  | 19590 | 103.4262 | 144.7102 |  | 0 | 130.1988 | 0 | 156.5117 | -12.5766 | 69.7893 |  |  |  |  | 40679.3458 | 59.9842 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30451.2969 | 103.4262 | [15 empty] | 3256.6656 | 0.015839
| 40679.3459 | 59.9819 | 0 |  |  | 19590 | 118.1729 | 135.4221 |  | 0 | 120.9108 | 0 | 156.4079 | -12.5766 | 69.5484 |  |  |  |  | 40679.3459 | 59.9819 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30425.7402 | 118.1729 | [15 empty] | 2816.8969 | 0.018097
| 40679.3459 | 59.979 | 0 |  |  | 19590 | 137.1045 | 136.011 |  | 0 | 121.4996 | 0 | 156.3064 | -12.5766 | 69.309 |  |  |  |  | 40679.3459 | 59.979 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30425.7402 | 137.1045 | [15 empty] | 2400.7146 | 0.020996
| 40679.3459 | 59.9777 | 0 |  |  | 19590 | 145.6735 | 139.3929 |  | 0 | 124.8815 | 0 | 156.2154 | -12.5766 | 69.071 |  |  |  |  | 40679.3459 | 59.9777 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30419.1836 | 145.6735 | [15 empty] | 2250.2325 | 0.022308
| 40679.3459 | 59.9777 | 0 |  |  | 19590 | 145.6735 | 141.5911 |  | 0 | 127.0797 | 0 | 156.1312 | -12.5766 | 68.8343 |  |  |  |  | 40679.3459 | 59.9777 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30419.1836 | 145.6735 | [15 empty] | 2250.2325 | 0.022308
| 40679.3459 | 59.9813 | 0 |  |  | 19590 | 122.3578 | 134.8594 |  | 0 | 120.3481 | 0 | 156.028 | -12.5766 | 68.599 |  |  |  |  | 40679.3459 | 59.9813 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30419.1836 | 122.3578 | [15 empty] | 2712.9341 | 0.018738
| 40679.346 | 59.9848 | 0 |  |  | 19590 | 99.2413 | 122.3931 |  | 0 | 107.8817 | 0 | 155.8897 | -12.5766 | 68.3651 |  |  |  |  | 40679.346 | 59.9848 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30419.1836 | 99.2413 | [15 empty] | 3407.6369 | 0.015198
| 40679.346 | 59.9887 | 0 |  |  | 19590 | 73.9328 | 105.432 |  | 0 | 90.9206 | 0 | 155.7035 | -12.5766 | 68.1325 |  |  |  |  | 40679.346 | 59.9887 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30424.293 | 73.9328 | [15 empty] | 4735.1518 | 0.011322
| 40679.346 | 59.9916 | 0 |  |  | 19590 | 54.8019 | 87.7115 |  | 0 | 73.2001 | 0 | 155.4678 | -12.5766 | 67.9012 |  |  |  |  | 40679.346 | 59.9916 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30424.293 | 54.8019 | [15 empty] | 6711.563 | 0.0083923
| 40679.346 | 59.9935 | 0 |  |  | 19590 | 42.2473 | 71.799 |  | 0 | 57.2876 | 0 | 155.1881 | -12.5766 | 67.6713 |  |  |  |  | 40679.346 | 59.9935 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30424.293 | 42.2473 | [15 empty] | 9243.4701 | 0.0064697
| 40679.3461 | 59.9958 | 0 |  |  | 19590 | 27.5006 | 56.2946 |  | 0 | 41.7832 | 0 | 154.8659 | -12.5766 | 67.4427 |  |  |  |  | 40679.3461 | 59.9958 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30424.293 | 27.5006 | [15 empty] | 16598.4892 | 0.0042114
| 40679.3461 | 59.9968 | 0 |  |  | 19590 | 21.1237 | 43.9848 |  | 0 | 29.4734 | 0 | 154.5107 | -12.5766 | 67.2153 |  |  |  |  | 40679.3461 | 59.9968 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30440.8223 | 21.1237 | [15 empty] | 25305.8934 | 0.0032349
| 40679.3461 | 59.9977 | 0 |  |  | 19590 | 14.7467 | 33.7514 |  | 0 | 19.2401 | 0 | 154.1286 | -12.5766 | 66.9893 |  |  |  |  | 40679.3461 | 59.9977 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30440.8223 | 14.7467 | [15 empty] | 53229.6379 | 0.0022583
| 40679.3461 | 59.9984 | 0 |  |  | 19590 | 10.5618 | 25.6351 |  | 0 | 11.1237 | 0 | 153.7257 | -12.5766 | 66.7645 |  |  |  |  | 40679.3461 | 59.9984 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30431.5801 | 10.5618 | [15 empty] | 192957.4375 | 0.0016174
| 40679.3462 | 59.9977 | 0 |  |  | 19590 | 14.7467 | 21.8241 |  | 0 | 7.3128 | 0 | 153.3145 | -12.5766 | 66.541 |  |  |  |  | 40679.3462 | 59.9977 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30431.5801 | 14.7467 | [15 empty] | 53229.6379 | 0.0022583
| 40679.3462 | 59.9971 | 0 |  |  | 19590 | 18.9316 | 20.8117 |  | 0 | 6.3004 | 0 | 152.9027 | -12.5766 | 66.3188 |  |  |  |  | 40679.3462 | 59.9971 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30431.5801 | 18.9316 | [15 empty] | 30873.19 | 0.0028992
| 40679.3462 | 59.9974 | 0 |  |  | 19590 | 16.9388 | 19.4562 |  | 0 | 4.9448 | 0 | 152.4894 | -12.5766 | 66.0978 |  |  |  |  | 40679.3462 | 59.9974 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30431.5801 | 16.9388 | [15 empty] | 38591.4875 | 0.002594
| 40679.3462 | 59.9974 | 0 |  |  | 19590 | 16.9388 | 18.5751 |  | 0 | 4.0637 | 0 | 152.0759 | -12.5766 | 65.878 |  |  |  |  | 40679.3462 | 59.9974 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30444.248 | 16.9388 | [15 empty] | 38591.4875 | 0.002594
| 40679.3463 | 59.9974 | 0 |  |  | 19590 | 16.9388 | 18.0024 |  | 0 | 3.491 | 0 | 151.6632 | -12.5766 | 65.6595 |  |  |  |  | 40679.3463 | 59.9974 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30444.248 | 16.9388 | [15 empty] | 38591.4875 | 0.002594
| 40679.3463 | 60.0006 | 0 |  |  | 19590 | -4.1849 | 10.2369 |  | 0 | -4.2745 | 0 | 151.2312 | -12.5766 | 65.4422 |  |  |  |  | 40679.3463 | 60.0006 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30444.248 | -4.1849 | [16 empty] | 0.00064087
| 40679.3463 | 60.0032 | 0 |  |  | 19590 | -21.1237 | -0.73933 |  | 0 | -15.2507 | 0 | 150.7713 | -12.5766 | 65.2261 |  |  |  |  | 40679.3463 | 60.0032 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30444.248 | -21.1237 | [16 empty] | 0.0032349
| 40679.3463 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -8.5713 |  | 0 | -23.0827 | 0 | 150.2924 | -12.5766 | 65.0111 |  |  |  |  | 40679.3463 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.1133 | -23.1165 | [16 empty] | 0.00354
| 40679.3463 | 60.0026 | 0 |  |  | 19590 | -16.9388 | -11.4999 |  | 0 | -26.0113 | 0 | 149.8081 | -12.5766 | 64.7974 |  |  |  |  | 40679.3463 | 60.0026 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.1133 | -16.9388 | [16 empty] | 0.002594
| 40679.3464 | 60.001 | 0 |  |  | 19590 | -6.377 | -9.7069 |  | 0 | -24.2183 | 0 | 149.3313 | -12.5766 | 64.5848 |  |  |  |  | 40679.3464 | 60.001 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.3027 | -6.377 | [16 empty] | 0.00097656
| 40679.3464 | 59.9994 | 0 |  |  | 19590 | 4.1849 | -4.8448 |  | 0 | -19.3562 | 0 | 148.8704 | -12.5766 | 64.3734 |  |  |  |  | 40679.3464 | 59.9994 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.3027 | 4.1849 | [16 empty] | 0.00064087
| 40679.3464 | 59.9974 | 0 |  |  | 19590 | 16.9388 | 2.7795 |  | 0 | -11.7319 | 0 | 148.4328 | -12.5766 | 64.1632 |  |  |  |  | 40679.3464 | 59.9974 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.3027 | 16.9388 | [15 empty] | 38591.4875 | 0.002594
| 40679.3464 | 59.9968 | 0 |  |  | 19590 | 21.1237 | 9.1999 |  | 0 | -5.3114 | 0 | 148.015 | -12.5766 | 63.9541 |  |  |  |  | 40679.3464 | 59.9968 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30465.3027 | 21.1237 | [15 empty] | 25305.8934 | 0.0032349
| 40679.3465 | 59.9968 | 0 |  |  | 19590 | 21.1237 | 13.3732 |  | 0 | -1.1381 | 0 | 147.6108 | -12.5766 | 63.7461 |  |  |  |  | 40679.3465 | 59.9968 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30478.248 | 21.1237 | [15 empty] | 25305.8934 | 0.0032349
| 40679.3465 | 59.9971 | 0 |  |  | 19590 | 18.9316 | 15.3187 |  | 0 | 0.80728 | 0 | 147.214 | -12.5766 | 63.5393 |  |  |  |  | 40679.3465 | 59.9971 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30478.248 | 18.9316 | [15 empty] | 30873.19 | 0.0028992
| 40679.3465 | 59.9977 | 0 |  |  | 19590 | 14.7467 | 15.1185 |  | 0 | 0.60709 | 0 | 146.8188 | -12.5766 | 63.3336 |  |  |  |  | 40679.3465 | 59.9977 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30478.248 | 14.7467 | [15 empty] | 53229.6379 | 0.0022583
| 40679.3465 | 59.9987 | 0 |  |  | 19590 | 8.3698 | 12.7564 |  | 0 | -1.755 | 0 | 146.4194 | -12.5766 | 63.129 |  |  |  |  | 40679.3465 | 59.9987 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30478.248 | 8.3698 | [16 empty] | 0.0012817
| 40679.3466 | 59.9997 | 0 |  |  | 19590 | 2.1921 | 9.0589 |  | 0 | -5.4525 | 0 | 146.0123 | -12.5766 | 62.9254 |  |  |  |  | 40679.3466 | 59.9997 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.8574 | 2.1921 | [16 empty] | 0.00033569
| 40679.3466 | 60 | 0 |  |  | 19590 | 0 | 5.8883 |  | 0 | -8.6231 | 0 | 145.5988 | -12.5766 | 62.723 |  |  |  |  | 40679.3466 | 60 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.8574 | 0 | [16 empty] | 0
| 40679.3466 | 60.0003 | 0 |  |  | 19590 | -2.1921 | 3.0602 |  | 0 | -11.4512 | 0 | 145.18 | -12.5766 | 62.5217 |  |  |  |  | 40679.3466 | 60.0003 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30468.8379 | -2.1921 | [16 empty] | 0.00033569
| 40679.3466 | 60.001 | 0 |  |  | 19590 | -6.377 | -0.24283 |  | 0 | -14.7542 | 0 | 144.7547 | -12.5766 | 62.3214 |  |  |  |  | 40679.3466 | 60.001 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30468.8379 | -6.377 | [16 empty] | 0.00097656
| 40679.3466 | 60.0023 | 0 |  |  | 19590 | -14.7467 | -5.3192 |  | 0 | -19.8306 | 0 | 144.3181 | -12.5766 | 62.1222 |  |  |  |  | 40679.3466 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30468.8379 | -14.7467 | [16 empty] | 0.0022583
| 40679.3467 | 60.0029 | 0 |  |  | 19590 | -18.9316 | -10.0835 |  | 0 | -24.5949 | 0 | 143.8712 | -12.5766 | 61.9241 |  |  |  |  | 40679.3467 | 60.0029 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30468.8379 | -18.9316 | [16 empty] | 0.0028992
| 40679.3467 | 60.0026 | 0 |  |  | 19590 | -16.9388 | -12.4829 |  | 0 | -26.9942 | 0 | 143.4204 | -12.5766 | 61.727 |  |  |  |  | 40679.3467 | 60.0026 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.627 | -16.9388 | [16 empty] | 0.002594
| 40679.3467 | 60.0023 | 0 |  |  | 19590 | -14.7467 | -13.2752 |  | 0 | -27.7866 | 0 | 142.9699 | -12.5766 | 61.5309 |  |  |  |  | 40679.3467 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.627 | -14.7467 | [16 empty] | 0.0022583
| 40679.3467 | 60.0023 | 0 |  |  | 19590 | -14.7467 | -13.7902 |  | 0 | -28.3016 | 0 | 142.5203 | -12.5766 | 61.3359 |  |  |  |  | 40679.3467 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.627 | -14.7467 | [16 empty] | 0.0022583
| 40679.3468 | 60.0032 | 0 |  |  | 19590 | -21.1237 | -16.3569 |  | 0 | -30.8683 | 0 | 142.0664 | -12.5766 | 61.1419 |  |  |  |  | 40679.3468 | 60.0032 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.627 | -21.1237 | [16 empty] | 0.0032349
| 40679.3468 | 60.0042 | 0 |  |  | 19590 | -27.5006 | -20.2572 |  | 0 | -34.7686 | 0 | 141.6047 | -12.5766 | 60.9489 |  |  |  |  | 40679.3468 | 60.0042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30488.4141 | -27.5006 | [16 empty] | 0.0042114
| 40679.3468 | 60.0049 | 0 |  |  | 19590 | -31.6855 | -24.2571 |  | 0 | -38.7685 | 0 | 141.135 | -12.5766 | 60.757 |  |  |  |  | 40679.3468 | 60.0049 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30488.4141 | -31.6855 | [16 empty] | 0.0048523
| 40679.3468 | 60.0045 | 0 |  |  | 19590 | -29.4934 | -26.0898 |  | 0 | -40.6012 | 0 | 140.663 | -12.5766 | 60.566 |  |  |  |  | 40679.3468 | 60.0045 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2891 | -29.4934 | [16 empty] | 0.0045166
| 40679.3469 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -25.0491 |  | 0 | -39.5605 | 0 | 140.1961 | -12.5766 | 60.376 |  |  |  |  | 40679.3469 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2891 | -23.1165 | [16 empty] | 0.00354
| 40679.3469 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -24.3727 |  | 0 | -38.8841 | 0 | 139.7333 | -12.5766 | 60.187 |  |  |  |  | 40679.3469 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2891 | -23.1165 | [16 empty] | 0.00354
| 40679.3469 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -23.933 |  | 0 | -38.4444 | 0 | 139.2741 | -12.5766 | 59.999 |  |  |  |  | 40679.3469 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2891 | -23.1165 | [16 empty] | 0.00354
| 40679.3469 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -23.6472 |  | 0 | -38.1586 | 0 | 138.818 | -12.5766 | 59.812 |  |  |  |  | 40679.3469 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30477.1328 | -23.1165 | [16 empty] | 0.00354
| 40679.3469 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -23.4615 |  | 0 | -37.9728 | 0 | 138.3647 | -12.5766 | 59.6259 |  |  |  |  | 40679.3469 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30477.1328 | -23.1165 | [16 empty] | 0.00354
| 40679.347 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -23.3407 |  | 0 | -37.8521 | 0 | 137.914 | -12.5766 | 59.4407 |  |  |  |  | 40679.347 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30477.1328 | -23.1165 | [16 empty] | 0.00354
| 40679.347 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -23.2622 |  | 0 | -37.7736 | 0 | 137.4658 | -12.5766 | 59.2565 |  |  |  |  | 40679.347 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30477.1328 | -23.1165 | [16 empty] | 0.00354
| 40679.347 | 60.0061 | 0 |  |  | 19590 | -40.0552 | -29.1398 |  | 0 | -43.6512 | 0 | 137.0049 | -12.5766 | 59.0733 |  |  |  |  | 40679.347 | 60.0061 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30487.8203 | -40.0552 | [16 empty] | 0.006134
| 40679.347 | 60.0049 | 0 |  |  | 19590 | -31.6855 | -30.0308 |  | 0 | -44.5422 | 0 | 136.5442 | -12.5766 | 58.891 |  |  |  |  | 40679.347 | 60.0049 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30487.8203 | -31.6855 | [16 empty] | 0.0048523
| 40679.3471 | 60.0045 | 0 |  |  | 19590 | -29.4934 | -29.8427 |  | 0 | -44.3541 | 0 | 136.0862 | -12.5766 | 58.7096 |  |  |  |  | 40679.3471 | 60.0045 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30489.7266 | -29.4934 | [16 empty] | 0.0045166
| 40679.3471 | 60.0045 | 0 |  |  | 19590 | -29.4934 | -29.7204 |  | 0 | -44.2318 | 0 | 135.6308 | -12.5766 | 58.5291 |  |  |  |  | 40679.3471 | 60.0045 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30489.7266 | -29.4934 | [16 empty] | 0.0045166
| 40679.3471 | 60.0035 | 0 |  |  | 19590 | -23.1165 | -27.409 |  | 0 | -41.9204 | 0 | 135.1836 | -12.5766 | 58.3496 |  |  |  |  | 40679.3471 | 60.0035 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30489.7266 | -23.1165 | [16 empty] | 0.00354
| 40679.3471 | 60.0029 | 0 |  |  | 19590 | -18.9316 | -24.4419 |  | 0 | -38.9533 | 0 | 134.7461 | -12.5766 | 58.1709 |  |  |  |  | 40679.3471 | 60.0029 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30489.7266 | -18.9316 | [16 empty] | 0.0028992
| 40679.3472 | 60.0016 | 0 |  |  | 19590 | -10.5618 | -19.5839 |  | 0 | -34.0953 | 0 | 134.3229 | -12.5766 | 57.9931 |  |  |  |  | 40679.3472 | 60.0016 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.0918 | -10.5618 | [16 empty] | 0.0016174
| 40679.3472 | 60.0016 | 0 |  |  | 19590 | -10.5618 | -16.4262 |  | 0 | -30.9376 | 0 | 133.9098 | -12.5766 | 57.8163 |  |  |  |  | 40679.3472 | 60.0016 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.0918 | -10.5618 | [16 empty] | 0.0016174
| 40679.3472 | 60.0042 | 0 |  |  | 19590 | -27.5006 | -20.3022 |  | 0 | -34.8136 | 0 | 133.489 | -12.5766 | 57.6403 |  |  |  |  | 40679.3472 | 60.0042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.0918 | -27.5006 | [16 empty] | 0.0042114
| 40679.3472 | 60.0042 | 0 |  |  | 19590 | -27.5006 | -22.8217 |  | 0 | -37.333 | 0 | 133.0641 | -12.5766 | 57.4652 |  |  |  |  | 40679.3472 | 60.0042 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.0918 | -27.5006 | [16 empty] | 0.0042114
| 40679.3472 | 60.0029 | 0 |  |  | 19590 | -18.9316 | -21.4601 |  | 0 | -35.9715 | 0 | 132.6446 | -12.5766 | 57.291 |  |  |  |  | 40679.3472 | 60.0029 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.9141 | -18.9316 | [16 empty] | 0.0028992
| 40679.3473 | 60.0003 | 0 |  |  | 19590 | -2.1921 | -14.7163 |  | 0 | -29.2277 | 0 | 132.244 | -12.5766 | 57.1176 |  |  |  |  | 40679.3473 | 60.0003 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.9141 | -2.1921 | [16 empty] | 0.00033569
| 40679.3473 | 59.998 | 0 |  |  | 19590 | 12.7539 | -5.1017 |  | 0 | -19.6131 | 0 | 131.869 | -12.5766 | 56.9451 |  |  |  |  | 40679.3473 | 59.998 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.8359 | 12.7539 | [15 empty] | 81245.2368 | 0.0019531
| 40679.3473 | 59.9965 | 0 |  |  | 19590 | 23.1165 | 4.7746 |  | 0 | -9.7368 | 0 | 131.5202 | -12.5766 | 56.7734 |  |  |  |  | 40679.3473 | 59.9965 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.8359 | 23.1165 | [15 empty] | 21741.6831 | 0.00354
| 40679.3473 | 59.9951 | 0 |  |  | 19590 | 31.6855 | 14.1934 |  | 0 | -0.31795 | 0 | 131.1963 | -12.5766 | 56.6026 |  |  |  |  | 40679.3473 | 59.9951 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.8359 | 31.6855 | [15 empty] | 13540.8728 | 0.0048523
| 40679.3474 | 59.9939 | 0 |  |  | 19590 | 40.0552 | 23.2451 |  | 0 | 8.7337 | 0 | 130.8961 | -12.5766 | 56.4326 |  |  |  |  | 40679.3474 | 59.9939 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.8359 | 40.0552 | [15 empty] | 9895.2532 | 0.006134
| 40679.3474 | 59.9929 | 0 |  |  | 19590 | 46.4322 | 31.3606 |  | 0 | 16.8492 | 0 | 130.6173 | -12.5766 | 56.2635 |  |  |  |  | 40679.3474 | 59.9929 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30476.0918 | 46.4322 | [15 empty] | 8210.9548 | 0.0071106
| 40679.3474 | 59.9926 | 0 |  |  | 19590 | 48.6243 | 37.4029 |  | 0 | 22.8915 | 0 | 130.3546 | -12.5766 | 56.0952 |  |  |  |  | 40679.3474 | 59.9926 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30476.0918 | 48.6243 | [15 empty] | 7757.0829 | 0.0074463
| 40679.3474 | 59.9922 | 0 |  |  | 19590 | 50.6171 | 42.0278 |  | 0 | 27.5164 | 0 | 130.1043 | -12.5766 | 55.9277 |  |  |  |  | 40679.3474 | 59.9922 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30476.0918 | 50.6171 | [15 empty] | 7385.9306 | 0.0077515
| 40679.3475 | 59.9897 | 0 |  |  | 19590 | 67.5558 | 50.9626 |  | 0 | 36.4513 | 0 | 129.877 | -12.5766 | 55.761 |  |  |  |  | 40679.3475 | 59.9897 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30476.0918 | 67.5558 | [15 empty] | 5250.5425 | 0.010345
| 40679.3475 | 59.9851 | 0 |  |  | 19590 | 97.0493 | 67.093 |  | 0 | 52.5816 | 0 | 129.6899 | -12.5766 | 55.5951 |  |  |  |  | 40679.3475 | 59.9851 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30456.7559 | 97.0493 | [15 empty] | 3492.4423 | 0.014862
| 40679.3475 | 59.9825 | 0 |  |  | 19590 | 113.988 | 83.5062 |  | 0 | 68.9948 | 0 | 129.5433 | -12.5766 | 55.4301 |  |  |  |  | 40679.3475 | 59.9825 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30456.7559 | 113.988 | [15 empty] | 2929.1452 | 0.017456
| 40679.3475 | 59.9784 | 0 |  |  | 19590 | 141.2894 | 103.7303 |  | 0 | 89.2189 | 0 | 129.4461 | -12.5766 | 55.2658 |  |  |  |  | 40679.3475 | 59.9784 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30457.1152 | 141.2894 | [15 empty] | 2324.7884 | 0.021637
| 40679.3475 | 59.9764 | 0 |  |  | 19590 | 154.0433 | 121.3399 |  | 0 | 106.8285 | 0 | 129.3917 | -12.5766 | 55.1023 |  |  |  |  | 40679.3475 | 59.9764 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30457.1152 | 154.0433 | [15 empty] | 2120.4114 | 0.02359
| 40679.3476 | 59.9771 | 0 |  |  | 19590 | 149.8584 | 131.3213 |  | 0 | 116.81 | 0 | 129.3616 | -12.5766 | 54.9396 |  |  |  |  | 40679.3476 | 59.9771 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30457.1152 | 149.8584 | [15 empty] | 2183.3939 | 0.022949
| 40679.3476 | 59.9771 | 0 |  |  | 19590 | 149.8584 | 137.8093 |  | 0 | 123.2979 | 0 | 129.3471 | -12.5766 | 54.7777 |  |  |  |  | 40679.3476 | 59.9771 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30457.1152 | 149.8584 | [15 empty] | 2183.3939 | 0.022949
| 40679.3476 | 59.9771 | 0 |  |  | 19590 | 149.8584 | 142.0265 |  | 0 | 127.5151 | 0 | 129.3427 | -12.5766 | 54.6166 |  |  |  |  | 40679.3476 | 59.9771 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30446.9785 | 149.8584 | [15 empty] | 2183.3939 | 0.022949
| 40679.3476 | 59.978 | 0 |  |  | 19590 | 143.4814 | 142.5357 |  | 0 | 128.0243 | 0 | 129.3395 | -12.5766 | 54.4562 |  |  |  |  | 40679.3476 | 59.978 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30446.9785 | 143.4814 | [15 empty] | 2286.903 | 0.021973
| 40679.3477 | 59.9796 | 0 |  |  | 19590 | 132.9196 | 139.1701 |  | 0 | 124.6587 | 0 | 129.3284 | -12.5766 | 54.2966 |  |  |  |  | 40679.3477 | 59.9796 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30446.9785 | 132.9196 | [15 empty] | 2481.7677 | 0.020355
| 40679.3477 | 59.9816 | 0 |  |  | 19590 | 120.1657 | 132.5186 |  | 0 | 118.0072 | 0 | 129.3016 | -12.5766 | 54.1378 |  |  |  |  | 40679.3477 | 59.9816 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30446.9785 | 120.1657 | [15 empty] | 2766.4149 | 0.018402
| 40679.3477 | 59.9813 | 0 |  |  | 19590 | 122.3578 | 128.9623 |  | 0 | 114.4509 | 0 | 129.2665 | -12.5766 | 53.9797 |  |  |  |  | 40679.3477 | 59.9813 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30461.0195 | 122.3578 | [15 empty] | 2712.9341 | 0.018738
| 40679.3477 | 59.9793 | 0 |  |  | 19590 | 135.1117 | 131.1146 |  | 0 | 116.6032 | 0 | 129.2366 | -12.5766 | 53.8224 |  |  |  |  | 40679.3477 | 59.9793 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30461.0195 | 135.1117 | [15 empty] | 2438.6406 | 0.020691
| 40679.3478 | 59.9761 | 0 |  |  | 19590 | 156.0361 | 139.8371 |  | 0 | 125.3257 | 0 | 129.2274 | -12.5766 | 53.6658 |  |  |  |  | 40679.3478 | 59.9761 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30460.9434 | 156.0361 | [15 empty] | 2091.6795 | 0.023895
| 40679.3478 | 59.9754 | 0 |  |  | 19590 | 160.4202 | 147.0412 |  | 0 | 132.5298 | 0 | 129.2352 | -12.5766 | 53.5099 |  |  |  |  | 40679.3478 | 59.9754 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30460.9434 | 160.4202 | [15 empty] | 2031.1309 | 0.024567
| 40679.3478 | 59.9758 | 0 |  |  | 19590 | 158.2281 | 150.9566 |  | 0 | 136.4452 | 0 | 129.2521 | -12.5766 | 53.3548 |  |  |  |  | 40679.3478 | 59.9758 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30460.9434 | 158.2281 | [15 empty] | 2060.9606 | 0.024231
| 40679.3478 | 59.9767 | 0 |  |  | 19590 | 151.8512 | 151.2697 |  | 0 | 136.7583 | 0 | 129.2696 | -12.5766 | 53.2004 |  |  |  |  | 40679.3478 | 59.9767 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30460.9434 | 151.8512 | [15 empty] | 2152.9421 | 0.023254
| 40679.3478 | 59.978 | 0 |  |  | 19590 | 143.4814 | 148.5438 |  | 0 | 134.0324 | 0 | 129.2807 | -12.5766 | 53.0467 |  |  |  |  | 40679.3478 | 59.978 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.2305 | 143.4814 | [15 empty] | 2286.903 | 0.021973
| 40679.3479 | 59.979 | 0 |  |  | 19590 | 137.1045 | 144.5401 |  | 0 | 130.0287 | 0 | 129.2824 | -12.5766 | 52.8937 |  |  |  |  | 40679.3479 | 59.979 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.2305 | 137.1045 | [15 empty] | 2400.7146 | 0.020996
| 40679.3479 | 59.9796 | 0 |  |  | 19590 | 132.9196 | 140.4729 |  | 0 | 125.9615 | 0 | 129.2747 | -12.5766 | 52.7414 |  |  |  |  | 40679.3479 | 59.9796 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.2305 | 132.9196 | [15 empty] | 2481.7677 | 0.020355
| 40679.3479 | 59.9806 | 0 |  |  | 19590 | 126.5427 | 135.5973 |  | 0 | 121.0859 | 0 | 129.2558 | -12.5766 | 52.5899 |  |  |  |  | 40679.3479 | 59.9806 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30469.2305 | 126.5427 | [15 empty] | 2616.372 | 0.019379
| 40679.3479 | 59.9819 | 0 |  |  | 19590 | 118.1729 | 129.4988 |  | 0 | 114.9874 | 0 | 129.2228 | -12.5766 | 52.439 |  |  |  |  | 40679.3479 | 59.9819 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30481.4863 | 118.1729 | [15 empty] | 2816.8969 | 0.018097
| 40679.348 | 59.9822 | 0 |  |  | 19590 | 115.9808 | 124.7675 |  | 0 | 110.2561 | 0 | 129.1791 | -12.5766 | 52.2889 |  |  |  |  | 40679.348 | 59.9822 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30481.4863 | 115.9808 | [15 empty] | 2874.5987 | 0.017761
| 40679.348 | 59.9825 | 0 |  |  | 19590 | 113.988 | 120.9947 |  | 0 | 106.4833 | 0 | 129.1269 | -12.5766 | 52.1394 |  |  |  |  | 40679.348 | 59.9825 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2852 | 113.988 | [15 empty] | 2929.1452 | 0.017456
| 40679.348 | 59.9829 | 0 |  |  | 19590 | 111.796 | 117.7751 |  | 0 | 103.2638 | 0 | 129.0676 | -12.5766 | 51.9907 |  |  |  |  | 40679.348 | 59.9829 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2852 | 111.796 | [15 empty] | 2991.5882 | 0.01712
| 40679.348 | 59.9825 | 0 |  |  | 19590 | 113.988 | 116.4496 |  | 0 | 101.9383 | 0 | 129.0055 | -12.5766 | 51.8426 |  |  |  |  | 40679.348 | 59.9825 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2852 | 113.988 | [15 empty] | 2929.1452 | 0.017456
| 40679.3481 | 59.9825 | 0 |  |  | 19590 | 113.988 | 115.5881 |  | 0 | 101.0767 | 0 | 128.9418 | -12.5766 | 51.6952 |  |  |  |  | 40679.3481 | 59.9825 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30480.2852 | 113.988 | [15 empty] | 2929.1452 | 0.017456
| 40679.3481 | 59.9829 | 0 |  |  | 19590 | 111.796 | 114.2608 |  | 0 | 99.7495 | 0 | 128.8753 | -12.5766 | 51.5484 |  |  |  |  | 40679.3481 | 59.9829 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.1465 | 111.796 | [15 empty] | 2991.5882 | 0.01712
| 40679.3481 | 59.9861 | 0 |  |  | 19590 | 90.6723 | 106.0049 |  | 0 | 91.4935 | 0 | 128.7903 | -12.5766 | 51.4024 |  |  |  |  | 40679.3481 | 59.9861 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.1465 | 90.6723 | [15 empty] | 3765.0232 | 0.013885
| 40679.3481 | 59.9939 | 0 |  |  | 19590 | 40.0552 | 82.9225 |  | 0 | 68.4111 | 0 | 128.6534 | -12.5766 | 51.2569 |  |  |  |  | 40679.3481 | 59.9939 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.1465 | 40.0552 | [15 empty] | 9895.2532 | 0.006134
| 40679.3481 | 60.0023 | 0 |  |  | 19590 | -14.7467 | 48.7383 |  | 0 | 34.2269 | 0 | 128.4398 | -12.5766 | 51.1122 |  |  |  |  | 40679.3481 | 60.0023 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30473.1465 | -14.7467 | [16 empty] | 0.0022583
| 40679.3482 | 60.011 | 0 |  |  | 19590 | -71.7407 | 6.5706 |  | 0 | -7.9408 | 0 | 128.1319 | -12.5766 | 50.9681 |  |  |  |  | 40679.3482 | 60.011 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.6582 | -71.7407 | [16 empty] | 0.010986
| 40679.3482 | 60.0171 | 0 |  |  | 19590 | -111.796 | -34.8577 |  | 0 | -49.3691 | 0 | 127.7321 | -12.5766 | 50.8247 |  |  |  |  | 40679.3482 | 60.0171 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.6582 | -111.796 | [16 empty] | 0.01712
| 40679.3482 | 60.0207 | 0 |  |  | 19590 | -135.1117 | -69.9466 |  | 0 | -84.458 | 0 | 127.2553 | -12.5766 | 50.6819 |  |  |  |  | 40679.3482 | 60.0207 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.5996 | -135.1117 | [16 empty] | 0.020691
| 40679.3482 | 60.0213 | 0 |  |  | 19590 | -139.2966 | -94.2191 |  | 0 | -108.7305 | 0 | 126.7262 | -12.5766 | 50.5397 |  |  |  |  | 40679.3482 | 60.0213 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.5996 | -139.2966 | [16 empty] | 0.021332
| 40679.3483 | 60.0213 | 0 |  |  | 19590 | -139.2966 | -109.9962 |  | 0 | -124.5076 | 0 | 126.1642 | -12.5766 | 50.3982 |  |  |  |  | 40679.3483 | 60.0213 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.5996 | -139.2966 | [16 empty] | 0.021332
| 40679.3483 | 60.0213 | 0 |  |  | 19590 | -139.2966 | -120.2513 |  | 0 | -134.7627 | 0 | 125.5817 | -12.5766 | 50.2573 |  |  |  |  | 40679.3483 | 60.0213 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30470.5996 | -139.2966 | [16 empty] | 0.021332
| 40679.3483 | 60.0233 | 0 |  |  | 19590 | -151.8512 | -131.3113 |  | 0 | -145.8227 | 0 | 124.9773 | -12.5766 | 50.1171 |  |  |  |  | 40679.3483 | 60.0233 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30461.2793 | -151.8512 | [16 empty] | 0.023254
| 40679.3483 | 60.0255 | 0 |  |  | 19590 | -166.5979 | -143.6616 |  | 0 | -158.173 | 0 | 124.348 | -12.5766 | 49.9774 |  |  |  |  | 40679.3483 | 60.0255 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30461.2793 | -166.5979 | [16 empty] | 0.025513
| 40679.3484 | 60.0268 | 0 |  |  | 19590 | -175.1669 | -154.6885 |  | 0 | -169.1998 | 0 | 123.6972 | -12.5766 | 49.8384 |  |  |  |  | 40679.3484 | 60.0268 | 0 | 0 | 0 | 0 |  | 0 | 0 | -653 | 30461.2793 | -175.1669 | [16 empty] | 0.026825
Note on L13: TC allowable range 0.050 to 1.000 with 1.0 turning filter off. Beginning Target slope should align with Actual slope.

## Graph 20 to 52s
"Auto" Event Detection adjustment of T(0).
# of rows to shift T(0)
1
A zero value aligns the data to the hightest Frequency change value.
Usually the event begins one or two data scans earlier than this scan.
Increasing this value shifts graph data to the right.
Decreasing this value shifts graph data to the left.
Note: The P.U. Performance values indicate performance as a P.U. value of BA Bias setting.
For BAs that utilize a variable Bias, the Bias average during T(+20) to T(+52) is used.
P.U. values above 1.0 indicate that the Bias setting was below measured Frequency Response.
P.U. values below 1.0 indicate that the Bias setting was above measured Frequency Response.
T(0)
First change in frequency of the event should occur here on the vertical grid line.
It is important that the pre-event frequency average to NOT contain frequency data of the event, "Average Frequency" trend to the left of center of the graph.
To shift the data on the graph left or right, adjust the value in cell Q3 highlighted in yellow above.
59.999

## Form 1 Summary Data
[6 empty] | Value A Data |  | BA Performance | [8 empty] | Value B | 20 to 52 second Average Period Evaluation | [13 empty] | Frequency Response Initiative - Additional Primary Frequency Response Evaluation Points
[9 empty] | Non- | [10 empty] | Non- | [10 empty] | Average | Unadjusted | Unadjusted | Unadjusted | Unadjusted | Unadjusted | Adjusted | Adjusted | Adjusted | Adjusted | Adjusted
Date | A Value | FPointA | A Value | t(0) Time | C Value |  | Contingent | Load | Conforming |  |  |  |  | BA | BA | Bias |  | Contingent | Load | Conforming |  |  |  |  | Initial | Initial | Sustained | BA | BA | Bias | Bias While | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR | PFR
| Time | Hz | Hz |  | Hz |  | Resource | Resources | Load |  |  |  |  | Bias | Load | Setting |  | Resource | Resources | Load |  |  |  |  | Performance | Performance | Performance | Bias | Load | Setting | Hz > +/-0.036 | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Performance | Maximum | Minimum
[6 empty] | Frequency | Lost | Tripped | Load (-) | Spare | Spare | Spare | Spare | Setting |  | EPFR | Frequency | Lost | Tripped | Load (-) | Spare | Spare | Spare | Spare | Adjusted | Unadjusted |  | Setting |  | EPFR | Hz | @ T(+46) | @ T(+76) | @ T(+106) | @ T(+136) | @ T(+166) | @ T(+46) | @ T(+76) | @ T(+106) | @ T(+136) | @ T(+166) | Bias Setting | Bias Setting
[6 empty] | Hz | MW | MW | MW | MW | MW | MW | MW | MW/0.1 Hz | MW | MW | Hz | MW | MW | MW | MW | MW | MW | MW | P.U. | P.U. | P.U. | MW/0.1 Hz | MW | MW | MW/0.1 Hz | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | P.U. | MW/0.1 Hz | MW/0.1 Hz
2011-05-16 08:07 | 40679.3379 | 60.002 | 59.9986 | 40679.3379 | 59.8701 | 59.9986 | 471.0875 | 0 | 0 | 0 | 0 | 0 | 0 | -653 | 30202.7422 | 8.9676 | 59.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71421 | 0.71421 | 0.73503 | -653 | 30141.1423 | 668.5617 | -653 | 0.73503 | 0.89033 | 1.3633 | 1.543 | 2.4346 | 0.73503 | 0.89033 | 1.3633 | 1.543 | 2.4346 | -653 | -653

## Instructions
Steps | To be completed for each event evaluated.
1 | Set-up Data collection in exact same order as the "Data" sheet of this work book. Data should be in this order:
Column A: Date and Time in this format, mm/dd/yy HH:MM:SS
Column B: Frequency Hz
Column C: Contingent Resouce Lost MW or Lost Load
Column D: Load Resources tripped during the event.
Column E: Non Conforming Load
Column F: Spare
Column G: Not Used
Column H: Spare
Column I: Spare
Column J: BA Bias Setting
Column K: BA Load
2 | Note: Columns D & E are optional data. If you choose not to use these, leave the columns blank. Do not delete the columns. Use the sign (+/-) convention defined in FRS Form 1.
3 | Data compression must be turned off for each data point. Quality data will give you quality results in the evaluation.
4 | Data must start a minimum of two (2) minutes before the event begins and includes a minimum of 15 minutes after the beginning of the event with up to 60 minutes of data.
Be sure the "Data" worksheet is clear of any old data. Collect the same total minutes of data for each event evaluated to minimize your effort and time.
If using PI historian as your data source, use "PasteSpecial/Values" to enter data into the spreadsheet. Do not include historian data collection formulas in the data.
5 | Verify that the "Auto" Event Detection selected the correct event. Verify time and delta Hz by comparing time of event and delta Hz on the graph on the "Copy Results" worksheet.
If the wrong event was selected, in cell "E4" of this worksheet select "Manual" and manually select the beginning and ending row numbers of the desired event and enter these in cells "E5" and "E6". Only rarely should you have to use the "Manual" process.
6 | Once data is in place in the "Data" worksheet, confirm the Auto selection of the beginning of the event by observing the "Graph 20 to 52s" worksheet. Adjust the selection if necessary.
To make an adjustment, change the value in cell "Q3" on the "Graph 20 to 52s" worksheet. Usually a 0, 1 or 2 will achive the correct alignment of T(0).
7 | If the correct row is selected, the "Graph 20 to 52s" worksheet will indicate the first change in frequency (red trend) of the event on the center vertical grid line of the graph.
8 | The end of the event will be Auto selected based on the frequency value in cell "N2" on the Data worksheet. This will be the frequency at the beginning of the event or 60 Hz, whichever is lower. (for low Hz events)
This value controls the end of the "Sustained Frequency Response" evaluation period.
Primary Frequency Response should be sustained during the event recovery period. This evaluation determines how well you achieved this goal.
9 | Use the "Copy Form 2 data for Pasting into Form 1" button provided on the "Copy Results" worksheet (Cells B21 through B28) to copy the evaluation and event specific data for the "FRS Form 1" of this field trial. This data is summarized
in the correct order on worksheet "Form 1 Summary Data".
10 | Use PasteSpecial/Values and paste the copied data into FRS Form 1 on the appropriate event row. Be sure to use the latest version of Form 1, currently Form 1.9.
11 | Save this Form 2 using the file name convention on the "Copy Results" worksheet. The complete file name is in bold in cell B38. Return all completed Form 2s with your Form 1 to NERC.
Steps | To be completed the first time you use Form 2 for your BA.
A | Enter the Balancing Authority name as you want it to appear on the graphs in cell "B1" of the "Copy Results" worksheet. For example: "ERCOT".