## 2022 Summary
2022 Standard Grading Summary
|  | Content Questions |  |  |  |  | Quality Questions
Standard | Req. | RSTC | RE | NERC | Avg | Delta | RSTC | RE | NERC | Avg | Delta
PER-003-2 | R1. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12.6667 | 1
PER-003-2 | R2. | 4 | 4 | 4 | 4 | 0 | 13 | 12 | 12 | 12.3333 | 1
PER-003-2 | R3. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12.6667 | 1
PER-005-2 | R1. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
PER-005-2 | R2. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
PER-005-2 | R3. | 4 | 4 | 4 | 4 | 0 | 13 | 12 | 13 | 12.6667 | 1
PER-005-2 | R4. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
PER-005-2 | R5. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
PER-005-2 | R6. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
PER-006-1 | R1. | 4 | 3 | 4 | 3.6667 | 1 | 13 | 13 | 13 | 13 | 0
TPL-007-4 | R1. | 4 | 4 | 4 | 4 | 1 | 13 | 13 | 13 | 13 | 0
TPL-007-4 | R2. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
TPL-007-4 | R3. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 13 | 13 | 0
TPL-007-4 | R4. | 3 | 4 | 3 | 3.3333 | 1 | 10 | 11 | 11 | 10.6667 | 1
TPL-007-4 | R5. | 4 | 4 | 4 | 4 | 1 | 12 | 13 | 13 | 12.6667 | 1
TPL-007-4 | R6. | 4 | 4 | 3 | 3.6667 | 1 | 11 | 13 | 12 | 12 | 2
TPL-007-4 | R7. | 4 | 4 | 4 | 4 | 1 | 12 | 12 | 12 | 12 | 0
TPL-007-4 | R8. | 4 | 4 | 3 | 3.6667 | 1 | 12 | 12 | 12 | 12 | 0
TPL-007-4 | R9. | 4 | 4 | 4 | 4 | 1 | 12 | 13 | 13 | 12.6667 | 1
TPL-007-4 | R10. | 4 | 4 | 3 | 3.6667 | 1 | 11 | 13 | 12 | 12 | 2
TPL-007-4 | R11. | 4 | 4 | 4 | 4 | 1 | 12 | 12 | 12 | 12 | 0
TPL-007-4 | R12. | 4 | 4 | 4 | 4 | 0 | 12 | 13 | 11 | 12 | 2
TPL-007-4 | R13. | 4 | 4 | 4 | 4 | 0 | 13 | 13 | 12 | 12.6667 | 1

## Summary Comments
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Content Score (0-4) | Quality Score (0-13) | Combined (RSTC/Regions/NERC) Comment/Rationale | Content Delta | Quality Delta
PER-003-2 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | 0 | 1
PER-003-2 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:12 | RSTC: No comment RE: Q6-Definition of System Operator: An individual at a Control Center of a Balancing Authority, Transmission Operator, or Reliability Coordinator, who operates or directs the operation of the Bulk Electric System (BES) in Real-Time. An entity could state they have System Operators who are NOT performing reliability-related tasks. And since PER-005 allows the entity to define what are reliability-related tasks and which are not, the entity can easily get around the PER-003 requirement. PER-003 should state: Each Transmission Operator shall staff its Real-time operating positions that issues Operating Instructions with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates. NERC: Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | 0 | 1
PER-003-2 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | 0 | 1
PER-005-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: 1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. 1.1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. 1.2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. 1.3. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. 1.4. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
PER-005-2 | R2. | R2. Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: 2.1. Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. 2.1.1. Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. 2.2. Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. 2.3. Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. 2.4. Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
PER-005-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. 3.1. Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:12 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 1
PER-005-2 | R4. | R4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. 4.1. A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
PER-005-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. 5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C3-Training on impacts of the personnel's job function(s) to the BES. Believe training should be on the job function. NERC: No comment | 1 | 0
PER-005-2 | R6. | R6. Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. 6.1. Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C3-Training on impacts of the personnel's job function(s) to the BES. Believe training should be on the job function. NERC: No comment | 1 | 0
PER-006-1 | R1. | R1. Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | Delta:1 RSTC:4 RE:3 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: C4: No time frame for training NERC: No comment | 1 | 0
TPL-007-4 | R1. | R1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | Delta:1 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 1 | 0
TPL-007-4 | R2. | R2. Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
TPL-007-4 | R3. | R3. Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:13 RE:13 NERC:13 | RSTC: No comment RE: No comment NERC: No comment | 0 | 0
TPL-007-4 | R4. | R4. Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 4.1. The study or studies shall include the following conditions: 4.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 4.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 4.2. The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. 4.3. The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. 4.3.1. If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Delta:1 RSTC:3 RE:4 NERC:3 | Delta:1 RSTC:10 RE:11 NERC:11 | RSTC: Q1:Might benefit to incorporate R8 into R4 Q13: the way the benchmark model is curently defined and calibrated may have significant cost impact on entities to comply. C1, Q9: Would be benefitial to review and update Attachment 1 and Attachment 1 - CAN (Canadian variance) to simplify benchmark model enough to be directly integrated into R4 and allow more flexibility to entities to specify their own benchmark model. In addition, In Applicable Facilities Section 4.2.1 "Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV." Review the applicable Facilities section to ensure the standard addresses the reliability risk based on updated research. RE: Q7-R4 includes three separate requirements in the second sentence. These don't appear to be addressed in the VSLs. Should these be split or the VSLs modified?? Q2-Part 4.3.1 seems administrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55 NERC: C1, Q9. Since the adoption of the standard, new research performed by EPRI and others have produced new earth conductivity models and scaling factors for some areas. These updated models will improve the accuracy of GMD Vulnerabillity Assessments. Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather modeling, latitude scaling, earth conductivity modeling, analysis of power system wide area harmonics due to GIC). A periodic review is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements. https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf Q1:Supportive of RSTC comment to consider incorporating R8 (supplemental assessment) into R4 | 1 | 1
TPL-007-4 | R5. | R5. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 5.1. The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 5.2. The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Delta:1 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q1: Might benefit to incorporate R9 into R5 RE: No comment NERC: No comment | 1 | 1
TPL-007-4 | R6. | R6. Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: 6.1. Be based on the effective GIC flow information provided in Requirement R5; 6.2. Document assumptions used in the analysis; 6.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 6.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Delta:1 RSTC:4 RE:4 NERC:3 | Delta:2 RSTC:11 RE:13 NERC:12 | RSTC: Q1: Might benefit to incorporate R10 into R6 Q9: Might benefit to reference the rational for specifying 75 A or greater per phase. The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (75A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. RE: No comment NERC: C1, Q9. New transformer models could potentailly impact this requirement as well. The same observation applies: The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (75A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf | 1 | 2
TPL-007-4 | R7. | R7. Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 7.2. Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. 7.3. Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: 7.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 7.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 7.4. Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: 7.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; 7.4.2. Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and 7.4.3. Updated timetable for implementing the selected actions in Part 7.1. 7.5. Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later 7.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Delta:1 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: Q1: Might benefit to incorporate R11 into R7 RE: Q2-Part 7.5.1 seems Administrative in nature. See Paragraph 81 review. See P81 whitepaper related to FAC-011-2 R5. Page 55 NERC: Q10. R7.4 and R11.4 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach including review timing and determination. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf | 1 | 0
TPL-007-4 | R8. | R8. Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 8.1. The study or studies shall include the following conditions: 8.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 8.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 8.2. The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. 8.3. The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. 8.3.1. If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Delta:1 RSTC:4 RE:4 NERC:3 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: Q1:Might benefit to incorporate R8 into R4 RE: Q2- Part 8.3.1 seems administrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55 NERC: C1, Q9. Since the adoption of the standard, new research performed by EPRI and others have produced new earth conductivity models and scaling factors for some areas. These updated models will improve the accuracy of GMD Vulnerabillity Assessments. Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather modeling, latitude scaling, earth conductivity modeling, analysis of power system wide area harmonics due to GIC). A periodic review is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements. https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf | 1 | 0
TPL-007-4 | R9. | R9. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 9.1. The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 9.2. The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Delta:1 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:12 RE:13 NERC:13 | RSTC: Q1: Might benefit to incorporate R9 into R5 RE: No comment NERC: No comment | 1 | 1
TPL-007-4 | R10. | R10. Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: 10.1. Be based on the effective GIC flow information provided in Requirement R9; 10.2. Document assumptions used in the analysis; 10.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 10.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Delta:1 RSTC:4 RE:4 NERC:3 | Delta:2 RSTC:11 RE:13 NERC:12 | RSTC: Q1: Might benefit to incorporate R10 into R6 Q9:Might benefit to reference the rational for specifying 85 A or greater per phase. The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (85A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. RE: No comment NERC: C1, Q9. New transformer models (see comments to R6) could potentailly impact this requirement as well. The same observation applies: The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (85A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf | 1 | 2
TPL-007-4 | R11. | R11. Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance equirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: 11.1.List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 11.2.Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. 11.3. Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: 11.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 11.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 11.4.Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: 11.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; 11.4.2. Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and 11.4.3. Updated timetable for implementing the selected actions in Part 11.1. 11.5.Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. 11.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Delta:1 RSTC:4 RE:4 NERC:4 | Delta:0 RSTC:12 RE:12 NERC:12 | RSTC: Q1: Might benefit to incorporate R11 into R7 RE: Q2- Part 11.5.1 seems adminisrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55 NERC: Q10. R7.4 and R11.4 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach including review timing and determination. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf | 1 | 0
TPL-007-4 | R12. | R12. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System model. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:2 RSTC:12 RE:13 NERC:11 | RSTC: Q6: Depending on earth condition variation in the Planning Coordinator area or System Model, having only one GIC monitor may not be appropriate to guarranty system reliability RE: No comment NERC: Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance. Q6: Depending on earth condition variation in the Planning Coordinator area or System Model, having only one GIC monitor may not be appropriate to guarranty system reliability | 0 | 2
TPL-007-4 | R13. | R13. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Delta:0 RSTC:4 RE:4 NERC:4 | Delta:1 RSTC:13 RE:13 NERC:12 | RSTC: No comment RE: No comment NERC: Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance. | 0 | 1

## RSTC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
PER-003-2 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-003-2 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-003-2 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: 1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. 1.1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. 1.2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. 1.3. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. 1.4. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R2. | R2. Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: 2.1. Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. 2.1.1. Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. 2.2. Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. 2.3. Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. 2.4. Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. 3.1. Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R4. | R4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. 4.1. A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. 5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R6. | R6. Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. 6.1. Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-006-1 | R1. | R1. Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R1. | R1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R2. | R2. Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R3. | R3. Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R4. | R4. Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 4.1. The study or studies shall include the following conditions: 4.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 4.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 4.2. The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. 4.3. The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. 4.3.1. If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | 3 | 10 | Q1:Might benefit to incorporate R8 into R4 Q13: the way the benchmark model is curently defined and calibrated may have significant cost impact on entities to comply. C1, Q9: Would be benefitial to review and update Attachment 1 and Attachment 1 - CAN (Canadian variance) to simplify benchmark model enough to be directly integrated into R4 and allow more flexibility to entities to specify their own benchmark model. In addition, In Applicable Facilities Section 4.2.1 "Facilities that include power transformer(s) with a high side, wyegrounded winding with terminal voltage greater than 200 kV." Review the applicable Facilities section to ensure the standard addresses the reliability risk based on updated research.
TPL-007-4 | R5. | R5. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 5.1. The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 5.2. The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: Might benefit to incorporate R9 into R5
TPL-007-4 | R6. | R6. Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: 6.1. Be based on the effective GIC flow information provided in Requirement R5; 6.2. Document assumptions used in the analysis; 6.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 6.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 4 | 11 | Q1: Might benefit to incorporate R10 into R6 Q9: Might benefit to reference the rational for specifying 75 A or greater per phase. The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (75A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models.
TPL-007-4 | R7. | R7. Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 7.2. Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. 7.3. Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: 7.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 7.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 7.4. Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: 7.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; 7.4.2. Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and 7.4.3. Updated timetable for implementing the selected actions in Part 7.1. 7.5. Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later 7.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: Might benefit to incorporate R11 into R7
TPL-007-4 | R8. | R8. Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 8.1. The study or studies shall include the following conditions: 8.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 8.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 8.2. The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. 8.3. The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. 8.3.1. If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1:Might benefit to incorporate R8 into R4
TPL-007-4 | R9. | R9. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 9.1. The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 9.2. The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: Might benefit to incorporate R9 into R5
TPL-007-4 | R10. | R10. Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: 10.1. Be based on the effective GIC flow information provided in Requirement R9; 10.2. Document assumptions used in the analysis; 10.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 10.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 4 | 11 | Q1: Might benefit to incorporate R10 into R6 Q9:Might benefit to reference the rational for specifying 85 A or greater per phase. The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (85A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models.
TPL-007-4 | R11. | R11. Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance equirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: 11.1.List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 11.2.Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. 11.3. Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: 11.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 11.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 11.4.Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: 11.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; 11.4.2. Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and 11.4.3. Updated timetable for implementing the selected actions in Part 11.1. 11.5.Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. 11.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1: Might benefit to incorporate R11 into R7
TPL-007-4 | R12. | R12. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System model. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q6: Depending on earth condition variation in the Planning Coordinator area or System Model, having only one GIC monitor may not be appropriate to guarranty system reliability
TPL-007-4 | R13. | R13. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13

## RE
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale
PER-003-2 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-003-2 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q6-Definition of System Operator: An individual at a Control Center of a Balancing Authority, Transmission Operator, or Reliability Coordinator, who operates or directs the operation of the Bulk Electric System (BES) in Real-Time. An entity could state they have System Operators who are NOT performing reliability-related tasks. And since PER-005 allows the entity to define what are reliability-related tasks and which are not, the entity can easily get around the PER-003 requirement. PER-003 should state: Each Transmission Operator shall staff its Real-time operating positions that issues Operating Instructions with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates.
PER-003-2 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: 1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. 1.1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. 1.2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. 1.3. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. 1.4. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R2. | R2. Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: 2.1. Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. 2.1.1. Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. 2.2. Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. 2.3. Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. 2.4. Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. 3.1. Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12
PER-005-2 | R4. | R4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. 4.1. A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
PER-005-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. 5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3-Training on impacts of the personnel's job function(s) to the BES. Believe training should be on the job function.
PER-005-2 | R6. | R6. Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. 6.1. Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | Yes | No | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C3-Training on impacts of the personnel's job function(s) to the BES. Believe training should be on the job function.
PER-006-1 | R1. | R1. Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 3 | 13 | C4: No time frame for training
TPL-007-4 | R1. | R1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R2. | R2. Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R3. | R3. Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R4. | R4. Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 4.1. The study or studies shall include the following conditions: 4.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 4.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 4.2. The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. 4.3. The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. 4.3.1. If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 11 | Q7-R4 includes three separate requirements in the second sentence. These don't appear to be addressed in the VSLs. Should these be split or the VSLs modified?? Q2-Part 4.3.1 seems administrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55
TPL-007-4 | R5. | R5. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 5.1. The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 5.2. The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R6. | R6. Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: 6.1. Be based on the effective GIC flow information provided in Requirement R5; 6.2. Document assumptions used in the analysis; 6.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 6.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R7. | R7. Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 7.2. Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. 7.3. Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: 7.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 7.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 7.4. Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: 7.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; 7.4.2. Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and 7.4.3. Updated timetable for implementing the selected actions in Part 7.1. 7.5. Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later 7.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q2-Part 7.5.1 seems Administrative in nature. See Paragraph 81 review. See P81 whitepaper related to FAC-011-2 R5. Page 55
TPL-007-4 | R8. | R8. Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 8.1. The study or studies shall include the following conditions: 8.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 8.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 8.2. The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. 8.3. The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. 8.3.1. If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q2- Part 8.3.1 seems administrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55
TPL-007-4 | R9. | R9. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 9.1. The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 9.2. The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R10. | R10. Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: 10.1. Be based on the effective GIC flow information provided in Requirement R9; 10.2. Document assumptions used in the analysis; 10.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 10.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R11. | R11. Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance equirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: 11.1.List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 11.2.Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. 11.3. Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: 11.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 11.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 11.4.Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: 11.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; 11.4.2. Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and 11.4.3. Updated timetable for implementing the selected actions in Part 11.1. 11.5.Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. 11.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q2- Part 11.5.1 seems adminisrative in nature. See P81 whitepaper related to FAC-011-2 R5. Page 55
TPL-007-4 | R12. | R12. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System model. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R13. | R13. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13

## NERC
[5 empty] | Content Questions from the Standards Independent Experts Report |  |  |  | Quality Questions from the Standards Independent Experts Report
Standard Number | Requirement Number | Text of Requirement (If text is incomplete, please see entire requirement posted on NERC.com) | Supports a Reliability Objective (as defined by the Reliability Principles)? | Appropriate as a guide rather than a standard? | C1. Is the content of the requirement technically correct? | C2. Are the correct functional entities identified? | C3. Does the requirement clearly state the action(s) required to achieve the reliability outcome? | C4. Is it clear when the action needs to be taken within the standard? | Q1. Should this requirement remain as a separate requirement within this standard? (Should not be consolidated with another requirement) | Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or competency)? | Q3. Is it technologically neutral? | Q4. Are the expectation(s) of each applicable functional entity clear? | Q5. Does the requirement align with the standard's purpose statement? | Q6. Does the requirement provide more than adequate protection of BPS? | Q7. Can compliance be objectively measured? | Q8. Can it be practically implemented? | Q9. Does it have a technical basis in engineering and operations? | Q10. Is the Reliability Standard complete and self-contained (not dependent on external information to determine the required level of performance)? | Q11. Is the requirement language clear and unambiguous? | Q12. Does it use consistent and current terminology? | Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | Content Score (0-4) | Quality Score (0-13) | Comment/Rationale | Barb Nutter | Jamie Calderon | Mark Olson | Craig Struck
PER-003-2 | R1. | R1. Each Reliability Coordinator shall staff its Real-time operating positions performing Reliability Coordinator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining a valid NERC Reliability Operator certificate 1.1. Areas of Competency 1.1.1. Resource and demand balancing 1.1.2. Transmission operations 1.1.3. Emergency preparedness and operations 1.1.4. System operations 1.1.5. Protection and control 1.1.6. Voltage and reactive 1.1.7. Interchange scheduling and coordination 1.1.8. Interconnection reliability operations and coordination | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-003-2 | R2. | R2. Each Transmission Operator shall staff its Real-time operating positions performing Transmission Operator reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 2.1. Areas of Competency 2.1.1. Transmission operations 2.1.2. Emergency preparedness and operations 2.1.3. System operations 2.1.4. Protection and control 2.1.5. Voltage and reactive 2.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Transmission Operator | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-003-2 | R3. | R3. Each Balancing Authority shall staff its Real-time operating positions performing Balancing Authority reliability-related tasks with System Operators who have demonstrated minimum competency in the areas listed by obtaining and maintaining one of the following valid NERC certificates 3.1. Areas of Competency 3.1.1. Resources and demand balancing 3.1.2. Emergency preparedness and operations 3.1.3. System operations 3.1.4. Interchange scheduling and coordination 3.2. Certificates • Reliability Operator • Balancing, Interchange and Transmission Operator • Balancing and Interchange Operator | Yes | No | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. | Q1. At this time, the standard should maintain the three requirements for the three real-time positions. After the completion of the credential maintenance research project in August 2022, the PCGC will determine what/if changes need made taking the research results into account. |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R1. | R1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement a training program for its System Operators as follows: 1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall create a list of Bulk Electric System (BES) company-specific Real-time reliability-related tasks based on a defined and documented methodology. 1.1.1. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall review, and update if necessary, its list of BES companyspecific Real-time reliability-related tasks identified in part 1.1 each calendar year. 1.2. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliability-related task list created in part 1.1. 1.3. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall deliver training to its System Operators according to its training program. 1.4. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training program established in Requirement R1 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R2. | R2. Each Transmission Owner shall use a systematic approach to develop and implement a training program for its personnel identified in Applicability Section 4.1.4.1 of this standard as follows: 2.1. Each Transmission Owner shall create a list of BES company-specific Real-time reliability-related tasks based on a defined and documented methodology. 2.1.1. Each Transmission Owner shall review, and update if necessary, its list of BES company-specific Real-time reliability-related tasks identified in part 2.1 each calendar year. 2.2. Each Transmission Owner shall design and develop training materials according to its training program, based on the BES company-specific Real-time reliabilityrelated task list created in part 2.1. 2.3. Each Transmission Owner shall deliver training to its personnel identified in Applicability Section 4.1.4.1 of this standard according to its training program. 2.4. Each Transmission Owner shall conduct an evaluation each calendar year of the training program established in Requirement R2 to identify any needed changes to the training program and shall implement the changes identified. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R3. | R3. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify, at least once, the capabilities of its personnel, identified in Requirement R1 or Requirement R2, assigned to perform each of the BES company-specific Real-time reliability-related tasks identified under Requirement R1 part 1.1 or Requirement R2 part 2.1. 3.1. Within six months of a modification or addition of a BES company-specific Realtime reliability-related task, each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner shall verify the capabilities of each of its personnel identified in Requirement R1 or Requirement R2 to perform the new or modified BES company-specific Real-time reliability-related tasks identified in Requirement R1 part 1.1 or Requirement R2 part 2.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R4. | R4. Each Reliability Coordinator, Balancing Authority, Transmission Operator, and Transmission Owner that (1) has operational authority or control over Facilities with established Interconnection Reliability Operating Limits (IROLs), or (2) has established protection systems or operating guides to mitigate IROL violations, shall provide its personnel identified in Requirement R1 or Requirement R2 with emergency operations training using simulation technology such as a simulator, virtual technology, or other technology that replicates the operational behavior of the BES. 4.1. A Reliability Coordinator, Balancing Authority, Transmission Operator, or Transmission Owner that did not previously meet the criteria of Requirement R4, shall comply with Requirement R4 within 12 months of meeting the criteria. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R5. | R5. Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall use a systematic approach to develop and implement training for its identified Operations Support Personnel on how their job function(s) impact those BES company-specific Real-time reliability-related tasks identified by the entity pursuant to Requirement R1 part 1.1. 5.1 Each Reliability Coordinator, Balancing Authority, and Transmission Operator shall conduct an evaluation each calendar year of the training established in Requirement R5 to identify and implement changes to the training. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-005-2 | R6. | R6. Each Generator Operator shall use a systematic approach to develop and implement training to its personnel identified in Applicability Section 4.1.5.1 of this standard, on how their job function(s) impact the reliable operations of the BES during normal and emergency operations. 6.1. Each Generator Operator shall conduct an evaluation each calendar year of the training established in Requirement R6 to identify and implement changes to the training. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
PER-006-1 | R1. | R1. Each Generator Operator shall provide training to personnel identified in Applicability section 4.1.1.1. on the operational functionality of Protection Systems and Remedial Action Schemes (RAS) that affect the output of the generating Facility(ies) it operates. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13 |  |  |  |  | I agree with the pre-populated reponses to the questions and the scores (pre-populated as of review on 4/3/2022).
TPL-007-4 | R1. | R1. Each Planning Coordinator, in conjunction with its Transmission Planner(s), shall identify the individual and joint responsibilities of the Planning Coordinator and Transmission Planner(s) in the Planning Coordinator’s planning area for maintaining models, performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments, and implementing process(es) to obtain GMD measurement data as specified in this standard. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R2. | R2. Each responsible entity, as determined in Requirement R1, shall maintain System models and GIC System models of the responsible entity’s planning area for performing the study or studies needed to complete benchmark and supplemental GMD Vulnerability Assessments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R3. | R3. Each responsible entity, as determined in Requirement R1, shall have criteria for acceptable System steady state voltage performance for its System during the GMD events described in Attachment 1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R4. | R4. Each responsible entity, as determined in Requirement R1, shall complete a benchmark GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This benchmark GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 4.1. The study or studies shall include the following conditions: 4.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 4.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 4.2. The study or studies shall be conducted based on the benchmark GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning benchmark GMD event contained in Table 1. 4.3. The benchmark GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, and adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the benchmark GMD Vulnerability Assessment, whichever is later. 4.3.1. If a recipient of the benchmark GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 11 | C1, Q9. Since the adoption of the standard, new research performed by EPRI and others have produced new earth conductivity models and scaling factors for some areas. These updated models will improve the accuracy of GMD Vulnerabillity Assessments. Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather modeling, latitude scaling, earth conductivity modeling, analysis of power system wide area harmonics due to GIC). A periodic review is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements. https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf Q1:Supportive of RSTC comment to consider incorporating R8 (supplemental assessment) into R4 |  |  | C1, Q9. Since the adoption of the standard, new research performed by EPRI and others have produced new earth conductivity models and scaling factors for some areas. These updated models will improve the accuracy of GMD Vulnerabillity Assessments. Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather modeling, latitude scaling, earth conductivity modeling, analysis of power system wide area harmonics due to GIC). A periodic review by SDT is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements.
TPL-007-4 | R5. | R5. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the benchmark thermal impact assessment of transformers specified in Requirement R6 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 5.1. The maximum effective GIC value for the worst case geoelectric field orientation for the benchmark GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 5.2. The effective GIC time series, GIC(t), calculated using the benchmark GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 5.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R6. | R6. Each Transmission Owner and Generator Owner shall conduct a benchmark thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R5, Part 5.1, is 75 A per phase or greater. The benchmark thermal impact assessment shall: 6.1. Be based on the effective GIC flow information provided in Requirement R5; 6.2. Document assumptions used in the analysis; 6.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 6.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R5, Part 5.1. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 12 | C1, Q9. New transformer models could potentailly impact this requirement as well. The same observation applies: The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (75A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf |  |  | C1, Q9. Since the adoption of the standard, EPRI, transformer manufacturers, and industry have performed additional testing and modeling of the thermal impacts of GIC on transformers. The results of this research should be considered and factored in to the thermal impact screening criterion (75A/phase for the benchmark GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11).
TPL-007-4 | R7. | R7. Each responsible entity, as determined in Requirement R1, that concludes through the benchmark GMD Vulnerability Assessment conducted in Requirement R4 that their System does not meet the performance requirements for the steady state planning benchmark GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: [Violation Risk Factor: High] [Time Horizon: Long-term Planning] 7.1. List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 7.2. Be developed within one year of completion of the benchmark GMD Vulnerability Assessment. 7.3. Include a timetable, subject to approval for any extension sought under Part 7.4, for implementing the selected actions from Part 7.1. The timetable shall: 7.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 7.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 7.4. Be submitted to the Compliance Enforcement Authority (CEA) with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 7.3. The submitted CAP shall document the following: 7.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 7.1 and how those circumstances are beyond the control of the responsible entity; 7.4.2. Revisions to the selected actions in Part 7.1, if any, including utilization of Operating Procedures, if applicable; and 7.4.3. Updated timetable for implementing the selected actions in Part 7.1. 7.5. Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later 7.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10. R7.4 and R11.4 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach including review timing and determination. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf |  | R7 and R11 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach for registered entities. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf
TPL-007-4 | R8. | R8. Each responsible entity, as determined in Requirement R1, shall complete a supplemental GMD Vulnerability Assessment of the Near-Term Transmission Planning Horizon at least once every 60 calendar months. This supplemental GMD Vulnerability Assessment shall use a study or studies based on models identified in Requirement R2, document assumptions, and document summarized results of the steady state analysis. 8.1. The study or studies shall include the following conditions: 8.1.1. System On-Peak Load for at least one year within the Near-Term Transmission Planning Horizon; and 8.1.2. System Off-Peak Load for at least one year within the Near-Term Transmission Planning Horizon. 8.2. The study or studies shall be conducted based on the supplemental GMD event described in Attachment 1 to determine whether the System meets the performance requirements for the steady state planning supplemental GMD event contained in Table 1. 8.3. The supplemental GMD Vulnerability Assessment shall be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinators, adjacent Transmission Planners within 90 calendar days of completion, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of completion of the supplemental GMD Vulnerability Assessment, whichever is later. 8.3.1. If a recipient of the supplemental GMD Vulnerability Assessment provides documented comments on the results, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 12 | C1, Q9. Since the adoption of the standard, new research performed by EPRI and others have produced new earth conductivity models and scaling factors for some areas. These updated models will improve the accuracy of GMD Vulnerabillity Assessments. Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather modeling, latitude scaling, earth conductivity modeling, analysis of power system wide area harmonics due to GIC). A periodic review is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements. https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf |  |  | C1, Q9. New earth conductivity models (see comments to R4) will impact results of this requirement. The same observation applies: Attachment 1 (P. 30-34) should be revised with the new modeling information. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). Many aspects of GMD vulnerabiltiy assessment are developing and maturing (e.g., severe space weather models, latitude scaling and geoelectric field enhancement, earth conductivity modeling, analysis of power system wide area harmonic due to GIC). A periodic review by SDT is needed to review relevant information since TPL-007 adoption and consider potential revisions to maintain state-of-the-art standard requirements.
TPL-007-4 | R9. | R9. Each responsible entity, as determined in Requirement R1, shall provide GIC flow information to be used for the supplemental thermal impact assessment of transformers specified in Requirement R10 to each Transmission Owner and Generator Owner that owns an applicable Bulk Electric System (BES) power transformer in the planning area. The GIC flow information shall include: 9.1. The maximum effective GIC value for the worst case geoelectric field orientation for the supplemental GMD event described in Attachment 1. This value shall be provided to the Transmission Owner or Generator Owner that owns each applicable BES power transformer in the planning area. 9.2. The effective GIC time series, GIC(t), calculated using the supplemental GMD event described in Attachment 1 in response to a written request from the Transmission Owner or Generator Owner that owns an applicable BES power transformer in the planning area. GIC(t) shall be provided within 90 calendar days of receipt of the written request and after determination of the maximum effective GIC value in Part 9.1. | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 13
TPL-007-4 | R10. | R10. Each Transmission Owner and Generator Owner shall conduct a supplemental thermal impact assessment for its solely and jointly owned applicable BES power transformers where the maximum effective GIC value provided in Requirement R9, Part 9.1, is 85 A per phase or greater. The supplemental thermal impact assessment shall: 10.1. Be based on the effective GIC flow information provided in Requirement R9; 10.2. Document assumptions used in the analysis; 10.3. Describe suggested actions and supporting analysis to mitigate the impact of GICs, if any; and 10.4. Be performed and provided to the responsible entities, as determined in Requirement R1, within 24 calendar months of receiving GIC flow information specified in Requirement R9, Part 9.1. | Yes | No | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | 3 | 12 | C1, Q9. New transformer models (see comments to R6) could potentailly impact this requirement as well. The same observation applies: The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (85A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11). https://www.nerc.com/FilingsOrders/us/NERC%20Filings%20to%20FERC%20DL/GMD%20Informational%20Filing.pdf |  |  | C1, Q9. New transformer models (see comments to R6) could potentailly impact this requirement as well. The same observation applies: The results of EPRI and industry research should be considered and factored in to the thermal impact screening criterion (85A/phase for the supplemental GMD Event). Additionally, the ERO-endorsed implementation guidance for completing this requirement should be updated with the new models. Technical details to support the revisions were published by EPRI, reviewed by the NERC GMDTF and RSTC, and filed with FERC in April 2021 (RM15-11).
TPL-007-4 | R11. | R11. Each responsible entity, as determined in Requirement R1, that concludes through the supplemental GMD Vulnerability Assessment conducted in Requirement R8 that their System does not meet the performance equirements for the steady state planning supplemental GMD event contained in Table 1, shall develop a Corrective Action Plan (CAP) addressing how the performance requirements will be met. The CAP shall: 11.1.List System deficiencies and the associated actions needed to achieve required System performance. Examples of such actions include: • Installation, modification, retirement, or removal of Transmission and generation Facilities and any associated equipment. • Installation, modification, or removal of Protection Systems or Remedial Action Schemes. • Use of Operating Procedures, specifying how long they will be needed as part of the CAP. • Use of Demand-Side Management, new technologies, or other initiatives. 11.2.Be developed within one year of completion of the supplemental GMD Vulnerability Assessment. 11.3. Include a timetable, subject to approval for any extension sought under Part 11.4, for implementing the selected actions from Part 11.1. The timetable shall: 11.3.1. Specify implementation of non-hardware mitigation, if any, within two years of development of the CAP; and 11.3.2. Specify implementation of hardware mitigation, if any, within four years of development of the CAP. 11.4.Be submitted to the CEA with a request for extension of time if the responsible entity is unable to implement the CAP within the timetable provided in Part 11.3. The submitted CAP shall document the following: 11.4.1. Circumstances causing the delay for fully or partially implementing the selected actions in Part 11.1 and how those circumstances are beyond the control of the responsible entity; 11.4.2. Revisions to the selected actions in Part 11.1, if any, including utilization of Operating Procedures, if applicable; and 11.4.3. Updated timetable for implementing the selected actions in Part 11.1. 11.5.Be provided: (i) to the responsible entity’s Reliability Coordinator, adjacent Planning Coordinator(s), adjacent Transmission Planner(s), and functional entities referenced in the CAP within 90 calendar days of development or revision, and (ii) to any functional entity that submits a written request and has a reliability-related need within 90 calendar days of receipt of such request or within 90 calendar days of development or revision, whichever is later. 11.5.1. If a recipient of the CAP provides documented comments on the CAP, the responsible entity shall provide a documented response to that recipient within 90 calendar days of receipt of those comments | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | 4 | 12 | Q10. R7.4 and R11.4 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach including review timing and determination. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf |  | R7 and R11 discuss an extention request submittal to the CEA. The ERO Enterprise have developed a CAP extention review process to ensure a consistent CMEP approach for registered entities. Further this procedural information ensures a common form for registered entities to submit their request for an extention as well as provide transparency on the CAP Extention review process. The CMEP has determined any such submittal to be considered a Periodic Data Submital. As such the CAP Extention review process can be found in Appendix C of the annually posted PDS Schedule. https://www.nerc.com/pa/comp/CAOneStopShop/2022%20ERO%20Enterprise%20Periodic%20Data%20Submittal%20Schedule.pdf
TPL-007-4 | R12. | R12. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain GIC monitor data from at least one GIC monitor located in the Planning Coordinator’s planning area or other part of the system included in the Planning Coordinator’s GIC System model. | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 11 | Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance. Q6: Depending on earth condition variation in the Planning Coordinator area or System Model, having only one GIC monitor may not be appropriate to guarranty system reliability |  |  | Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance.
TPL-007-4 | R13. | R13. Each responsible entity, as determined in Requirement R1, shall implement a process to obtain geomagnetic field data for its Planning Coordinator’s planning area. | Yes | No | Yes | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 4 | 12 | Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance. |  |  | Q2. GMD data (such as required by R12 and R13) provides entities with the ability to validate models and assess the accuracy of studies performed for GMD Vulnerability Assessments. In the time since the adoption of the standard, technical guidance for performing validations has been developed for industry use. The approved requirements (R12 and R13) should be revisited, and developed into a results-based requirement by an SDT. (e.g., TPs shall use actual measurement data [under certain criteria] to assess the accuracy of GIC models and system models required by R2.) At the time of TPL-007-4's drafting, such an objective was not attainable due to lack of technical guidance.

## Resources
Questions: | Supporting Resource(s):
Supports a Reliability Objective (as defined by the Reliability Principles) | https://www.nerc.com/pa/Stand/Resources/Documents/Reliability_Principles.pdf
C2. Are the correct functional entities identified? | https://www.nerc.com/pa/Stand/Pages/FunctionalModel.aspx
Q2. Does this standard meet any of the three criteria for a results-based standard (RBS) (performance, risk (prevention) or capability)? | https://www.nerc.com/pa/Stand/Resources/Documents/Results-Based_Reliability_Standard_Development_Guidance.pdf
Q4. Are the expectation(s) of each applicable functional entity clear? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q5. Does the requirement align with the standard's purpose statement? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q6. Does the requirement provide more than adequate protection of BPS? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q7. Can compliance be objectively measured? | https://www.nerc.com/pa/comp/Pages/ERO-Enterprise-Compliance-Auditor-Manual.aspx https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q8. Can it be practically implemented? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q9. Does it have a technical basis in engineering and operations? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q10. Does the requirement depend on external information to determine the required level of performance? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q11. Is the requirement language clear and unambiguous? | https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q12. Does it use consistent and current terminology? | https://www.nerc.com/files/glossary_of_terms.pdf https://www.nerc.com/pa/Stand/Resources/Documents/Ten_Benchmarks_of_an_Excellent_Reliability_Standard.pdf
Q13. Does the requirement language support the least cost solution that achieves the reliability objective? | https://www.nerc.com/pa/Stand/Pages/Cost-Effective-Analysis-Process-CEAP-for-NERC-ERO-Standards.aspx