## Sheet1
Standard | Section | Requirements | Comment | Contact | Organization | Response
1 |  | R3 and R4 | No measurements. Requirement 1 and 2 have measurements but 3 and 4 do not. Every requirement should be measureable or it should not be a requirement. Note this is typical of many standards. There are many cases of the standards having multiple requirements and only one measurement. I will only provide this comment once. I am sure you are familiar with all of the requirements that do not have measurements. | Alan Boesch | NPPD | The assignment to the drafting team was tp translate existing requirements and measures only, not to add new ones.
1 |  | M2 | The first formula in the measure has CPS2 instead of CPM2. | Alan Boesch | NPPD | Corrections made.
1 |  | M1 | The formula on the 5th line has CPR1 instead of CPM1. | Alan Boesch | NPPD | Corrections made.
1 |  | Compliance monitoring process | The statement on the reset period seems quite stringent. If you need to go a full calendar month without a violation (defined as a Violation clock-ten minute) it would be almost impossible to reset. A more reasonable reset would be be in compliance for a calendar month. | Alan Boesch | NPPD | The drafting team does not understand your concern. The proposed change should be in Version 1.
1 |  | R2 | Much of the information contained in this requirement actually comes from the Performance Standards Review Document, not Policy 1.A | Alan Johnson | Mirant | Corrections made.
1 |  | R1 | suggest replacing "NERC Operating Committee" with "NERC Operating Committee or its designee". | Alan Johnson | Mirant | The Operating Committee may delegate the task but is accountable.
1 |  | N/A | The ACE equation, including definitions needs to be pulled over from Appendix 1A and included within this standard. Also need to decide on whether we are going to use CPS or replace it with CPM. Whichever, need to be consistent. | Alan Johnson | Mirant | Equations corrected and changed all CPM back to CPS.
1 |  | R3 | The proper reference is Policy 1A, Requirement 2.2 | Alan Johnson | Mirant | Corrections made.
1 |  | R4 | The proper reference is Policy 1A, Requirement 2.3 | Alan Johnson | Mirant | Corrections made.
1 |  |  | Various references to CPM1 and CPM2 should be updated to CPS1 and CPS2. Various references to Control Area should be updated to BA. Level 1 non-compliance should say "…or equal to 95%" | Anita Lee | AESO | Corrections made.
1 |  |  | A new terminology “CPM1 & CPM2” is being used that is more related to “Standard under development: Standard 300”. The use of this terminology needs to be clarified or corrected. | Brandian | ISO-NE | Corrections made.
1 |  |  | In various locations in Policy 1 related material, there are survey and other requirements referred to in the Performance Standard Reference Document. These Requirements should be moved into the Standard. Also, although the strikeout version of Policy 1 shows a survey section, it was omitted from the translation. | Brandian | ISO-NE | The surveys that are currently in practice were moved into the measures sections of the standards
1 | Purpose |  | Reword the Purpose to read: “To maintain interconnection frequency within the defined limits and bound large net unscheduled tie line flows by balancing real power demand and supply in real-time. | Brandian | ISO-NE | The drafting team does not agree that a purpose is to bound unscheduled tie line flows.
1 |  | R3 | For clarity purposes, please define Overlap Regulation, as it is used in this standard. If the reader is to reply upon a definition in a NERC Glossary please reference it in this standard so that uninformed readers know how to access this definition. | Deanna Phillips | BPA | Glossary provided.
1 |  | R4 | For clarity purposes, please define Overlap Regulation, as it is used in this standard. If the reader is to reply upon a definition in a NERC Glossary please reference it in this standard so that uninformed readers know how to access this definition. | Deanna Phillips | BPA | Glossary provided.
1 |  | R1 | The Resources Subcommittee has the authority to set and approve epsilon. Why did the Drafting Team shift this authority to the Operating Committee? Subtle though it may seem, this "change to existing policy" moves this technical determination from a technical group to a policy group. To ensure the technical integrity of this calculation, the authority to set epsilon should remain with the Resources Subcommittee. | Deanna Phillips | BPA | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
1 |  | M1 | To avoid the potential for “gaming”, this Standard should include requirements and/or measurements, to ensure that the “sustained interruption” clause of this measure is used seldom enough to guarantee that the resultant CPM2 calculation is representative of the Balancing Authority’s actual operation. If not covered in present NERC policy, then please pass this comment on to the appropriate Version 1 drafting teams. | Deanna Phillips | BPA | Version 1 issue.
1 |  | M1 | CPR1=(2-CF)*100% | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | CPS1=(2-CF)*100% | Gerald Reahlt | Manitoba | Corrections made.
1 |  | R3 | Existing Document References: | Gerald Reahlt | Manitoba | Corrections made.
1 |  | R4 | Existing Document References: | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | P1 A. 2.1.1.2 should be Performance Standard Reference Document 1.1.1.2 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | P1 A. 2.1.1.3 should be Performance Standard Reference Document 1.1.1.3 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | P1 A. 2.1.2 should be Performance Standard Reference Document 1.1.2 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | P1A Requirement 2.1.1 Should be: | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Performance Standard Reference Document, C. Calc of Compliance 1.1.1.1 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Policy 1A | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Policy 1A | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Requirement 2.4 should be 2.2 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Requirement 2.5 should be 2.3 | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | Standards Reference Doc states: | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | There is a large number of Existing Document References that seem to be wrong all through the document as well as quite a number were missing. The NERC Operating manual from June 15, 2004 was reviewed and the references didn’t line up. It becomes quite a bit of work when the wrong references are listed. Here is a sample: | Gerald Reahlt | Manitoba | Corrections made.
1 |  |  | A new terminology “CPM1 & CPM2” is being used that is more related to “Standard under development: Standard 300”. The use of this terminology needs to be clarified or corrected. | Guy Zito | NPCC | Corrections made.
1 | Purpose |  | Reword the Purpose to read: “To maintain interconnection frequency within the defined limits and bound large net unscheduled tie line flows by balancing real power demand and supply in real-time. | Guy Zito | NPCC | The drafting team does not agree that a purpose is to bound unscheduled tie line flows.
1 |  |  | R1 references the NERC OC (The reference should be to the Standards Developer not to NERC and not to a committee) | Mike Kormos | PJM | The drafting team believes it is inappropriate to assign the Standards Developer to set Interconnection operating targets. The task is currently assigned to the Resources Subcommittee, which reports to the Operating Committee.
1 |  | R1 | Replace OC with STANDARDS DEVELOPER | Mike Kormos | PJM | The drafting team believes it is inappropriate to assign the Standards Developer to set Interconnection operating targets. The task is currently assigned to the Resources Subcommittee, which reports to the Operating Committee.
1 |  |  | A new terminology “CPM1 & CPM2” is being used that is more related to “Standard under development: Standard 300”. The use of this terminology needs to be clarified or corrected. | Pete Henderson | IMO | Corrections made.
1 |  |  | Some references throughout the Standard do not seem to correctly correspond to the right Policy sections. It is recommended that all references be checked for accuracy to be sure they point back to the correct Policy. | Roman Carter | Southern Company | References corrected.
1 |  |  | - Reference Policy 1A Requirement 2.2.1 should be Performance Standard Reference Document, 1.2.1 |  | Southern Company | Reference corrected.
1 |  |  | - Reference Policy 1A Requirement 2.2.2 should be Performance Standard Reference Document, 1.2.2 |  | Southern Company | Reference corrected.
1 |  |  | - Reference Policy 1A Requirement 2.2.2.1 should be Performance Standard Reference Document, 1.2.2.1 |  | Southern Company | Reference corrected.
1 |  | M2 | - Suggest CPM2 be changed to CPS2 to preserve the Policy 1 designations |  | Southern Company | Corrections made.
1 |  |  | “Epsilon 1” should be changed to the symbol. |  | FRCC | Corrections made.
1 |  | R3 | CPM1 and CPM2 are not identified in the Policy used for translation. Should this requirement reference CPS1 and CPS2 or R1 and R2? For consistency, the same terminology must be used throughout the standard. |  | FRCC | Corrections made.
1 |  | M1 | CPR1 is not identified in the Policy or Reference Document used for translation. Should it be CPS1 as indicated in the Compliance Template P1T1? |  | FRCC | Corrections made.
1 |  | M2 | CPS2 not consistent with CPR1 in M1 |  | FRCC | Corrections made.
1 |  |  | In the Policy 1 redline used for translation to Version 0, “BALANCING AUTHORITY’S ACE” is used. In Version 0, the term “BALANCING AUTHORITY AREA’S ACE” is used. For clarity, the terms in the Version 0 should be consistent with the existing policy. |  | FRCC | Corrections made.
1 |  |  | In the Policy 1 redline used for translation to Version 0, the words “its average ACE” was used. In Version 0, “ its Area’s average ACE” was used. Also the terms BALANCING AUTHORITY AREA(S) were used to replace “balancing area and systems” in the Policy 1 redline used for translation to Version 0, but this change was not made throughout R2. As stated in R1, for clarity, the terms in the Version 0 should be consistent with the existing policy. |  | FRCC | Corrections made.
1 |  | M1 Existing Document References | Policy 1A Requirement 2.1 discusses supplemental regulation not compliance. |  | FRCC | Reference corrected.
1 |  |  | Recommend the following revision to remove the words “reporting area’s ACE” : Normally, sixty (60) clock-minute averages of BALANCING AUTHORITY AREA’S ACE and of the respective Interconnection’s frequency error will be used to compute the respective Hourly Average Compliance parameter. |  | FRCC | Version 1 correction.
1 |  | ? | Redline version shows more of the Introduction section included in the Standard, including the addition of a term "Standards Developer" in the place of Resources Subcommittee. Who is the "Standards Developer" and why does this term not exist in the Standard? |  | SRP | The drafting team believes it is inappropriate to assign the Standards Developer to set Interconnection operating targets. The task is currently assigned to the Resources Subcommittee, which reports to the Operating Committee.
1 |  | M1 | Reference to "reporting area" should now be converted to Functional Model term. |  | SRP | The term Area will be added to the glossary.
1 |  | R1 | Replace OC with STANDARDS DEVELOPER |  | PSE&G | The drafting team believes it is inappropriate to assign the Standards Developer to set Interconnection operating targets. The task is currently assigned to the Resources Subcommittee, which reports to the Operating Committee.
1 |  | R2.5? | Section 2.3 from Policy 1A is entirely excluded from the conversion with no explanation. |  | SRP | Policy 1A 2.3 is the same as Standard 001 Requirement 4. The reference has been corrected.
1 |  | Levels of Non Compliance | See comments for R3, M1, M2 regarding CPS/CPM/CPR |  | FRCC | Corrections made.
1 |  |  | See comments for R3, M1, M2 regarding CPS/CPM/CPR |  | FRCC | Corrections made.
1 |  |  | Should also include – P1T1 and section C 1.1 of the Performance Standards Reference Document |  | FRCC | Reference corrected.
1 |  |  | Since the NERC Performance Standard Training Document will be retired with the adoption of Version 0 Standards, it should not be referenced in Standard 001. |  | FRCC | Corrections made.
1 |  |  | Suggest changing CPM1 and CPM2 to CPS1 and CPS2 to preserve the Policy 1A designations. I agree that CPM1 and CPM2 may be better choices to communicate measures instead of standard but suggest those changes appear in Revision 1. |  | TVA | Corrections made.
1 |  | R3 and R4 | The definition for term “OVERLAP REGULATION SERVICE” used in these requirements should be provided in this standard or in a glossary of approved reliability terms. |  | FRCC | Glossary provided.
1 |  |  | The definition for term “SUPPLEMENTAL REGULATION SERVICE” used in this measure should be provided in this standard or in a glossary of approved reliability terms. |  | FRCC | Glossary provided.
1 |  | Compliance Monitoring Process | The Drafting Team proposes to remove the compliance monitoring process from the Version 0 standards. Information in the compliance template is shown here for reference. What does this mean? Would this be the same for all standards included in Version 0? |  | FRCC | The drafting team intends to include all relevent information from existing approved compliance templates in the Version 0 standards.
1 |  | R1 | The formula included in this requirement is the calculation of CPS1 and should be indicated as such in this requirement. |  | FRCC | It is referenced as CPS1 in the measure.
1 |  | R2 | The formula included in this requirement is the calculation of CPS2 and should be indicated as such in this requirement. |  | FRCC | It is referenced as CPS2in the measure.
1 |  |  | We recommend the following be added as an additional requirement instead of included in M2: A Balancing Authority providing or receiving Supplemental Regulation Service through Dynamic Transfer shall continue to be evaluated on the characteristics of its own ACE with the Supplemental Regulation Service included. |  | FRCC | This statement describes a measurement.
2 |  |  | Standard Training Document. The details of the training document that are necessary for compliance monitoring should be included in the standard. At the end of the measurement section the end of this sentence is missing. | Alan Boesch | NPPD | Required elements of the training document have been included in the standard. Sentence corrected.
2 |  | Compliance monitoring process | The Compliance Monitoring Process section of this standard references the NERC Performance | Alan Boesch | NPPD | Corrections made.
2 |  | M1 | The first graph in this measurement has 10 min. as the recovery time. This should be generic as in the second graph. The second paragraph of the Determination of AceM or Acem is incomplete and redundant. It should be removed. | Alan Boesch | NPPD | Corrections made.
2 |  | R2 | The requirement should state a minimum performance level that must be met by the reserve levels and mix of Operating Reserve - Spinning and Operating Reserve - Supplemental. | Alan Boesch | NPPD | The minimum performance level is the DCS criterion. The mix of spinning and operating reserve - supplemental is a Version 1 issue.
2 |  | Reset Period | The reset period should be one calendar quarter without a violation on a reportable disturbance. | Alan Boesch | NPPD | This clarification could be added in Version 1.
2 |  | R3 | There appear to be two requirements here. First the requirement to deploy contingency reserves. Second the requirement to review the amount of reserves to be carried. They should be split. There is no measurement included for review of the contingencies on an annual basis and there should be. | Alan Boesch | NPPD | The requirement was split. The drafting team cannot add new measures in Version 0. New measures are candidates for inclusion in a later version.
2 |  | R4 | Should include definition of Reportable Disturbance from Section B.2.4, presently in the notes | Alan Johnson | Mirant | Included in glossary.
2 |  |  | Some important info in Supporting Notes should be included in the standard. | Anita Lee | AESO | The drafting team is including in the standard only what it believes are current requirements. Non-mandatory information such as guides and notes are not part of the standard, but can be developed as complementary references.
2 | Notes |  | At a recent Resources Subcommittee meeting, the RS interpreted the second contingency rule to exclude off-line resources that were activated to provide contingency reserve. This was always the intent and the addition of a sentence to clarify this would be beneficial. | Brandian | ISO-NE | This would require a Version 1 change.
2 |  | Compliance Monitoring | Drop references to the Performance Standard Training Document and refer to the Section in the Standard itself | Brandian | ISO-NE | Materials came from both the existing policies and appendices and the Performance Standards Training Document - these references must remain in to be accurate.
2 |  | R4 | Include the term “disturbance recovery criterion” preferably in the second paragraph. | Brandian | ISO-NE | The drafting team does not believe this change is necessary.
2 |  |  | Refer to DCS, not DCM | Brandian | ISO-NE | Corrections made.
2 | Measures |  | There are references to ACEm, which is not used in the calculations at all. Drop this unless a reason to keep is provided. There is also a lack of clarity in the test concerning ACE little m and ACE big M. Additionally one of the graphs shows a 10 min. duration without explanation. Is this related to the old 10 min. recovery period? | Brandian | ISO-NE | ACEM and ACEm are used in the standard.
2 |  | R4 | The Disturbance Recovery Period referenced at the end of this requirement should be a separate requirement. | Deanna Phillips | BPA | Changed to a separate numbered requirement 4.1.
2 |  | R6 | This is an area where reducing redundancy will lead to greater clarity. Please re-write these requirements to be clearer than the 90-minutes in the second paragraph is indeed referring Contingency Reserve Restoration Period that was described in the first paragraph. | Deanna Phillips | BPA | Clarification made.
2 |  | Levels of Noncompliance | Level 1 – need to add “…to 95%.” | Ed Riley | CAISO | Corrections made.
2 |  | R6 | As a "Standard", the 90 minute rule for re-establishing contingency reserves should not be subject to arbitrary change by the NERC OC. This statement applies across the board to each standard represented in Version 0. In addition, many Reserve Sharing Groups have legally binding contracts in place that cannot easily be changed, resulting in noncompliance. | Eric Grant | Progress | Version 1 issue. This was included in Policy 1 to allow interconnection differences.
2 |  | R6 | As a "Standard", the 90 minute rule for re-establishing contingency reserves should not be subject to arbitrary change by the NERC OC. This statement applies across the board to each standard represented in Version 0. In addition, many Reserve Sharing Groups have legally binding contracts in place that cannot easily be changed, resulting in noncompliance. | Eric Grant | Progress Florida | Version 1 issue. This was included in Policy 1 to allow interconnection differences.
2 |  | R1 and others | Smaller control areas may be disadvantaged with the change in terminology from Control Area to Balancing Authority. The goal of Version 0 is to make no enhancements over existing the existing situation. TAPS wants to be assured that this name change puts no greater burden on existing control area operators. | Gayle Mayo | TAP | The Version 0 standards do not impose any new requirements on control areas. Small control areas who meet control area obligations today should be able to meet BA requirements. By splitting functions, the obligations should be reduced or remain the same.
2 |  |  | Compliance for DCS DCM will be evaluated for each reporting period. | Gerald Reahlt | Manitoba | Corrections made.
2 |  | Full compliance | CONTROL AREA Balancing Authority or RESERVE SHARING GROUP returned the ACE to zero or to its pre-disturbance level within the DISTURBANCE RECOVERY PERIOD, following the start of all Reportable Disturbances. DCS DCM is calculated quarterly and compliance evaluated as the Average Percentage Recovery (APR) as defined in the Performance Standard Training Document. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | CONTROL AREAS Balancing Authorities and/or RESERVE SHARING GROUPS must return one completed copy of DCS DCM form “NERC Control Performance Standard Survey-All Interconnections” each quarter to the Region as per set dates. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | Each BALANCING AUTHORITY or RESERVE SHARING GROUP shall submit one completed copy of DCS DCM Form, | Gerald Reahlt | Manitoba | Corrections made.
2 |  | Levels of non compliance | Each Balancing Authority or Reserve Sharing Group not meeting the Disturbance Control Standard Measure during a given calendar quarter shall increase its Contingency Reserve obligation for the calendar quarter (offset by one month) following the evaluation by the NERC or Region Compliance Monitor . [e.g. For the first calendar quarter of the year, the penalty is applied for May, June, and July.] The increase shall be directly proportional to the non-compliance with the Disturbance Control Standard Measure in the preceding quarter. This adjustment is not compounded across quarters, and is an additional percentage of reserve needed beyond the Most Severe Single Contingency. A Reserve Sharing Group may choose an allocation method for increasing its Contingency Reserve for the Reserve Sharing Group provided that this increase is fully allocated A representative from each Balancing Authority or Reserve Sharing Group that was non-compliant in the calendar quarter most recently completed shall provide written documentation verifying that the Balancing Authority or Reserve Sharing Group will apply the appropriate Disturbance Control Performance Adjustment beginning the first day of the succeeding month, and will continue to apply it for three months. The written documentation shall accompany the quarterly Disturbance Control Standard Measure Report when a Balancing Authority or Reserve Sharing Group is non-compliant. | Gerald Reahlt | Manitoba | Corrected back to CPS, so Standard is correct.
2 |  |  | in the DCS DCM calculation. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | Periodic Compliance Monitoring | Gerald Reahlt | Manitoba
2 |  | M1 | Regions Regional Reliability Council may, at their discretion, require a lower | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | Reportable Disturbances. Reportable Disturbances are contingencies that are greater than or equal to 80% of the Most Severe Single Contingency loss. Region may optionally reduce the 80% threshold, provided that normal operating characteristics are not being considered or misrepresented as contingencies. Normal operating characteristics are excluded because DCS DCM only measures the recovery from sudden, unanticipated losses of supply-side resources. | Gerald Reahlt | Manitoba | Corrections made.
2 |  | ACEA | Retain the value of ACEA | Gerald Reahlt | Manitoba | ACEM value is retained. Drafting team is uncertain of the meaning of the comment.
2 |  | ACEM | Retain the value of ACEM | Gerald Reahlt | Manitoba | ACEA value is retained. Drafting team is uncertain of the meaning of the comment.
2 |  | ACEm | Retain the value of ACEm used | Gerald Reahlt | Manitoba | ACEA value is retained. Drafting team is uncertain of the meaning of the comment.
2 |  | MW loss | Retain the value of MW loss | Gerald Reahlt | Manitoba | MWLoss value is retained. Drafting team is uncertain of the meaning of the comment.
2 |  |  | The Regional Reliability Council must submit a summary document reporting compliance with DCS DCM to NERC no later than the 20th day of the month following the end of the quarter. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | used in DCS DCM calculation. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | used in DCS DCM calculation. | Gerald Reahlt | Manitoba | Corrections made.
2 |  |  | used in the DCS calculation. | Gerald Reahlt | Manitoba | Corrections made.
2 | Notes |  | At a recent Resources Subcommittee meeting, the RS interpreted the second contingency rule to exclude off-line resources that were activated to provide contingency reserve. This was always the intent and the addition of a sentence to clarify this would be beneficial. | Guy Zito | NPCC | This would require a Version 1 change.
2 |  | Compliance Monitoring | Drop references to the Performance Standard Training Document and refer to the Section in the Standard itself | Guy Zito | NPCC | Materials came from both the existing policies and appendices and the Performance Standards Training Document - these references must remain in to be accurate.
2 |  | R4 | Include the term “disturbance recovery criterion” preferably in the second paragraph. | Guy Zito | NPCC | The drafting team does not believe this change is necessary.
2 |  |  | Refer to DCS, not DCM | Guy Zito | NPCC | Corrections made.
2 | Measures |  | There are references to ACEm, which is not used in the calculations at all. Drop this unless a reason to keep is provided. There is also a lack of clarity in the test concerning ACE little m and ACE big M. Additionally one of the graphs shows a 10 min. duration without explanation. Is this related to the old 10 min. recovery period? | Guy Zito | NPCC | ACEM and ACEm are used in the standard.
2 |  |  | Exelon Corporation agrees with the placing of some requirements and equations from the reference document into the Standard. | John Blazekovich | Exelon | Corrections made.
2 |  | all | Drop references to RSG | Mike Kormos | PJM | Reserve Sharing Groups are in current policy.
2 |  |  | From INTRO, R1 holds RSG as responsible as BA; this can be a practice but it is not necessary as there are RSG models that don't hold entire RSG responsible. | Mike Kormos | PJM | P1 Introduction states that a Reserve Sharing Group shall have the same obligations and responsibilities. The drafting team is retaining that requirement in the standard. The drafting team has interpreted that any "shall" statement in current operating policy is a requirement.
2 |  |  | R2 NOTES references the NERC RS (The reference should be to the Standards Developer not to NERC and not to a subcommittee) | Mike Kormos | PJM | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
2 |  |  | R5 indicates RSG has outage; outage is with BA not the Group. | Mike Kormos | PJM | R5 states that when a member BA has a reportable outage, then the Reserve Sharing Group has a reportable outage.
2 |  | Notes | Replace Resources Subcommittee with STANDARDS DEVELOPER | Mike Kormos | PJM | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
2 |  |  | Standards do not apply to RSG; responsibility is with BA RSG is "a way" to meet reserve obligations | Mike Kormos | PJM | Current requirement is that all generation and load is in a control area. This requirement is a translation of that requirement.
2 |  | R6 | As a "Standard", the 90 minute rule for re-establishing contingency reserves should not be subject to arbitrary change by the NERC OC. This statement applies across the board to each standard represented in Version 0. In addition, many Reserve Sharing Groups have legally binding contracts in place that cannot easily be changed, resulting in noncompliance. | Phil Creech | Progress | Version 1 issue. This was included in Policy 1 to allow interconnection differences.
2 |  |  | Add the NERC Resources Subcommittee as an additional approver for adjustment for the default performance criterion |  | TVA | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
2 |  | R3 | DCM is referenced and defined. Then starting in the Measures section and continuing through the end, all other references are to the former DCS. |  | SRP | Corrections made.
2 |  | Policy 1B, Sections 2.3, 3.3.1, 5 & 7 | Disturbance Control Performance - Recovery time duration: "The duration of the incident in hours, minutes and seconds to have the ACE return to 0" - should be changed to, "The duration of the incident in hours, minutes and seconds to have the ACE return to 0 or predisturbance value." |  | Consumers | Standard 2 R4 says the same thing, with more words, as is used in Policy 1.
2 |  | R1 | Do not agree that a BA can assign its obligation to a Reserve Sharing Group. |  | FRCC | Reworded to not say "assign obligation".
2 |  | R1 | Do not agree that a BA can assign its obligation to a Reserve Sharing Group. |  | FRCC | Reworded to not say "assign obligation".
2 |  | all | Drop references to RSG |  | PSE&G | Reserve Sharing Groups are in current policy.
2 |  | R6 | First paragraph, "Balancing Authority" needs to be formatted as a defined term, if indeed that is the reference. This reoccurs throughout Standard 002. |  | SRP | Changed all defined terms to only initial capital.
2 |  | Supporting Notes | For clarification, are supporting notes going to be included within the Standards? If so, is compliance with the notes required? We believe supporting notes should be for clarification purposes only and contain no compliance requirements. Current supporting notes contain clarification information as well as compliance requirements - additionally a good faith effort is not a measurable requirement thus needs clarity. If these notes are to remain part of the standard, the notes should be included as actual requirements. |  | FRCC | The drafting team intends to include only mandatory requirements, measures and compliance information. Additional reference information will be excluded. The drafting team evaluated the supporting notes section to determine whether it should stay in the standard or not.
2 |  |  | From INTRO, R1 holds RSG as responsible as BA; this can be a practice but it is not necessary as there are RSG models that don't hold entire RSG responsible. |  | PSE&G | P1 Introduction states that a Reserve Sharing Group shall have the same obligations and responsibilities. The drafting team is retaining that requirement in the standard. The drafting team has interpreted that any "shall" statement in current operating policy is a requirement.
2 |  |  | Level 1— Value of APR is less than 100% but greater than or equal to 95%. |  | FRCC | Corrections made.
2 |  | Levels of Non Compliance | Level 1 was translated incorrectly it should be: |  | FRCC | Corrections made.
2 |  |  | R2 NOTES references the NERC RS (The reference should be to the Standards Developer not to NERC and not to a subcommittee) |  | PSE&G | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
2 |  |  | R5 indicates RSG has outage; outage is with BA not the Group. |  | PSE&G | R5 states that when a member BA has a reportable outage, then the Reserve Sharing Group has a reportable outage.
2 |  |  | Recommend the following revision: A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a RESERVE Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority within it, with respect to monitoring and meeting the requirements of Standard 002. |  | FRCC | Corrections made.
2 |  |  | Recommend the following revision: A Balancing Authority may elect to fulfill its Contingency Reserve obligations by participating as a member of a RESERVE Sharing Group. In such cases, the Reserve Sharing Group shall have the same responsibilities and obligations as each Balancing Authority within it, with respect to monitoring and meeting the requirements of Standard 002. |  | FRCC | Corrections made.
2 |  |  | References should be Policy 1B 2 and Policy 1B 2.1 |  | TVA | References corrected.
2 |  | Notes | Replace Resources Subcommittee with STANDARDS DEVELOPER |  | PSE&G | Operating Committee provides the authority and accountability for the work of its subcommittees and can delegate the assignment to a subcommittee.
2 |  | Applicability | Reserve Sharing Group is shown as a defined term. Later in the conversion (Policy 9), the term is deleted with the note that it is no longer applicable to the Functional Model. |  | SRP | The term is used and the Policy 9 markup will be corrected.
2 |  | Compliance Monitoring Process | Since the NERC Performance Standard Training Document will be retired with the adoption of Version 0 Standards, it should not be referenced in Standard 002. |  | FRCC | Corrections made.
2 |  | Full Compliance | Since the NERC Performance Standard Training Document will be retired with the adoption of Version 0 Standards, it should not be referenced in Standard 002. |  | FRCC | Corrections made.
2 |  |  | Standards do not apply to RSG; responsibility is with BA RSG is "a way" to meet reserve obligations |  | PSE&G | R5 states that when a member BA has a reportable outage, then the Reserve Sharing Group has a reportable outage.
2 |  |  | Suggest changing DCM to DCS |  | TVA | Corrections made.
2 |  |  | Suggest changing Disturbance Control Performance Measure M1 (DCM) to NERC Disturbance Control Standard. |  | TVA | Corrections made.
2 |  |  | The definition for term “Disturbance Control Performance Adjustment” used in this measure should be provided in this standard or in a glossary of approved reliability terms. |  | FRCC | Included in glossary.
2 |  | Compliance Monitoring | The note for Standard #1 indicates that the compliance monitoring process would be removed from the standard. There is no similar note for Standard #2. Would the compliance monitoring process be excluded from all standards? This is probably OK as long as the compliance measures are adequately defined as to frequency and resposiblity, which seems to be the case for Standard #1 but omitting it from Standard #2 would leave out the timeframe in which results must be reported.. |  | PG&E | After reviewing comments, the drafting team has decided to leave in compliance monitoring information that is required.
2 |  | Measures | This is a mention of a correction to the current policy. The figure that demonstrates the reaction of ACE to a disturbance should be updated to show "15 min.". Even though it is not specifically reflecting compliance to the 15 minute standard, showing "10 min." will likely confuse people from the previous 10 minute requirement. |  | SRP | Will correct picture to say recovery period.
2 |  | Compliance Monitoring Process | Under Periodic Control, change CONTROL AREAS to BALANCING AUTHORITIES |  | Southern Company | Corrections made.
3 |  | R1 | The section in R2 dealing with calculation of the Bias should be in R1. | Alan Boesch | NPPD | The requirements were realigned as suggested.
3 |  | R2 | There is only one criteria in this measurement the remaining portion is only the method to calculate frequency bias. Calculation methods should be included in R1 and not in R2. | Alan Boesch | NPPD | The requirements were realigned as suggested.
3 |  |  | R2's existing document references have been given as Policy 1C Requirements 2, 2.1, 2.1.1 and 2.1.2 whereas these requirements do not appear to exist in the original Policy 1C. In fact, the Version 0 standard 003 Requirement R2 has been derived from Policy1C Standards 1, 1.1, 1.1.1 and 1.1.2. | Brandian | ISO-NE | References corrected.
3 |  |  | R3’s existing document is also stated incorrectly as Policy 1C Requirement 2.2. Requirement 2.2 does NOT exist in the original Policy 1C. The standard 003 Requirement R3 has been derived from Policy 1C Standard 1.1.3. | Brandian | ISO-NE | References corrected.
3 |  |  | R4’s existing document is stated incorrectly as Policy 1C Requirement 2.3 & 2.4. Requirements 2.3 & 2.4 do NOT exist in the original Policy 1C. The standard 003 Requirement R4 has been derived from Policy 1C Standard 1.1.4 & 1.1.5. | Brandian | ISO-NE | References corrected.
3 |  |  | R5’s existing document is also stated incorrectly as Policy 1C Requirement 2.5. Requirement 2.5 does NOT exist in the original Policy 1C. The standard 003 Requirement R5 has been derived from Policy 1C Standard 1.1.6 | Brandian | ISO-NE | References corrected.
3 |  |  | The NERC Resources Subcommittee interpreted that the 1% minimum applies to the computations of Policy 1 Sections 2.1.1 and 2.1.2 [Standard 003, R2]. A specific sentence should be added to the end of R4 to define clearly its applicability. This is not a change in policy. | Brandian | ISO-NE | This is a Version 1 issue.
3 |  |  | When computing bias, “several disturbances” is vaguely defined. | Brandian | ISO-NE | This is a Version 1 issue.
3 |  | R3 | Please replace the term "should", used at the end of this requirement, to the more positive and definitive term "shall". In this case, "should" is still being used in reference to the requirement that a party receiving energy from a joint unit via a flat schedule NOT include "their share of the governor droop" in their frequency bias setting. | Deanna Phillips | BPA | Corrections made.
3 |  | R2 | Please revise scope of this requirement to include only those things pertaining specifically to the requirment to operate AGC on tie-line bias control. The remaining information on how the BA is to calculate its Frequency Bias setting, including that on fixed verses variable bias setting and how they should be calculated should be moved to Standard 003 R1, which is the specific requirement for calculation of Frequency Bias Obligation. | Deanna Phillips | BPA | This clarification could be added in Version 1.
3 |  | R1 | 1.3. Bias setting verification. Each CONTROL AREA must be able to demonstrate and verify to the Performance Subcommittee that its FREQUENCY BIAS SETTING closely matches or is greater than its system response. Each BALANCING AUTHORITY shall establish and maintain a Frequency Bias Setting that closely matches or is greater than its system response. Slight change in meaning. The BA no longer has to demonstrate and verify to P.S. that it’s Bias setting closely matches or is greater than it’s system response? | Gerald Reahlt | Manitoba | Compliance enforcement is through the compliance program, not the Performance Subcommittee.
3 |  |  | R2‘s existing document references have been given as Policy 1C Requirements 2, 2.1, ,2.1.1 and 2.1.2 whereas these requirements do not appear to exist in the original Policy 1C. In fact, the Version 0 standard 003 Requirement R2 has been derived from Policy1C Standards 1, 1.1, 1.1.1 and 1.1.2. | Guy Zito | NPCC | References corrected.
3 |  |  | R2's existing document references have been given as Policy 1C Requirements 2, 2.1, 2.1.1 and 2.1.2 whereas these requirements do not appear to exist in the original Policy 1C. In fact, the Version 0 standard 003 Requirement R2 has been derived from Policy1C Standards 1, 1.1, 1.1.1 and 1.1.2. | Guy Zito | NPCC | References corrected.
3 |  |  | R3’s existing document is also stated incorrectly as Policy 1C Requirement 2.2. Requirement 2.2 does NOT exist in the original Policy 1C. The standard 003 Requirement R3 has been derived from Policy 1C Standard 1.1.3. | Guy Zito | NPCC | References corrected.
3 |  |  | R3’s existing document is also stated incorrectly as Policy 1C Requirement 2.2. Requirement 2.2 does NOT exist in the original Policy 1C. The standard 003 Requirement R3 has been derived from Policy 1C Standard 1.1.3. | Guy Zito | NPCC | References corrected.
3 |  |  | R4’s existing document is stated incorrectly as Policy 1C Requirement 2.3 & 2.4. Requirements 2.3 & 2.4 do NOT exist in the original Policy 1C. The standard 003 Requirement R4 has been derived from Policy 1C Standard 1.1.4 & 1.1.5. | Guy Zito | NPCC | References corrected.
3 |  |  | R4’s existing document is stated incorrectly as Policy 1C Requirement 2.3 & 2.4. Requirements 2.3 & 2.4 do NOT exist in the original Policy 1C. The standard 003 Requirement R4 has been derived from Policy 1C Standard 1.1.4 & 1.1.5. | Guy Zito | NPCC | References corrected.
3 |  |  | R5’s existing document is also stated incorrectly as Policy 1C Requirement 2.5. Requirement 2.5 does NOT exist in the original Policy 1C. The standard 003 Requirement R5 has been derived from Policy 1C Standard 1.1.6 | Guy Zito | NPCC | References corrected.
3 |  |  | R5’s existing document is also stated incorrectly as Policy 1C Requirement 2.5. Requirement 2.5 does NOT exist in the original Policy 1C. The standard 003 Requirement R5 has been derived from Policy 1C Standard 1.1.6. | Guy Zito | NPCC | References corrected.
3 |  |  | The NERC Resources Subcommittee interpreted that the 1% minimum applies to the computations of Policy 1 Sections 2.1.1 and 2.1.2 [Standard 003, R2]. A specific sentence should be added to the end of R4 to define clearly its applicability. This is not a change in policy. | Guy Zito | NPCC | This is a Version 1 issue.
3 |  |  | When computing bias, “several disturbances” is vaguely defined. | Guy Zito | NPCC | This is exactly as stated in Policy 1. Clarification is a Version 1 issue.
3 | Operating |  | The deletion of governor-related items (Policy 1.C) can contribute to decline on frequency response performance and potentially degrade reliability. | Travis Bessier | TXU | Version 1 issue - these are guides to be proposed as future standards.
3 |  | R5 | For clarity, this requirement should be revised as follows: A Balancing Authority that is performing Overlap Regulation Service shall increase its Frequency Bias Setting to match the frequency response of the entire area being controlled. A Balancing Authority that is performing Supplemental Regulation Service shall not change its Frequency Bias Setting for Supplemental Regulation Service. |  | FRCC | Correction made.
4 |  | All | Time Error Correction is not material to the reliability of bulk electric system. It is an after the fact correction that moves frequency away from 60 Hz. The Purpose is not a purpose but an explanation of an industry practice called time error correction. Time error correction is not in the functional model. | Alan Boesch | NPPD | Purpose was corrected.
4 |  | First Drafting Team comment | We agree with the Drafting Team that the ability to halt a Time Error Correction is a Reliability Consideration and must remain a NERC Standard. | Boisvert | TransEnergie | Agreed.
4 |  |  | Proposed Version 0 does not appear to include information from the existing Policy 1D, Standard 2, Requirements 1, 2, 3, 1.1, 1.2, 5, 5.1, 6 & 7 from the existing Policy should be restored/added. | Brandian | ISO-NE | These requirements are being included in the NAESB standard on time error correction. NERC is not duplicated the NAESB standards.
4 |  |  | Repeat answer from Question 7. This should remain a NERC standard. | Brandian | ISO-NE | JIC has assigned certain business practices to NAESB - see posted document on business practices.
4 |  | new | Add a specific requirement for all Balancing Authorities to participate in all Time Error Corrections, as instructed by the Reliability Authority that has been designated as the Time Keeper for the interconnection. | Deanna Phillips | BPA | This requirement will be part of the NAESB business practice.
4 |  | R1 | Each of the 3 statements in this "requirement" is actually a separate and distinct "requirement" that would result in separate and distinct measurements. These requirements also apply to different entities. Therefore, the requirements in this section should be separated into three separate requirements. | Deanna Phillips | BPA | The requirements were separated.
4 |  | Purpose | What is written here is far more of a "why" than a "what is the purpose". For clarity to those unfamiliar, please start with an "executive summary" type statement along the lines of "purpose is to adjust the interconnection frequency as required to correct the time errors, as reflected by electrric clocks that utilize system frequency as a basis for keeping time". | Deanna Phillips | BPA | Purpose was corrected.
4 |  | NAESB interaction | Version 0 of the NERC requirements must be consistent with Version 0 NAESB standards on this topic. The split here between NERC and NAESB needs to be clear, especially where reliability becomes an issue. We agree that the RA has the authority to intervene in a time error correction for reliability purposes. | Gayle Mayo | TAP | The division of requirements has been closely coordinated with NAESB.
4 |  | R1 | Any RELIABILITY AUTHORITY in an INTERCONNECTION shall have the authority to terminate a time error correction in progress for reliability considerations. (change from original statement) | Gerald Reahlt | Manitoba | Edit made.
4 |  |  | Any RELIABILITY COORDINATOR in an INTERCONNECTION may request the termination of a time error correction in progress. | Gerald Reahlt | Manitoba | Edit made.
4 |  |  | Proposed Version 0 does not appear to include information from the existing Policy 1D, Standard 2, Requirements 1, 2, 3, 1.1, 1.2, 5, 5.1, 6 & 7 from the existing Policy should be restored/added. | Guy Zito | NPCC | These requirements are being included in the NAESB standard on time error correction. NERC is not duplicated the NAESB standards.
4 |  |  | Proposed Version 0 does not appear to include information from the existing Policy 1D, Standard 2, Requirements 1, 2, 3, 1.1, 1.2, 5, 5.1, 6 &7. Is this intentional? | Guy Zito | NPCC | These requirements are being included in the NAESB standard on time error correction. NERC is not duplicated the NAESB standards.
4 |  |  | Repeat answer from Question 7. This should remain a NERC standard. | Guy Zito | NPCC
4 |  |  | Exelon Corporation agrees with the drafting team in regard to 1) moving time error procedures to NAESB and moving R1 to Standard 38, allowing the removal of Standard 4. | John Blazekovich | Exelon | Agreed.
4 |  |  | Proposed Version 0 does not appear to include information from the existing Policy 1D, Standard 2, Requirements 1, 2, 3, 1.1, 1.2, 5, 5.1, 6 & 7. These requirements need to be included. | Pete Henderson | IMO | These requirements are being included in the NAESB standard on time error correction. NERC is not duplicated the NAESB standards.
4 | Operating |  | With respect to any time correction control actions, Reliability Authority needs to be informed as this may need to be recognized in ACE and CPS determinations (See Standard # 005). | Travis Bessier | TXU | Informing parties of the time error correction is part of the NAESB standard.
4 |  | Drafting Team Comments | Although the Drafting Team recommends time error correction procedures become NAESB business practice standards, the use of frequency set-points for time error correction is a reliability issue and should be included in the NERC Version 0 Standard. |  | FRCC | Frequency set points have been returned to the NERC standard.
4 |  |  | In addition, requirements of this standard should provide the Reliability Authority the authority to intervene in time error correction procedures for reliability reasons. |  | FRCC | This requirement was already in the standard and will remain.
4 |  | R1 | This standard should be eliminated now rather than later. The requirement should be moved to standard 38 as recommended. |  | PG&E | Because additional requirements were included, the drafting team now recommends leaving this as a separate standard.
5 |  | R1 | This requirement is an extension of what exists today. Current language only notes that generation, transmission and load be included in the CA | Alan Johnson | Mirant | The drafting team disagrees. The current policy that all synchronized generators, loads and transmission facilities must be in a balancing area is a requirement, not a statement of fact.
5 |  |  | The last sentence in the Purpose section and the sentence in R4 do not read properly. | Anita Lee | AESO | A specific suggestion is needed.
5 |  | -Compliance Monitoring Process | - No information imported from existing document Policy 1E Requirement 2 4.8.3.3 & 4.8.3.4. | Brandian | ISO-NE | These are informational statements but not requirements.
5 |  | -Levels of Non-Compliance | - These are missing and needs to be added in Standard simultaneously. | Brandian | ISO-NE | There is no compliance template from which to draw the levels of non-compliance.
5 |  |  | Policy 1 Section 4.3.1.2 was omitted. It allows asynchronous Balancing Authorities to use alternative ACE equations other than tie line bias. NPCC requests this be added back. | Brandian | ISO-NE | Addressed in second sentence of R6 Standard 5.
5 |  | R2 | Refer to CPS not CPM | Brandian | ISO-NE | Corrected.
5 |  |  | Requirements 4.8.3.3 and 4.8.3.4 from the AGC section of Policy 1 have been removed. They were to be included in a ‘notes section’ that apparently doesn’t exist. | Brandian | ISO-NE | These are informational statements but not requirements.
5 |  | R1 | This should apply to Transmission Owners as well | Brandian | ISO-NE | Drafting team believes that the standard applies to the Transmission Operator, who is operating the system for the owner.
5 |  |  | Unlike the AIE survey, which was moved into the inadvertent section, the FRC survey was not moved into the frequency bias section. Please find a way to maintain this requirement. | Brandian | ISO-NE | Move from Policy 1G 2.1.2 to Compliance Monitoring section of 003.
5 |  | R6 | Each of the 3 statements in this "requirement" is actually a separate and distinct "requirement" that would result in separate and distinct measurements. Therefore, the requirements in this section should be separated into three separate requirements. | Deanna Phillips | BPA | Requirement was split as suggested.
5 |  | R11 | Each of the 4 statements in this "requirement" is actually a separate and distinct "requirement" that would result in separate and distinct measurements. Therefore, the 4 requirements in this section should be separated into 4 separate requirements, as they were in Policy 1. | Deanna Phillips | BPA | Requirement was split as suggested.
5 |  | R14 | Each of the 4 statements in this "requirement" is actually a separate and distinct "requirement" that would result in separate and distinct measurements. Therefore, the requirements in this section should be separated into four separate requirements. | Deanna Phillips | BPA | Requirement was split as suggested.
5 |  | R13 | The 2 statements in this "requirement" are actually separate and distinct "requirements" that would result in separate and distinct measurements. These requirements also apply to different entities. Therefore, the requirements in this section should be separated into three separate requirements. | Deanna Phillips | BPA | Requirement was split as suggested.
5 |  | R7 | The requirements for frequency of ACE calculation and use of separate and redundant frequency metering equipment are separate, distinct, and not necessarily related requirements that will result in equally separate and distince measurements. Therefore, these should be listed as separate requirements. | Deanna Phillips | BPA | Requirement was split as suggested.
5 |  | Applicability | Generator Operators and Load Serving Entities are listed as applicable entities under this translation. GOs and LSEs should not be listed as applicable entities as they are not obligated under existing standards. | Gayle Mayo | TAP | Current requirement is that all generation and load is in a control area. This requirement is a translation of that requirement.
5 |  | Compliance monitoring process | Within one week upon request, BALANCING AUTHORITIES shall provide NERC or the Regional Reliability Organization CPS CPM source data in daily CSV files with time stamped one minute averages of: 1) ACE and 2) Frequency Deviation from Schedule. | Gerald Reahlt | Manitoba | Corrected
5 |  |  | Within one week upon request, BALANCING AUTHORITIES shall provide NERC or the Regional Reliability Organization DCS DCM source data in CSV files with time stamped scan rate values for: 1) ACE and 2) Frequency Deviation from Schedule for a time period, from two minute prior to thirty minutes after the identified disturbance. | Gerald Reahlt | Manitoba | Corrected
5 |  | -Compliance Monitoring Process | - No information imported from existing document Policy 1E Requirement 2 4.8.3.3 & 4.8.3.4. | Guy Zito | NPCC | These are informational statements but not requirements.
5 |  | -Levels of Non-Compliance | - These are missing and needs to be added in Standard simultaneously. | Guy Zito | NPCC | There is no compliance template from which to draw the levels of non-compliance.
5 |  |  | Policy 1 Section 4.3.1.2 was omitted. It allows asynchronous Balancing Authorities to use alternative ACE equations other than tie line bias. NPCC requests this be added back. | Guy Zito | NPCC | The allowance for asynchronous balancing authorities is already address in R8 and does not need to be repeated.
5 |  | R2 | Refer to CPS not CPM | Guy Zito | NPCC | Corrected.
5 |  |  | Requirements 4.8.3.3 and 4.8.3.4 from the AGC section of Policy 1 have been removed. They were to be included in a ‘notes section’ that apparently doesn’t exist. | Guy Zito | NPCC | These are informational statements but not requirements.
5 |  | R1 | This should apply to Transmission Owners as well | Guy Zito | NPCC | The drafting team believes that would be redundant and that the obligation falls on the operator of the energized facilities, not the owner of the "wires".
5 |  |  | Unlike the AIE survey, which was moved into the inadvertent section, the FRC survey was not moved into the frequency bias section. Please find a way to maintain this requirement. | Guy Zito | NPCC | The FRC survey is not used in practice.
5 |  | R15 | If the BA does not have a reliability requirement for Time Error, then the requirement to calibrate the Time error equipment is not needed | Mike Kormos | PJM | Corrected.
5 |  | -Compliance Monitoring Process | - No information imported from existing document Policy 1E Requirement 2 4.8.3.3 & 4.8.3.4. | Pete Henderson | IMO | References corrected.
5 |  | -Levels of Non-Compliance | - These are missing and needs to be added in Standard simultaneously. | Pete Henderson | IMO | There is no compliance template from which to draw the levels of non-compliance.
5 |  | R1 | The BA should be the one to insure which GOPs, TOPs, LSEs, and DPs are within its BA Area. | Peter Burke | ATC | The drafting team believes the obligation is on the transmission and generation operators and loads. The comment presents a circular argument, because if transmission, generation or load is not in a balancing area, then the balancing area cannot be responsible for making sure it is.
5 |  | Effective Date | Date is missing. |  | PG&E | Corrected.
5 |  | R15 | If the BA does not have a reliability requirement for Time Error, then the requirement to calibrate the Time error equipment is not needed |  | PSE&G | Corrected.
5 |  | General Comment | In the Policy 1 redline used for translation to Version 0, it was indicated that Policy 1 sections 4.8.3.3 and 4.8.3.4 were to be in Standard 005-Supporting Notes. There are no Supporting Notes included in this standard. |  | FRCC | Supporting notes were not included in Version 0, only requirements and measures. Supporting notes may be developed as separate reference materials.
5 |  | Purpose | It is stated in the purpose that: AGC is used to limit the magnitude of Area Control Error (ACE) variations to the CPS bounds. |  | FRCC | The point of the comment is not clear.
5 |  | R6 | Net Actual Interchange and Net Schedule Interchange are not formatted as defined terms here. Will these no longer be defined terms? |  | SRP | These are defined terms. In the next posting all defined terms will have initial capitalization only.
5 |  | R8 | Section 4.3.1.2 of Policy 1E was exluded with no reason provided. |  | SRP | These are informational statements but not requirements.
5 |  | Applicability | The Generator Operator and Load Serving Intites should not be included in the list of applicable entities. |  | FRCC | Requirement 1 applies to Generator Operators and Load-Serving Entities. The drafting team believes this is a necessary requirement, since current policy requires that all generation and transmission facilities, as well as loads, must be within a balancing area.
5 |  | R2 | The term “Control Performance Measure” continues the inconsistency of terminology as discussed in Standard 001. |  | FRCC | Corrected.
5 |  |  | The term “CPS bounds” continues the inconsistency of terminology as discussed in Standard 001. |  | FRCC | Not certain which prior comment is being referenced. Attempted to make correction.
5 |  | R1 | This requirement should be revised to reflect the recommended change in applicability of the standard . |  | FRCC | See prior response on this issue.
6 |  | Compliance Monitoring | The Compliance Monitoring Process contains requirements. The level of non-compliace refers to the requirements in the Compliance Monitoring Process instead of the requirements. | Alan Boesch | NPPD | There is no compliance template from which to draw the levels of non-compliance.
6 |  | Levels of Non Compliance | The only non-compliance is related to providing a report and does not support the purpose “to ensure that, over the long term, the BALANCING AUTHORITY AREAS do not excessively depend on other BALANCING AUTHORITY AREAS in the INTERCONNECTION for meeting their demand or INTERCHANGE obligations.” | Alan Boesch | NPPD | There is no compliance template from which to draw the levels of non-compliance.
6 |  | All | The requirements do not match the pupose. | Alan Boesch | NPPD | Purpose was corrected.
6 |  | R6 | Is the BA always responsible for this calculation or could the TP be the responsible entity? | Alan Johnson | Mirant | Reference is not clear - there is no R6 in Standard 6.
6 |  |  | How will Indadvertant Interchange be paid back? Grant does not have the confidence that NAESB will establish an appropriate solution. | Bill Dearing | Grant PUD | NAESB is committed to developing a Version 0 inadvertent payback procedure based on current NERC policy.
6 |  |  | 006 does not appear to import any information from the corresponding existing document Policy 1F Requirements 5, 5.1, 5.1.1, 5.1.1.1, 5.1.1.2 and 5.1.2. | Brandian | ISO-NE | Payback procedures have been assigned by the JIC to NAESB.
6 |  |  | Repeat answer from Question 7. This should remain a NERC standard. | Brandian | ISO-NE | Payback procedures have been assigned by the JIC to NAESB.
6 |  | Purpose | The second and third sentences of this purpose statement do not specifically address the purpose of this standard. It is definition and background. As such, it should be moved to a separate "background information" type of section. | Deanna Phillips | BPA | Purpose was corrected.
6 |  | R1 - R5 | These requirements correctly describe how to calculate Inadvertent Interchange. However, they fail to actually address the stated purposes of the standard, which are to ensure that both "reliability is not compromised by inadvertent flows" and "Balancing Authorities do not excessively depend upon (others) ". Please either modify the purpose to reflect the requirements or add requirements that address the purposes as stated. | Deanna Phillips | BPA | This would require a Version 1 change.
6 |  | R5 | CAISO uses the dispute resolution process designed by WECC, and would continue to use this process. This should be identified as a Regional Difference. | Ed Riley | CAISO | The drafting team is eliminating a unique dispute resolution for inadvertent and will rely on the general NERC dispute resolution. As such, WECC should not require a regional difference.
6 |  | R4 | In the last paragraph, the term "non-reliability considerations" is going to be impossible to define in this context. After-the-fact changes that are made between consenting BAs do not affect the interconnection. | Ed Riley | CAISO | This is the language used in current operating policy and clarification will require a Version 1 change.
6 |  | Purpose | Should include "interchange ramps" in the list of things that cause inadvertent. | Ed Riley | CAISO | Purpose was corrected.
6 |  | R5 | Should read: BALANCING AUTHORITIES shall report their NET ACTUAL AND NET SCHEDULED INTERCHANGE quantities to their respective Resources Subcommittee Survey Contact by the 15th calendar day of the following month for the purposes of comparison and dispute resolution. The report shall describe..." The 3rd to last paragraph of this section states that only the "monthly summary report" is due by the 15th. | Ed Riley | CAISO | Reference corrected.
6 |  | R5 | Speaks about Appendix 1F. Where will this reside? The WECC is currently revising (updating) its reconciliation that is in due process at this time and it is expected that WECC (and the CAISO) will continue to use this process. This should be identified as a Regional Difference. | Ed Riley | CAISO | Reference to Appendix 1F is removed since a special dispute resolution for inadvertent is not retained.
6 |  | R4 | The Version 1 of this Standard should review the language in the second sentence of the last paragraph "Changes or corrections.." The language should state that reliability functions should drive the after the fact process to reflect system interchange and not market conditions. | Ed Riley | CAISO | Agreed.
6 |  |  | There does not appear to be a methodology for paying back inadvertent in this procedure. While we realize that NAESB has been given this to handle as a business practice, but that discussion has been going for quite sometime without resolution, and until there is a business practice from NAESB, this needs to be addressed in the NERC Standards. | Ed Riley | CAISO | NAESB is committed to developing a Version 0 inadvertent payback procedure based on current NERC policy.
6 |  | NAESB Drafting Team issue | Inadvertent interchange acccounting and payback are primarily business functions. The NERC Drafting Team has retained similar provisions to ensure metering and recording of inadvertent is done for reliability purposes. It is important that these standards remain consistent. Further, only a single dispute resolution process should be put into place. | Gayle Mayo | TAP | Agreed.
6 |  |  | 006 does not appear to import any information from the corresponding existing document Policy 1F Requirements 5, 5.1, 5.1.1, 5.1.1.1, 5.1.1.2 and 5.1.2. | Guy Zito | NPCC | Payback procedures have been assigned by the JIC to NAESB.
6 |  |  | Repeat answer from Question 7. This should remain a NERC standard. | Guy Zito | NPCC | Payback procedures have been assigned by the JIC to NAESB.
6 |  |  | Exelon Corporation agrees that Inadvertent Interchange payback should be developed by NAESB as a business practice. | John Blazekovich | Exelon | Agreed.
6 |  |  | R5 and Levels of Compliance reference the NERC RS (The reference should be to the Standards Developer not to NERC and not to a subcommittee) | Mike Kormos | PJM | Corrected.
6 |  | R5 | Replace Resources Subcommittee with STANDARDS DEVELOPER | Mike Kormos | PJM | Corrected.
6 |  |  | 006 does not appear to import any information from the corresponding existing document Policy 1F Requirements 5, 5.1, 5.1.1, 5.1.1.1, 5.1.1.2 and 5.1.2. These requirements need to be included. | Pete Henderson | IMO | Payback procedures have been assigned by the JIC to NAESB.
6 | Operating |  | With respect to any Inadvertent Interchange payback control schedules, Reliability Authority needs to be informed as this may need to be recognized in ACE determinations (see Standard # 005). | Travis Bessier | TXU | Agreed.
6 |  | Drafting Team Comments | Although we agree that Inadvertent Interchange payback in-kind is a business practice, section 5.1.2 of existing policy in regards to Unilateral payback should remain a reliability issue and should be included in the NERC Version 0 Standard. If the practices result in unscheduled flows, all parties will comply with Standard 012. |  | FRCC | The JIC has assigned inadvertent payback to NAESB.
6 |  |  | In addition, requirements of this standard should provide the Reliability Authority the authority to intervene in issues relating to Inadvertent Interchange if they contribute to or affect reliability issues. |  | FRCC | That is one of the requirements.
6 |  |  | R5 and Levels of Compliance reference the NERC RS (The reference should be to the Standards Developer not to NERC and not to a subcommittee) |  | PSE&G | Corrected.
6 | R5 |  | R5 Speaks about Appendix 1F. Where will Apendix 1F reside? The WECC is currently revising (upating) our reconciliation process with a document that is in due process at this time and WECC will contiunue to utilize the WECC Process. |  | WECC Interchange Subcommittee | The drafting team is eliminating a unique dispute resolution for inadvertent and will rely on the general NERC dispute resolution. As such, WECC should not require a regional difference.
6 |  | R5 | Replace Resources Subcommittee with STANDARDS DEVELOPER |  | PSE&G | Corrected.
6 |  | R4 | The definitions for terms “On-Peak and Off-Peak” are not provided. Is this due to development of the companion NAESB Standard? |  | FRCC | The definitions are in the glossary.
6 | R4 |  | The version 1 of this standard should review the language in the second sentence " Changes or corrections.." . The language should state that reliability functions should drive the after the fact process to reflect system interchange and not market conditions. |  | WECC Interchange Subcommittee | Agreed.
6 |  |  | The WECC ISAS does not see a methodology of paying back inadvertant in this procedure. We realize that NAESB has been handling this debate for quite some time, but until there is a NAESB solution this needs to be addressed in the NERC document |  | WECC Interchange Subcommittee | NAESB is committed to developing a Version 0 inadvertent payback procedure based on current NERC policy.
6 |  | R5 Drafting Team Comments | We agree with the Drafting Team that a separate dispute resolution procedure should not be maintained and that the existing Inadvertent Interchange Dispute Resolution Process and Error Adjustment Procedures either be incorporated in the existing Dispute Resolution Procedures or transferred to NAESB for development. |  | FRCC | Agreed.
6 | R5 |  | WECC has developed a dispute resloution procedure based on current NERC policy. WECC would continue to utilize this procedure. |  | WECC Interchange Subcommittee | The drafting team is eliminating a unique dispute resolution for inadvertent and will rely on the general NERC dispute resolution. As such, WECC should not require a regional difference.
7 |  |  | In the existing policy the overall role of monitoring of SOL or IROL was assigned to a Control Area. In the applicable version 0 standards a clarification on the role and relationship between Reliability Authority and Transmission Operator should be made with regards to the monitoring of SOL & IROL. | Brandian | ISO-NE | This clarification could be added in Version 1.
7 |  | R1 | Add Reliability Authority to Functional Model entities | Brandian | ISO-NE | Corrected
7 |  | R2 | Add Reliability Authority to Functional Model entities | Brandian | ISO-NE | Corrected
7 |  |  | In various locations in Policy 1 related material, there are survey and other requirements referred to in the Performance Standard Reference Document. These Requirements should be moved into the Standard. Also, although the strikeout version of Policy 1 shows a survey section, it was omitted from the translation. | Brandian | ISO-NE | Survey requirements have been moved into the measures of the applicable balancing standards.
7 |  |  | These Standards must clearly identify, define and provide examples of what a SOL and IROL are. The reason for this is that this is not consistently interpreted by industry. | Brandian | ISO-NE | The standard is not meant as a tutorial. Examples can be provided in a reference document. Adding clarifications to the standard can only be done in a future version.
7 |  |  | In the existing policy the overall role of monitoring of SOL or IROL was assigned to a Control Area. In the applicable version 0 standards a clarification on the role and relationship between Reliability Authority and Transmission Operator should be made with regards to the monitoring of SOL & IROL. | Guy Zito | NPCC | This clarification could be added in Version 1.
7 |  | R1 | Add Reliability Authority to Functional Model entities | Guy Zito | NPCC | Corrected.
7 |  | R2 | Add Reliability Authority to Functional Model entities | Guy Zito | NPCC | Corrected.
7 |  |  | In various locations in Policy 1 related material, there are survey and other requirements referred to in the Performance Standard Reference Document. These Requirements should be moved into the Standard. Also, although the strikeout version of Policy 1 shows a survey section, it was omitted from the translation. | Guy Zito | NPCC | The surveys that are currently in practice were moved into the measures sections of the standards
7 |  |  | These Standards must clearly identify, define and provide examples of what a SOL and IROL are. The reason for this is that this is not consistently interpreted by industry. | Guy Zito | NPCC | This clarification could be added in Version 1.
7 |  | R3 | Exelon Corporation suggests that Transmission Owners be included in the "Applicability" section and listed within R3. Transmission Owners are responsible for developing equipment ratings. | John Blazekovich | Exelon | Standard does not require Transmission Operator to calculate ratings; simply to have a procedure
7 |  |  | Functional Model does not require T-Oper to have wide-area data, therefore R1 and R2 should be assigned to RA category. | Mike Kormos | PJM | This requirement addresses the transmission operator requirement that corresponds to reliability authority requirements later. The transmission operator operates the system and has some accountability. The reliability authority has oversight.
7 |  | R1 & R2 | RA vs. T-Oper | Mike Kormos | PJM | The functional model does not anticipate that the transmission operator is a "switching-only" function. It also has responsibility for grid reliability.
7 |  |  | In the existing policy the overall role of monitoring of SOL or IROL was assigned to a Control Area. In the applicable version 0 standards a clarification on the role and relationship between Reliability Authority and Transmission Operator should be made with regards to the monitoring of SOL & IROL. | Pete Henderson | IMO | This clarification could be added in Version 1.
7 |  | R1 | The drawing needs to be updated to reflect IROL and SOL rather than Operating Security Limit | Ray Morella | FirstEnergy | Drawing is not being moved into a standard. DT will review all standards to ensure IROL and SOL language is used consistently.
7 |  | R2 - R5 | These standards need an extensive re-write in version 1 to enhance clarity and the understanding of what IROL's and SOL's are and how to apply them. More detail is definitely needed in this area. | Ray Morella | FirstEnergy | Agreed.
7 |  |  | Transmission Security during operation should conform to the applicable portions of Table 1 in the planning standards. | Robert Snow |  | This is a Version 1 issue.
7 |  | 2 | The requirement states "A TO shall, when practical, operate….". This is not an active enforceable requirement. What is practical for some is not for others. If it is needed as a requirement, then the wording should be changed. | Roman Carter | Southern Company | "When practical" is in the current policy.
7 |  | Applicability | Balancing Authority is listed but none of the requirements apply to it. |  | PG&E | Corrected.
7 |  | Effective Date | Date is missing. |  | PG&E | Corrected.
7 |  | R2 | Existing Document Reference should cite Standard 1.1 rather than Requirement 1.1. Also, we concur that language and examples for multiple outage criteria should be addressed in future revisions along with better references of what constitutes a SOL or IROL violation. |  | Southern Company | Corrected.
7 |  | R1, R2 | Functional Model does not requre Transmission Operator to have wide-area data, therefore R1 and R2 should be assigned to RA |  | PEPCO | Reliability Authority has been added. Transmission Operator also has an obligation to avoid cascading failures.
7 |  | R1 & R2 | RA vs. T-Oper |  | PSE&G | The functional model does not anticipate that the transmission operator is a "switching-only" function. It also has responsibility for grid reliability.
7 |  | Applicability | Since there are no requirements included in this Standard for the Balancing Authority it should be removed from the list of applicable entities. |  | FRCC | Corrected.
7 |  | R3 | The definitions for terms “Interconnected Reliability Operating Limits and System Operating Limits” used in this requirement should be provided in this standard or in a glossary of approved reliability terms. |  | FRCC | These terms are defined in the standards glossary.
7 |  | R2 | The translation of R2 from existing policy was modified. It should be revised as follows to reflect the words from existing policy: … cascading outages resulting from credible multiple outages … |  | FRCC | The drafting team does not understand your concern. Clarification would be helpful.
8 |  |  | The requirement for the RA to report to he RRC violation of SOL exceeding 30 minutes does not align with the requirements identified in the standard. | Anita Lee | AESO | Corrected.
8 |  |  | Reference to Template P2T2 is missing. | Brandian | ISO-NE | Reference corrected.
8 |  |  | In 3rd paragraph, ‘Control Area Operator’ should be replaced with ‘Balancing Authority’. | Brandian | ISO-NE | Corrected.
8 |  | Compliance Monitoring Process | In 3rd paragraph, ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Brandian | ISO-NE | Corrected.
8 |  | -R5 | Policy 2A Requirement 2.1.1 does not exist. R5 is covered by Policy 2A Standard 2.1. | Brandian | ISO-NE | Corrected.
8 |  |  | Should SOLs be reported to the Regional Council? | Brandian | ISO-NE | Policy requires only SOLs that become an IROL be reported to the RRO.
8 |  |  | This section is inconsistent with reporting of SOL and IROL violations to the RRO. The term RRO should be used consistently. | Brandian | ISO-NE | Corrected.
8 |  | Measures | 2nd paragraph should be changed to read “…within IROL or SOL…” The CAISO believes that suggesting that the determination of an SOL becoming an IROL after the fact is inappropriate. | Ed Riley | CAISO | We agree but this needs to be addressed in Version 1 standards.
8 |  | R5 | Additionally, the RRO should report to NERC. | Ed Riley | CAISO | Addressed in the compliance monitoring section.
8 |  | R4 | "Applicability" for this standard should include "Reliability Authorities" | Eric Grant | Progress | Corrected.
8 |  | R1-R5 | In general, unless better bounds/criteria are set for the determination of IROLs, this standard will not be enforceable or auditable. | Eric Grant | Progress | This is a Version 1 issue.
8 |  |  | Agree | Gerald Reahlt | Manitoba
8 |  | Measures | Evidence that the Reliability Authority evaluated actions and provided direction as required to the Control Area Operator Balancing Authority? or Transmission Operator to return the system to within limits. | Gerald Reahlt | Manitoba | Corrected.
8 |  | Levels of non compliance | The limit violation was reported to the RELIABILITY COORDINATOR Reliability Authority who did not provide appropriate direction to the Transmission Operator resulting in an IROL violation in excess of 30 minutes duration. | Gerald Reahlt | Manitoba | Corrected.
8 |  | R5 | This should be considered as a compliance monitoring or administrative procedure rather than a standard. | Gerald Reahlt | Manitoba | This will be considered in Version 1.
8 |  |  | Reference to Template P2T2 is missing. | Guy Zito | NPCC | Reference corrected.
8 |  |  | In 3rd paragraph, ‘Control Area Operator’ should be replaced with ‘Balancing Authority’. | Guy Zito | NPCC | Corrected.
8 |  | Compliance Monitoring Process | In 3rd paragraph, ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Guy Zito | NPCC | Corrected.
8 |  | -R5 | Policy 2A Requirement 2.1.1 does not exist. R5 is covered by Policy 2A Standard 2.1. | Guy Zito | NPCC | Corrected.
8 |  |  | Reference to Template P2T2 is missing. | Guy Zito | NPCC | Corrected.
8 |  |  | Should SOLs be reported to the Regional Council? | Guy Zito | NPCC | Policy requires only SOLs that become an IROL be reported to the RRO.
8 |  | Measures | This section is inconsistent with reporting of SOL and IROL violations to the RRO. The term RRO should be used consistently. | Guy Zito | NPCC | Corrected.
8 |  | R5 | The requirement of the Reliability Authority to pass on IROL violations (R5) should remain a part of this Standard until version 1 is composed. | John Blazekovich | Exelon | Agreed.
8 |  |  | Reference to Template P2T2 is missing. | Pete Henderson | IMO | Reference corrected.
8 |  | -Measures | In 3rd paragraph, ‘Control Area Operator’ should be replaced with ‘Balancing Authority’. | Pete Henderson | IMO | Corrected.
8 |  |  | In 3rd paragraph, ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Pete Henderson | IMO | Corrected.
8 |  |  | This section is inconsistent with reporting of SOL and IROL violations to the RRO. The term RRO should be used consistently. | Pete Henderson | IMO | Corrected.
8 |  | Measures | A Control Area Operator is not an entity identified in the Functional Model. | Peter Burke | ATC | Corrected.
8 |  | R3 | Per the Functional Model, the Transmission Operator orders the LSE and/or the Distribution provider to shed load. The language in this standard requires the TOP to perform this action. | Peter Burke | ATC | Corrected.
8 |  | R1 | The additional language “and the actions being taken to return the system to within limits” changes the scope of the Compliance Template P2T1. Due to the amount of information being reviewed, it is not fair to the industry to make this type of change in version zero. | Peter Burke | ATC | DT does not see the change referenced. This requirement comes from P2T1.
8 |  | R4 | "Applicability" for this standard should include "Reliability Authorities" | Phil Creech | Progress | This clarification could be added in Version 1.
8 |  | R1-R5 | In general, unless better bounds/criteria are set for the determination of IROLs, this standard will not be enforceable or auditable. | Phil Creech | Progress | This clarification could be added in Version 1.
8 |  | R1 | Refers to Reliability Coordinator rather than Reliability Authority | Ray Morella | FirstEnergy | Corrected
8 |  | R10 | With the addition of the various functional entities, this requirement should read The Transmission Operator, Balancing Authority, and Distribution Operator shall coordinate corrective action including load reduction necessary to prevent voltage collapse when reactive resources are insufficient. (The BA needs to be consulted and informed any time a significant load reduction is required in order to manage the generation resources.) | Ray Morella | FirstEnergy | Standard does not have a Requirement 10.
8 |  | Applicability | Balancing Authority is listed but none of the requirements apply to it. The Balancing Authority should be required to take action as directed by the Transmission Operator or Reliability Authority. May be able to add to R3 or R4. |  | PG&E | Corrected.
8 |  | Levels of Non Compliance | Could not find the following statement in P2T1 as referenced.Draft: "The limit violation was reported to the RELIABILITY COORDINATOR who did not provide appropriate direction to the Transmission Operator resulting in an IROL violation in excess of 30 minutes duration." |  | SRP | Corrected.
8 |  | Measures | In the translation of existing policy the term Control Area Operator remained in the last sentence of this section. It should be revised as follows: Evidence that the Reliability Authority evaluated actions and provided direction as required to the Balancing Authority or Transmission Operator to return the system to within limits. |  | FRCC | Corrected.
8 |  | Compliance Monitoring Process | In the translation of existing policy, the term Reliability Coordinator remained in the last section of the Compliance Monitoring Process. It should be revised as follows:Reliability Authorities shall report to its Regional Reliability Council any occurrences where an IROL violation extended beyond 30 minutes. |  | FRCC | Corrected.
8 |  | Levels of Non Compliance | In the translation of existing policy, the term Reliability Coordinator remained in the last sentence of the Levels of Non-Compliance. It should be revised as follows: The limit violation was reported to the Reliability Authority who did not provide appropriate direction to the Transmission Operator resulting in an IROL violation in excess of 30 minutes duration. |  | FRCC | Corrected.
8 |  | R1 | Language in Draft and Operating Policy Markup do not match. |  | SRP | Updated policy markups.
8 |  | R4 | Language in Draft, Operating Policy Markup and referenced Compliance Template P2T2 do not match. |  | SRP | Updated policy markups.
8 |  | R3 | Last paragraph of Operating Policy Markup, "Coordinating transmission outages." States, "Needs to move to Policy 4 template" but there will no longer be a Policy 4 or teplate.This is also new language added to the Standard. |  | SRP | Updated policy markups.
8 |  | R5 Drafting Team Comment | The Drafting Team stated that R5 should be considered as a compliance monitoring or administrative procedure rather than a standard. We agree, and during the transition from Version 0 Standards to Version 1 Standards these types of changes will be addressed. In addition, these types of administrative issues will need to be consistent with the approved NERC Disclosure Guidelines. |  | FRCC | Agreed this is Version 1.
8 |  | R5 | We don’t believe that the Existing Document Reference shown, Requirement 2.1.1 exists in current policies. This should be referenced as Standard 2.1. |  | Southern Company | Corrected.
9 |  |  | Requirement 3 as stated in policy is related to providing reactive resources within a Control Area. It no longer indicates that because it is now a separate requirement (it is not a sub-requirement of Requirement 2). Remove the BA beacuse it has no responsibilities for reative resources. | Alan Boesch | NPPD | Removed BA as suggested.
9 |  | R9 and R3 | Requirement R9 references a section of policy 2 that does not exist (or the latest version of Policy 2 is not posted on the NERC website). | Alan Boesch | NPPD | References corrected.
9 |  | Entire Standard | Standard 0009 is in the adobe document twice. | Alan Boesch | NPPD | Corrected.
9 |  | R8 | The 2nd paragraph of this requirement calls for the GOP to provide information to its TOP. The current language (see Policy 2B, requirement 4) only indicates that the System Operator is to be provided with information. The proposed language does clarify, but concerned that it is creating a new requirement. Should be a Version 1 consideration. | Alan Johnson | Mirant | Policy 2B Requirement 4 requires that generator reactive information be provided. The generator is obligated to provide the information to meet that requirement.
9 |  | R3 | Should use the function model name for PSE. | Anita Lee | AESO | Need clarification of the comment.
9 |  | R3 | NERC Standards should not dictate how a market works. Remove “(self-provide or provide)”. | Brandian | ISO-NE | Version 1 issue.
9 |  | 8 | The requirements on "how to operate when the voltage regulator is out of service" and that to "inform the Transmission Operator of the status of all generation reactive sources" are spearate and distinct requirements that result in very different measurements for compliance. Therefore, we feel that these requirements should be separated. | Deanna Phillips | BPA | These were split as suggested.
9 |  | R6 | The requirements to maintain sufficient Reactive Resources and to locate them in a dispersed manner are separate and distince requirements that result in very different measurements for compliance. Therefore, we feel that these requirements should be separated. | Deanna Phillips | BPA | These were split as suggested.
9 |  |  | Agree. | Gerald Reahlt | Manitoba
9 |  | R9 | The TRANSMISSION OPERATOR shall provide information on the status of all transmission reactive power resources, to its RELIABILITY AUTHORITY. | Gerald Reahlt | Manitoba | Corrected.
9 |  |  | There is no reference to this in Policy 2 B. | Gerald Reahlt | Manitoba | This is a translation of Policy 2B Requirement 4.
9 |  | R5 | This requirement may be somewhat redundant with Requirement 4, unless this requirement can be clarified to refer to more urgent actions to avoid a critical voltage violation. | Gerald Reahlt | Manitoba | Merged R5 into R4 as suggested.
9 |  | -Measures | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously | Guy Zito | NPCC | There is no compliance template from which to draw the levels of non-compliance.
9 |  |  | In 2nd paragraph, Policy 2B Requirement 4.2 does not exist. R8 is covered by Policy 2B Requirement 4. | Guy Zito | NPCC | Corrected.
9 |  |  | In 2nd paragraph, Policy 2B Requirement 4.2 should be Policy 2B Requirement 3.2. R8 is covered by Policy 2B Requirement 4. | Guy Zito | NPCC | Corrected.
9 |  | R3 | NERC Standards should not dictate how a market works. Remove “(self-provide or provide)”. | Guy Zito | NPCC | This is a current requirement in Policy 2B, requirement 2.1
9 |  | R5 | Exelon Corporation would not view the combining R4 & R5 as a significant change to the objective of this Standard or existing Operating Policy. | John Blazekovich | Exelon | Merged R5 into R4 as suggested.
9 |  |  | Functional Model does not assume BA has transmission information, thus R3 should place reactive requirements on RA not BA | Mike Kormos | PJM | Corrected to Transmission Service Provider.
9 |  |  | R10 - RA (not BA) will be taking actions re voltage collapse | Mike Kormos | PJM | Corrected.
9 |  |  | R4 is another wide-area vs. local area issue | Mike Kormos | PJM | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  |  | R6 - T-Oper can't be held responsible to disperse Reactive over wide area | Mike Kormos | PJM | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  | R3 & R10 | RA vs. BA | Mike Kormos | PJM | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  | R4 & R6 | RA vs. T-Oper | Mike Kormos | PJM | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously | Pete Henderson | IMO | There is no compliance template from which to draw the levels of non-compliance.
9 |  |  | In 2nd paragraph, Policy 2B Requirement 4.2 should be Policy 2B Requirement 3.2. R8 is covered by Policy 2B Requirement 4. | Pete Henderson | IMO | Corrected.
9 |  | R10 | Per the Functional Model, the Transmission Operator orders the LSE and/or the Distribution provider to shed load. The language in this standard requires the TOP to perform this action. | Peter Burke | ATC | Changed to tranmission operator "shall initiate". The transmission operator may either operate to shed load or direct the LSE/DP to do so.
9 |  | R11 | Policy 2B R6 today states that devices used to regulate transmission voltage and reactive flow shall be available under the direction of the System Operator. It does not state anything about establishing authority. | Raj Rana | AEP | Having reactive devices available for direction by the transmission operator requires the transmission operator have authority to direct their use. This is a tranlslation of a passive statement to an active statement.
9 |  | 11 | The requirement states " The TO shall establish authority to direct…..". How do you establish authority and is this what the requirement really is meant to say? | Roman Carter | Southern Company | This is a translation to active voice.
9 |  | 5 | The requirement states "The TO, if necessary, shall…" This is not an active enforceable requirement. What is necessary for one is not for another. If it is needed as a requirement, then the wording should be changed. | Roman Carter | Southern Company | Requirement was merged into Requirement 4.
9 |  | R6 | Add Balancing Authority as in above Requirements. | Travis Bessier | TXU | The transmission operator is responsible for managing reactive resources for voltage control.
9 |  | R1 | Add Generation Owner as an entity that also provides voltage support as stated in the Functional Model. Balancing Authority is another entity that should also be added to R1. | Travis Bessier | TXU | Version 1 issue.
9 |  | R7, R8, R10, R11 | Add Reliability Authority for its role in overall reliability coordination even though existing Functional Model omits this aspect with respect to voltage/reactive support. | Travis Bessier | TXU | Version 1 issue.
9 |  | R5 | Add the Balancing Authority as in R1 & R3. Also add "as directed by Reliability Authority" to the end of R5. | Travis Bessier | TXU | Version 1 issue.
9 | Operating |  | Both existing Policy and Functional Model appear deficient with respect to responsibility for voltage/reactive support. It appears that Version 0 attempts to address this somewhat. See following suggested changes. | Travis Bessier | TXU | Version 1 issue.
9 |  | R3 | Version 0 includes Balancing Authority even though not found in the Functional Model but this is advantageous because it helps address aforementioned deficiency. | Travis Bessier | TXU | Corrected.
9 |  | R4 & R6 | RA vs. T-Oper |  | PSE&G | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  |  | A Distribution Provider needs to present a reasonable Power Factor to the transmission system. |  | PSE&G | Version 1 issue.
9 |  |  | Functional Model does not assume BA has transmission information, thus R3 should place reactive requirements on RA not BA |  | PSE&G | Corrected.
9 |  |  | Guide 4 on DC Equipment does not appear to be included in the new standards. |  | Southern Company | Guides are not required.
9 |  | R11 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Corrected policy markups.
9 |  | R5 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Corrected policy markups.
9 |  | R8 | Language in Draft and Operating Policy Markup don't match.Draft: "The GENERATOR OPERATOR shall provide information to its Transmission Operator . . . . "Operating Policy Markup: "The GENERATOR OPERATOR shall provide information . . . to its Reliability Authority." |  | SRP | Policy markups corrected.
9 |  | R10 | Operating Policy Markup includes DISTRIBUTION OPERATOR. |  | SRP | Policy markups corrected.
9 |  | R11 | Policy 2B R6 today states that devices used to regulate transmission voltage and reactive flow shall be available under the direction of the System Operator. It does not state anything about establishing authority. |  |  | The drafting team has translated a passive statement into an active statement.
9 |  |  | R10 - RA (not BA) will be taking actions re voltage collapse |  | PSE&G | Corrected.
9 |  |  | R4 is another wide-area vs. local area issue |  | PSE&G | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  |  | R6 - T-Oper can't be held responsible to disperse Reactive over wide area |  | PSE&G | The drafting team believes the transmission operator is responsible for maintaining the voltage profile of its system and the RA has reliability oversight.
9 |  | R3 & R10 | RA vs. BA |  | PSE&G | Corrected.
9 |  | R9 | Same as above, there is no 4.1. |  | Southern Company | Corrected.
9 |  | R8 | The Existing Document Reference should be Requirement 4 rather than 4.2. There is no 4.2. |  | Southern Company | Corrected.
10 |  | Attachment 1 | May need to either add more text or include some references for clarity. For example, "E-Tag System" is referenced for the first time. Where does one go to find out what this is? As another example, there is a reference to a NERC TLR event. Again, this needs to be defined or a reference (to the NAESB TLR Standard?) provided. | Alan Johnson | Mirant | Clarifications added.
10 |  | R1 | 2.1 P3T3 goes directly to Level 4 violations. The CAISO agrees with the sanctions for a tag violation, but believes the practice as written is too stringent and there should be Level 1 through 4 violations. This should be identified as a Regional Difference. | Ed Riley | CAISO | Version 1 issue.
10 |  | R2 | Change "exempt from tagging for 60 minutes" to "tagged within 60 minutes". | Ed Riley | CAISO | Corrected.
10 |  | R2 | Will a new tag template be issued to conform with the functional entities? Will E-tag Spec need to be changed to implement this standard? | Eric Grant | Progress | There may be some function substitutions, but the operation of E-Tag should be unaffected by Version 0.
10 |  | R2 | Will a new tag template be issued to conform with the functional entities? Will E-tag Spec need to be changed to implement this standard? | Eric Grant | Progress Florida | There may be some function substitutions, but the operation of E-Tag should be unaffected by Version 0.
10 |  |  | This is a combination of Policy 3A Requirement 2.1 & 2.4.1 not just a translation of Requirement 2.4.1. | Guy Zito | NPCC | Agreed.
10 |  | R2 | Will a new tag template be issued to conform with the functional entities? Will E-tag Spec need to be changed to implement this standard? | Phil Creech | Progress | There may be some function substitutions, but the operation of E-Tag should be unaffected by Version 0.
10 |  | R1 | Current Policy indicates that bilateral payback should be tagged. The Reliability Standard places this requirement on the Sink BA. This is a new requirement. | Raj Rana | AEP | Addressed in Policy 3A Requirement 2.1, 4th bullet.
10 |  | R1 | In the markup version of the policy, CA has been replaced with BA, TP has been replaced with TSP. Are these exact equivalents? | Raj Rana | AEP | This is a best translation to the functional model.
10 |  | R2 | Policy says that "If a PSE is not involved in the Transaction, such as delivery from a jointly owned generator…". R2 takes this "such as" and makes it the only situation in which a BA would tag. This is a new restriction. | Raj Rana | AEP | This comment needs to be explained further.
10 |  | R1 | Policy says that Dynamic Interchange Schedules should be tagged (doesn't say who has to do it). R1 and R4 says that the Load PSE is responsible. This is a new restriction. | Raj Rana | AEP | Policy 3A Requirements 1 and 2 obligate the PSE to tag transactions to which it is party, including dynamic schedules. Futher clarifications should be addressed in Version 1.
10 |  | R1 | Purpose of 010 indicates that "certain" transactions are tagged in adequate time. This makes it sound like it is the exception rather than the rule to tag in adequate time. | Raj Rana | AEP | This is because exceptions exist to the tagging requirements.
10 |  | R1 | R1 says the load PSE is responsible for tagging. Policy says the load PSE is responsible for providing the tag with the caveat that any PSE may provide the tag, but the load PSE is responsible for ensuring that a single tag is provided. R1 is changing the requirements. | Raj Rana | AEP | Agreed - language was corrected.
10 |  | R2 | The exemption from tagging for 60 minutes now includes the words "reqardless of magnitude or duration". Why has this addition been made? | Raj Rana | AEP | Corrected.
10 |  | R2 | The note about a change in the hourly energy profile of 25% requiring a revised tag has been dropped without explanation. | Raj Rana | AEP | The drafting team is asking a question about what the threshold should be for tagging dynamic transfers.
10 |  | R1 | The reference indicates that this is from 3A section 2.1 of the Policy. It is from section 1.2 | Raj Rana | AEP | Corrected.
10 |  | R2 - R3 | References Operating Security Limit violation, should be SOL and IROL. | Ray Morella | FirstEnergy | Corrected.
10 |  | 1 | The first sentence in the requirement should say "The load-serving PSE shall be responsible for tagging all Interchange Transactions except for those identified as being required by the Sink BA". The second sentence should pick up here and say "These Interchange Transactions (those that are between BA areas) shall include all transfers that are….etc." Otherwise, Requirement 3 of this Std 10 conflicts with Req. 1 | Roman Carter | Southern Company | Corrected.
10 |  | 2 | The requirement left out an important point contained within Policy 3 section A 1.2 under note 2.-"If a PSE is not inolved in the Transaction, such as delivery from a jointly owned generator, then the Sink BA is responsible for providing the tag". This requirement should be added to Standard 10 | Roman Carter | Southern Company | Corrected.
10 |  | R2 | Clarification of the following is required: … such as through prearranged reserve sharing agreements or other arrangements…Does this mean that reserves will need to be tagged is an entity is part of a reserve sharing group, or, does it mean reserves are tagged if purchased from another member of the reserve sharing group when the purchaser cannot cover their required reserves? |  | FRCC | This is a restatement of the requirement in Policy 3A, requirement 2.1, 5th bullet. Any further clarification must be done in after Version 0.
10 |  | R2 | Clarify the last sentence - Such interchange shall be "tagged within 60 minutes" from the time that the interchange transaction begins |  | WECC Interchange Subcommittee | Further clarification is a Version 1 issue.
10 |  | R1 | Current Policy indicates that bilateral payback should be tagged. The Reliability Standard places this requirement on the Sink BA. This is a new requirement. |  |  | This is a requirement of Policy 3A requirement 2.1, 4th bullet.
10 |  | R1 | In the markup version of the policy, CA has been replaced with BA, TP has been replaced with TSP. Are these exact equivalents? |  |  | This is an interpretation for the purspose of the existing rules.
10 |  | R2 | Policy says that "If a PSE is not involved in the Transaction, such as delivery from a jointly owned generator…". R2 takes this "such as" and makes it the only situation in which a BA would tag. This is a new restriction. |  |  | This comment needs to be explained further.
10 |  | R1 | Policy says that Dynamic Interchange Schedules should be tagged (doesn't say who has to do it). R1 and R4 says that the Load PSE is responsible. This is a new restriction. |  |  | Policy 3A Requirements 1 and 2 obligate the PSE to tag transactions to which it is party, including dynamic schedules. Futher clarifications should be addressed in Version 1.
10 |  | R1 | Purpose of 010 indicates that "certain" transactions are tagged in adequate time. This makes it sound like it is the exception rather than the rule to tag in adequate time. |  |  | There are exceptions.
10 |  | R1 | R1 says the load PSE is responsible for tagging. Policy says the load PSE is responsible for providing the tag with the caveat that any PSE may provide the tag, but the load PSE is responsible for ensuring that a single tag is provided. R1 is changing the requirements. |  |  | Corrected.
10 |  |  | Std 10, R1 - The first sentence in the requirement should say "The load-serving PSE shall be responsible for tagging all Interchange Transactions except for those identified as being required by the Sink BA". The second sentence should pick up here and say "These Interchange Transactions (those that are between BA areas) shall include all transfers that are….etc." Otherwise, Requirement 3 of this Std 10 conflicts with Req. 1. |  | Southern Company | Corrected.
10 |  | R2 | The exemption from tagging for 60 minutes now includes the words "reqardless of magnitude or duration". Why has this addition been made? |  |  | Corrected.
10 |  | R2 | The note about a change in the hourly energy profile of 25% requiring a revised tag has been dropped without explanation. |  |  | This was a question put to industry for comment.
10 | R1 | 2.1 P3T3 | The P3T3 template goes directly to Level 4. The WECC ISAS agrees with sanctions for tag violations, but think the practice as written is too stringent and there should be level 1 through 4 violations |  | WECC Interchange Subcommittee | Version 1 issue.
10 |  | R1 | The reference indicates that this is from 3A section 2.1 of the Policy. It is from section 1.2 |  |  | Corrected.
10 |  | R1 | This document excludes the Policy 3 requirement of redoing a tag if there is a change of 25% . By excluding this existing language you are changing the scope of this document and not living with the version zero " no change direction" |  | WECC Interchange Subcommittee | This was a question put to industry for comment.
11 |  | R3 | “Energy profile, including the ramp (ability of the generation to support the magnitude and maneuverability of the transaction" is not correct. Maneuverability is associated with generation. Please restate as: Energy profile (ability to support the magnitude of the transaction) The ramp (ability of generation maneuverability to accommodate) | Alan Boesch | NPPD | Corrected.
11 |  | R4 | The numbering sequence skips R4. | Alan Boesch | NPPD | Corrected.
11 |  | R2 | The following text from Pollicy 3A, Requirement 4 should be inserted at the end of the first sentence: "based on established reliability criteria and adequacy of Interconnected Operating Services and transmission rights as well as the reasonableness of the Interchange Transaction Tag." | Alan Johnson | Mirant | Corrected.
11 |  |  | A new task “Connectivity of adjacent Transmission Service Providers” is added for verification and assessment by the Transmission Service Providers in order to approve or deny an Interchange Transaction. | Brandian | ISO-NE | Dtafting team will verify this is an existing requirement or delete.
11 |  |  | In 2nd paragraph, Policy 2B Requirement 4.2 should be Policy 2B Requirement 3.2. R8 is covered by Policy 2B Requirement 4. | Brandian | ISO-NE | Cannot find reference.
11 |  |  | The 4th bullet should be amended to read "all interchange transactions" not "multiple interchange transactions". | Brandian | ISO-NE | Corrected.
11 |  |  | The 5th bullet is not included in existing policy - it makes sense to include it however it is a new requirement. | Brandian | ISO-NE | Dtafting team will verify this is an existing requirement or delete.
11 |  | NEW | Add a requirement requiring Generation Operators to communicate their approval or denial of the tag; in much the way as those requirements for the BA and the TSP to approve or deny the tag. This requirements is part of Policy 3A Requirement 4. Addition of this requirement is necessary in order to make the requirements of Version 0 the same as those of Policy 3 in this regard. | Deanna Phillips | BPA | This is a business practice to be addressed by NAESB, not a reliability requirement.
11 |  | R1 | Please modify this requirement to ethe need to provide this information to the Generation Operator, as required in Policy 3A Requirement 2.2. Without this information, the Generation Operator has no way of ensuring that tags were not submitted for his generator to produce more services than it either contracted to provide or is able to provide at the time. | Deanna Phillips | BPA | This is a business practice to be addressed by NAESB, not a reliability requirement.
11 |  | Regional Differences | Losses are tagged separately in the WECC and the CAISO does not use the losses portion of the tag in its current form. The CAISO would like to add "WECC Losses Waiver" to identify this Regional Difference. | Ed Riley | CAISO | A waiver is not required. Tagging losses separately is an acceptable implementation of the Version 0 requirements. The requirement is to tag losses, not necessarily on the same form.
11 |  |  | A new task “Connectivity of adjacent Transmission Service Providers” is added for verification and assessment by the Transmission Service Providers in order to approve or deny an Interchange Transaction. | Guy Zito | NPCC | Dtafting team will verify this is an existing requirement or delete.
11 |  |  | The 4th bullet should be amended to read "all interchange transactions" not "multiple interchange transactions". | Guy Zito | NPCC | Corrected.
11 |  |  | The 5th bullet is not included in existing policy - it makes sense to include it however it is a new requirement. | Guy Zito | NPCC | Dtafting team will verify this is an existing requirement or delete.
11 |  |  | Transmission Service Provider should be changed to Transmission Operator. | Guy Zito | NPCC | The Transmission Service Provider evaluates transaction tags and may do so in coordination with the Transmission Operator.
11 |  |  | A new task “Connectivity of adjacent Transmission Service Providers” is added for verification and assessment by the Transmission Service Providers in order to approve or deny an Interchange Transaction. | Pete Henderson | IMO | Dtafting team will verify this is an existing requirement or delete.
11 |  |  | The 4th bullet should be amended to read "all interchange transactions" not "multiple interchange transactions". | Pete Henderson | IMO | Corrected.
11 |  |  | The 5th bullet is not included in existing policy - it makes sense to include it however it is a new requirement. | Pete Henderson | IMO | Dtafting team will verify this is an existing requirement or delete.
11 |  | R3 | Current Policy allows for the PSE or LSE to defer approval to the Host Control Area. This allowance has been dropped. | Raj Rana | AEP | Need clarification of the comment.
11 |  | R1 | The Markup Policy differs from the Current Policy regarding who the complete tag must be provided to. Cannot adequately evaluate the Reliability Standard because the Markup is misleading. | Raj Rana | AEP | Markup has been corrected.
11 |  | purpose | The purpose states that all affected Reliability Entities will assess the reliability impacts before approving or denying the tag. Currently, Reliability Authorities have nothing to do with approval or denial of tags. They assess AFTER the tags have been approved and confirmed. To put the Reliability Authorities in the position of approving and denying tags would require a restructuring of the entire tagging process. | Raj Rana | AEP | Tags are provided to Reliability Authorities through the IDC. There is no statement requiring RA approval of a tag.
11 |  | 2 | Bullet 4 should say "OASIS reservation accomodates ALL Interchange Transactions" vs. multiple Interchange Transactions. | Roman Carter | Southern Company | Corrected.
11 |  | 4 | There is not a requirement 4. However, there is a requirement 3 and 5. It needs renumbering. | Roman Carter | Southern Company | Corrected.
11 |  | R3 | Current Policy allows for the PSE or LSE to defer approval to the Host Control Area. This allowance has been dropped. |  |  | This is a NAESB Version 0 business practice.
11 | Regional Differences | R2 | Losses are tagged separately in the WECC and we do not use the losses portion of the tagin its current form. WECC ISAS would ask for a regional difference to accomodate our current practice. |  | WECC Interchange Subcommittee | A waiver is not required. Tagging losses separately is an acceptable implementation of the Version 0 requirements. The requirement is to tag losses, not necessarily on the same form.
11 |  | R3 or new R# | Reliability Authority or Balancing Authority tag assessment should ensure that proposed interchange transactions or schedule changes do not cause the maximum Net Scheduled Interchange between BA's to exceed the total capacity of facilities or the established network Total Transfer Capability (TTC) between the BA's (Current NERC Policy 3 B, 5.1-5.2). Total Capacity of Facilities and TTC should be added as defined terms. |  | SRP | Could not find this reference.
11 |  |  | Std 11, R4 - There is not a requirement 4. However, there is a requirement 3 and 5. It needs renumbering. |  | Southern Company | Corrected.
11 |  | R1 | The language needs to be clear that the generating entity receives the tag. We understand that NERC will hand off the tagging requirements to be covered in the NAESB standard but feel this needs to remain in this version zero document |  | WECC Interchange Subcommittee | This is a NAESB Version 0 business practice.
11 |  | R1 | The Markup Policy differs from the Current Policy regarding who the complete tag must be provided to. Cannot adequately evaluate the Reliability Standard because the Markup is misleading. |  |  | Markup has been corrected.
11 |  | purpose | The purpose states that all affected Reliability Entities will assess the reliability impacts before approving or denying the tag. Currently, Reliability Authorities have nothing to do with approval or denial of tags. They assess AFTER the tags have been approved and confirmed. To put the Reliability Authorities in the position of approving and denying tags would require a restructuring of the entire tagging process. |  |  | Reliability Authority is not referenced in tag approval. Purpose clarified.
11 |  | R3 or new R# | There are some important missing reliability considerations that are in the existing Policy 3 that should be included in Version 0 as requirements. Reliability Authority or perhaps even Balancing Authority tag assessment should ensure that proposed interchange transactions or schedule changes do not knowingly cause any other systems to violate established operating reliability criteria. (Current NERC Policy 3 B, 4.1.2) |  | SRP | Policy 3 reviewed to ensure all reliability assessments included.
12 |  |  | The reference for the last bullet should be Policy 3B, Requirement 4.1.3 instead of Policy 3C, Requirement 3.4. | Brandian | ISO-NE | References corrected.
12 |  |  | The reference should be Policy 3A, Requirement 6 instead of Requirement 1. | Brandian | ISO-NE | References corrected.
12 |  |  | The reference should be Policy 3B, Requirement 1 instead of Policy 3B, Requirement 4.1.3. | Brandian | ISO-NE | References corrected.
12 |  |  | The reference for the last bullet should be Policy 3B, Requirement 4.1.3 instead of Policy 3C, Requirement 3.4 | Guy Zito | NPCC | References corrected.
12 |  |  | The reference for the last bullet should be Policy 3B, Requirement 4.1.3 instead of Policy 3C, Requirement 3.4. | Guy Zito | NPCC | References corrected.
12 |  |  | The reference should be Policy 3A, Requirement 6 instead of Requirement 1. | Guy Zito | NPCC | References corrected.
12 |  |  | The reference should be Policy 3B, Requirement 1 instead of Policy 3B, Requirement 4.1.3. | Guy Zito | NPCC | References corrected.
12 |  |  | The reference for the last bullet should be Policy 3B, Requirement 4.1.3 instead of Policy 3C, Requirement 3.4. | Pete Henderson | IMO | References corrected.
12 |  |  | The reference should be Policy 3A, Requirement 6 instead of Requirement 1. | Pete Henderson | IMO | References corrected.
12 |  |  | The reference should be Policy 3B, Requirement 1 instead of Policy 3B, Requirement 4.1.3. | Pete Henderson | IMO | References corrected.
12 |  | R1 | Current Policy indicates that the sending and receiving CAs should agree "before making generation changes". The Reliability Standards change this to "prior to implementation in their ACE equation…". This unannounced change should be carefully reviewed. | Raj Rana | AEP | R1 requires the balancing authorities to agree on the schedule details prior to implementation.
12 |  | R2 | Should also be a cross reference to Policy 3B 4.1.3 on DC ties. | Raj Rana | AEP | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 2.0 on ramp start time. | Raj Rana | AEP | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 3.0 on ramps duration. | Raj Rana | AEP | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 3.4 on DCS. | Raj Rana | AEP | References corrected.
12 |  | R2 | The reference is incorrect. It should be to Policy 3B section 1 | Raj Rana | AEP | References corrected.
12 |  | R1 | Current Policy indicates that the sending and receiving CAs should agree "before making generation changes". The Reliability Standards change this to "prior to implementation in their ACE equation…". This unannounced change should be carefully reviewed. |  |  | R1 requires the balancing authorities to agree on the schedule details prior to implementation.
12 |  | R2 | Should also be a cross reference to Policy 3B 4.1.3 on DC ties. |  |  | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 2.0 on ramp start time. |  |  | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 3.0 on ramps duration. |  |  | References corrected.
12 |  | R1 | Should include a cross reference to Policy 3C 3.4 on DCS. |  |  | References corrected.
12 |  | R2 | The reference is incorrect. It should be to Policy 3B section 1 |  |  | References corrected.
12 |  | Purpose | The word AGC should be removed. |  | Southern Company | Corrected.
13 |  | R1 | According to the functional model the Transmission Operator is the transmission entity involved in transmission modifications for reliability events. The Transmission Service Provider should be removed and replaced by the TOP. | Alan Boesch | NPPD | This would be a change from current policy - address in Version 1.
13 |  | R4 | Agree in concept with the proposed modification, but would like some technical support for the proposed breakpoints. It seems that should probably be addressed as a Version 1 modification. | Alan Johnson | Mirant | Agreed. Question will be looked at again in second posting.
13 |  |  | - The reference should be Policy 3D, Requirement 2.5. | Brandian | ISO-NE | Reference corrected.
13 |  |  | - This requirement includes the existing PSE responsibility for updating tags associated with dynamic schedules where they deviate by more than 25%. The drafting team is asking for acceptance of new criteria however a question is still raised whether for transactions >100MW the requirement is 10% or 25%. Which of this is required or appropriate. | Brandian | ISO-NE | Addressed as a question to industry in the second posting.
13 |  | -Measures | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously | Brandian | ISO-NE | Compliance measures and compliance monitoring will be provided only as available in an existing compliance template. All other additions are for Version 1.
13 |  |  | Transmission Service Provider should be changed to Transmission Operator. | Brandian | ISO-NE | The drafting team believes the transmission service provider is responsible for the interface with the PSE in assessing and implementing transactions.
13 |  | R4 | We agree with the modified language on when the tags for Dynamic Schedules must be modified. | Deanna Phillips | BPA | Agreed. Question will be looked at again in second posting.
13 |  | R4 | The CAISO agrees with the drafting team proposal. | Ed Riley | CAISO | Agreed. Question will be looked at again in second posting.
13 |  | R4 | The Drafting Team proposed improvement is acceptable. I still have reservations with the fact that this standard could require me to re-tag a firm dynamic transaction in a window that would cause it to be treated as non-firm for curtailment purposes during TLR. In addition, large balancing authorities which do not have to tag internal transactions, and thus are not subject to this standard, may cause harm to smaller neighboring balancing authorities which are subject to this standard. | Eric Grant | Progress | Agreed. Question will be looked at again in second posting.
13 |  | R4 | The Drafting Team proposed improvement is acceptable. I still have reservations with the fact that this standard could require me to re-tag a firm dynamic transaction in a window that would cause it to be treated as non-firm for curtailment purposes during TLR. In addition, large balancing authorities which do not have to tag internal transactions, and thus are not subject to this standard, may cause harm to smaller neighboring balancing authorities which are subject to this standard. | Eric Grant | Progress Florida | Agreed. Question will be looked at again in second posting.
13 |  | R4 | For the TAPS Group, many with smaller loads and transactions, a change in deviation threshold from a percentage to MW value may be preferred. However, Version 0 is a translation of current policies only. For Version 1, a preferred change would be a straight MW deviation threshold level. This approach would maintain reliability and not overly burden small users with no added reliability increase. | Gayle Mayo | TAP | The drafting team has refined the proposal and will ask the question again in the second posting.
13 |  |  | - The reference should be Policy 3D, Requirement 2.5. | Guy Zito | NPCC | Reference corrected.
13 |  |  | - This requirement includes the existing PSE responsibility for updating tags associated with dynamic schedules where they deviate by more than 25%. The drafting team is asking for acceptance of new criteria however a question is still raised whether for transactions >100MW the requirement is 10% or 25%. Which of this is required or appropriate. | Guy Zito | NPCC | Addressed as a question to industry in the second posting.
13 |  |  | The reference should be Policy 3D, Requirement 2.5 | Guy Zito | NPCC | References corrected.
13 |  | R4 | Exelon Corporation has commented on changing the dynamic interchange schedule requirements several times in the past (when the opportunity to comment was available). With that said we do not believe Version 0 is the time to make the obvious needed change (once the door is opened for this change you will not be able to shut the door on other changes), therefore we suggest this change be implement in Version 1. | John Blazekovich | Exelon | The question will be asked again in the second posting with two clear alternatives. No change is one choice.
13 |  | R5 | - The reference should be Policy 3D, Requirement 2.5. | Pete Henderson | IMO | Reference corrected.
13 |  |  | - This requirement includes the existing PSE responsibility for updating tags associated with dynamic schedules where they deviate by more than 25%. The drafting team is asking for acceptance of new criteria however a question is still raised whether for transactions >100MW the requirement is 10% or 25%. Which of this is required or appropriate. | Pete Henderson | IMO | The drafting team has refined the proposal and will ask the question again in the second posting.
13 |  | R4 | The Drafting Team proposed improvement is acceptable. I still have reservations with the fact that this standard could require me to re-tag a firm dynamic transaction in a window that would cause it to be treated as non-firm for curtailment purposes during TLR. In addition, large balancing authorities which do not have to tag internal transactions, and thus are not subject to this standard, may cause harm to smaller neighboring balancing authorities which are subject to this standard. | Phil Creech | Progress | Agreed. Question will be looked at again in second posting.
13 |  | R2 | Current Policy 3D 2.3 assigns the responsibility during loss of generation to the Source CA. The Reliability Standard assigns all responsibilities to the Sink BA. This is a change that should be thoroughly discussed. | Raj Rana | AEP | Loss of generation is addressed in the last sentence of R1.
13 |  | R3 | Releasing a tag limit imposed by a reliability event may not necessarily reload the tag. There may be other reliability events which prevent the reload. Also, why is the Reliability Authority not informed of this ReLoad? | Raj Rana | AEP | Releasing the tag limit is not intended to reload the tag - that requires PSE action.
13 |  | R1 | The Current Policy says that a tag may be modified for a reliability related issue. The Reliability Standard says that a new limit may be set. The Reliability Standard is wrong in assuming that the only modification would be by setting a new limit. | Raj Rana | AEP | Setting a new limit is not mean only the MW amount. There can be other limits.
13 |  | R1 | This tag modification section is said to apply to loss of generation, loss of load, or regional congestion management. Why isn't there an allowance for modifying tags due to a local congestion management issue as in Policy 3D 2.2.1? | Raj Rana | AEP | R1 lists as a reason to modify a transation: TLR or other regional congestion management procedure.
13 |  | 5 | It only includes BA having the authority to modify a tag for reliability reasons. This does not match Requirement 1 of Std 13 which says the RA, TSP, Source and Sink BA are allowed to make reliability modifications. The PSE can be removed since it would modify only market related changes which is covered under NAESB. | Roman Carter | Southern Company | Policy 3D requirement 2 allows multiple functions to initiate a request to curtail a transaction for reliability purposes.
13 |  | 1 | Should have the TO vs. TSP in the requirement. | Roman Carter | Southern Company | The drafting team believes the transmission service provider is responsible for the interface with the PSE in assessing and implementing transactions.
13 |  | 4 | The V-0 DT asked for comments on modifications to dynamic schedules. It is recommended that for transactions =<100 mw, deviations of 10mw or less should not require modifications to the tag. For transactions > 100 mw, modifications to a tag should only be required for deviations greater than 25%. | Roman Carter | Southern Company | The question will be asked again in the second posting with two clear alternatives. No change is one choice.
13 |  |  | 25% deviation threshold - we feel that the proposed change would be appropriate for version one, but not for this document. |  | WECC Interchange Subcommittee | The question will be asked again in the second posting with two clear alternatives. No change is one choice.
13 |  | R2 | Current Policy 3D 2.3 assigns the responsibility during loss of generation to the Source CA. The Reliability Standard assigns all responsibilities to the Sink BA. This is a change that should be thoroughly discussed. |  |  | Last sentence of R1 assigns this responsibility to the generator BA.
13 |  | R1 | It may be a good idea to clearly define some requirements on establishing a reliability limit. If it is not proper to allow denial of a tag cutail request then perhaps that should be spelled out in the requirements. Tag cutail requests currently qualify for passive approval even if late yet an entity could deny the request. The NERC Interchange Subcomittee addressed this issue in a letter submitted on 6/10/02 (continued in next field).(cont. from above) From NERC IS letter. Curtailment orders may be denied only for the following two reasons: 1. The order requests actions in the past (for example, an order to curtail a transaction five minutes ago). 2. The order for curtailment cannot be reliably implemented. In either case, the denying party should immediately issue its own curtailment order to effect the transaction curtailment. |  | SRP | Version 1 issue.
13 |  |  | R2 - As worded, the expectations of the term "implementing" are ambiguous since it is unclear if that term implies communication of the modified Interchange Transaction tag by the Sink Balancing Authority, if it refers to the inclusion of the modified tag into the BA's Interchange Schedules and ACE equation, or both. |  | Southern Company | Have added "communicating" for clarity.
13 |  |  | R4 - Strictly from a reliability point of view, we would support the 10% deviation option over the 25% option for all transactions that are greater than 100MWs. The goal is to increase the accuracy of your reliability tool(s), i.e. IDC. For a one hour 700 MW transaction, there is the choice of your reliability tool being off by 70MW (10%) or 175MWS (25%). The 10% would be continuous and seems to be the best compromise from not imposing undue burden on smaller schedules to chase "noise" while still requiring large schedules to be tracked more closely than they are today with the 25% required in Policy 3. Also, we propose the following language to be more specific: …."The Tag author or a Purchasing-Selling Entity responsible for tagging a DYNAMIC INTERCHANGE SCHEDULE shall modify the projected next hour schedule (not current hour schedule) when the last hour actual energy profile deviates from the projected next hour schedule as follows:…..." When the proposed language talks about 10%, 25%, or 10 MWs deviations, are we assuming a plus/minus deviation? |  | Southern Company | Addressed as a question to industry in the second posting.
13 |  |  | R5 - It only includes BA having the authority to modify a tag for reliability reasons. This does not match Requirement 1 of Std 13 which says the RA, TSP, Source and Sink BA are allowed to make reliability modifications. The PSE can be removed since it would modify only market related changes which is covered under NAESB. |  | Southern Company | All of these other functions may request the tag be modified for reliability reasons per R1. R2 states that the BA must communicate and implement the change. R5 simply allows a PSE or BA to restore a transaction or otherwise modify it for other than reliability reasons.
13 |  | R3 | Releasing a tag limit imposed by a reliability event may not necessarily reload the tag. There may be other reliability events which prevent the reload. Also, why is the Reliability Authority not informed of this ReLoad? |  |  | Releasing the tag limit is not intended to reload the tag - that requires PSE action.
13 |  | R1 | The Current Policy says that a tag may be modified for a reliability related issue. The Reliability Standard says that a new limit may be set. The Reliability Standard is wrong in assuming that the only modification would be by setting a new limit. |  |  | Setting a new limit is not mean only the MW amount. There can be other limits.
13 |  | Drafting Team Comments - R4 | The Drafting Team asked commenters if they agree with the modified structure of requirement R4. We believe it is important that no changes are made to existing policy with the translation to Version 0. Any modified format should be considered in Version 1, but we do not agree with the format provided. The minimum requirement to change a tag should be at least 25 MW in both cases ( above and below 100 MW). If the Drafting Team wants better resolution of Dynamic Interchange Schedules, then tagging requirements for changes could be eliminated if the actual dynamic value was provided to the RA then the RA would place the value into the IDC and there is no doubt about dynamic Interchange Schedule actual value. |  | FRCC | The question will be asked again in the second posting with two clear alternatives. No change is one choice.
13 |  | R4 | The proposed dynamic interchange schedule language (included in Draft 0 comments column) should be adopted. |  | SRP | Agreed. Question will be looked at again in second posting.
13 |  | R1 | This tag modification section is said to apply to loss of generation, loss of load, or regional congestion management. Why isn't there an allowance for modifying tags due to a local congestion management issue as in Policy 3D 2.2.1? |  |  | R1 lists TLR and regional congestion management procedure as reasons for curtailment.
14 |  | R4 | In the Functional Model load forecasts are developed by the Load Serving Entity and provided to the Balancing Authority. The BA sends the agregated information to the RA. The TOP is not involved in this process. Please change the requirement to match the functional model. | Alan Boesch | NPPD | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue. The Version 0 effort is focused on a good translation of existing rules, consistent with the functional model; not a 100% implementation of the functional model.
14 |  | R7 | In the functonal model the TOP does not monitor frequency. As discussed in Policy 9 frequency is a system wide parameter that is monitored by the RC (RA). The BA provides frequency response through the frequency bias setting. Please assign the responsibility for monitoring system frequency to the RA. | Alan Boesch | NPPD | This standard addresses the responsibili.ties of the TOP and BA. Obligations of the RC have been translated into standards 033-040. The TOP would need to monitor frequency as an indicator of a reliable system, particularly during large disturbances, islanding, restoration, etc.
14 |  | R6 | The functional model says the Transmission Operator (not the Balancing Authority) is responsible for telemeter values. Please revise. | Alan Boesch | NPPD | The drafting team interprets Control Area in Policy 4A 5.1 to include balancing area and transmission provider. The standard says the BA shall "use" sufficient metering. It does not require the BA to own or maintain that metering.
14 |  | R1 | This requirement as written in Policy 4 is all about providing system operators real-time information on the status of the commponents of the transmission system. It is not about reporting the information on status to each other and the RA. Those requirements are in different policies. Please change this requirement to reflect the intent of policy 4. | Alan Boesch | NPPD | This is a translation of the obligations of Policy 4A Requirement 1 from passive voice to active voice.
14 |  | R1 | As written believe that the proposed requirement extends current policy. Prefer taking the approach that the standard applies only to the BAs and TOPs and that GOP and other functions are obligated through service agreements or interconnection requirements. | Alan Johnson | Mirant | The drafting team is proposing revisions to incorporate a clearer model of the relationships between functions. Generator operators are currently obligated to provide real-time information affecting reliability.
14 |  | R3 | Change “to operating personnel” to “to its operating personnel.” | Brandian | ISO-NE | Added "their"
14 |  | R4 | Load forecasting is the starting point for planning capacity for obligations and thus, deemed to be required for reliability. | Eric Grant | Progress | Requirement implies load forecasting is needed. Version 1 can make the requirement more explicit.
14 |  | R4 | Load forecasting is the starting point for planning capacity for obligations and thus, deemed to be required for reliability. | Eric Grant | Progress Florida | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue.
14 |  | R1 | BALANCING AUTHORITIES shall inform the RELIABILITY AUTHORITY and other affected BALANCING AUTHORITIES and TRANSMISSION OPERATORS of all generation and transmission resources available for use. | Gerald Reahlt | Manitoba | The drafting team is proposing revisions to incorporate a clearer model of the relationships between functions. Generator operators are currently obligated to provide real-time information affecting reliability.
14 |  | R4 | Is load forecasting required for reliability or not, if not, why is this information required? | Gerald Reahlt | Manitoba | The requirement is in current policy.
14 |  |  | Load forecasting is required for reliability as there is a need to predict possible shortages due to high loads. | Gerald Reahlt | Manitoba | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue.
14 |  |  | There is no reference to this in Policy 4 | Gerald Reahlt | Manitoba
14 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. | Guy Zito | NPCC | Compliance measures and compliance monitoring will be provided only as available in an existing compliance template. All other additions are for Version 1.
14 |  | R3 | Change “to operating personnel” to “to its operating personnel.” | Guy Zito | NPCC | Added "their"
14 |  | R3 | Based on requirement listed in R3 Exelon Corporation suggests that Transmission Owner be added to the "applicable" list and be included in the R3 statement. | John Blazekovich | Exelon | This is a requirement to provide relay information to operating personnel. The RA, BA, and TOP should each be responsible for providing this information to their operating personnel. This requirement does not address how the relay information is obtained.
14 |  |  | Functional Model does not assume BA has transmission information, thus R4 should place analysis requirements on RA not BA | Mike Kormos | PJM | The drafting team interprets policy 4A4 as including the need for a BA to have forecast information to meeting balancing objectives.
14 |  | R4 | RA vs. BA | Mike Kormos | PJM | See prior response on this issue.
14 |  | R3 | Change “to operating personnel” to “to its operating personnel.” | Pete Henderson | IMO | Added "their"
14 |  | R4 | Load forecasting is the starting point for planning capacity for obligations and thus, deemed to be required for reliability. | Phil Creech | Progress | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue.
14 |  | R4 | In answer to the question under “Comments”, load forecasting is required for reliability. For example, with forecast load information, potential overloaded facilities can be identified given expected transmission configuration when evaluating future grid operating requirements. | Travis Bessier | TXU | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue.
14 |  | R7 | It is not necessary to require Transmission Operator to monitor frequency if the Reliability Authority is responsible for directing emergency actions. | Travis Bessier | TXU | Disagree - under islanding or certain emergency conditions the TOP may be required to monitor frequency.
14 |  |  | Functional Model does not assume BA has transmission information, thus R4 should place analysis requirements on RA not BA |  | PSE&G | The drafting team interprets policy 4A4 as including the need for a BA to have forecast information to meeting balancing objectives.
14 |  | Applicability | In the comments for R1, the Drafting Team asked the industry to consider the following approach: “ … to have the standard apply only to BAs and TOs and assume that Generator Operator and other functions are obligated through service agreements or connection requirements …” We agree with this approach and the applicable entities be modified to reflect this proposed change. |  | FRCC | The majority of respondents to Question 6 supported being more expansive in the identification of functions, as needed to complete a good translation of the intent and scope of existing policies. The drafting team is proposing this approach in the second posting: include all functions needed to implement today's rules and don't include any functions unnecessary to meeting a reliability requirement.
14 |  | R1 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Policy markups corrected.
14 |  | R4 | Load Forecasts are essential for reliable system operations and form the foundation for operational planning. |  | PG&E | Since there is no specific load-forecasting requirement in policy, the drafting team believes this should be a Version 1 issue.
14 |  | R4 | RA vs. BA |  | PSE&G | See prior response on this issue.
14 |  | Drafting Team Comments - Standard | Since this standard is one with potential redundancy with other standards, the Drafting Team asked to what extent should the redundancies be eliminated in Version 0. It is important that no changes are made to existing policy with the translation to Version 0.The removal of redundancy should be considered in Version 1. |  | FRCC | Agreed - the second draft retains these requirements.
14 |  | Drafting Team Comments - R4 | The Drafting Team asked the following: Is load forecasting required for reliability or not, if not, why is this information required? We believe that load forecasting is required to determine SOLs or IROLs. If load is known, the Operations Planning process will identify actions required to eliminate or mitigate potential reliability issues. |  | FRCC | Version 1 issue.
14 |  | R1 | The following was not included in exiting policy and should be removed from the Version 0 translation: …and other affected Balancing Authorities and Transmission Operators… |  | FRCC | This shows the hierarchy intended in the functional model as the DT interprets existing policy.
14 |  | R1 | This requirement should be revised to reflect the applicability of the standard to BAs and TOs. |  | FRCC | The drafting team is proposing revisions to incorporate a clearer model of the relationships between functions. Generator operators are currently obligated to provide real-time information affecting reliability.
15 |  | Measurement | Because requirement 5 the measurement revised to read "Evidence that the RELIABILITY AUTHORITY, BALANCING AUTHORITY, TRANSMISSION OPERATOR, and PURCHASING-SELLING ENTITY is providing the information required, within the time intervals specified therein, and in a format agreed upon by the requesting entities.” | Alan Boesch | NPPD | Comment needs further clarification.
15 |  | Applicability | Add Generator Owners and Load Serving Entities. Extend R5 to include these Functional Model entities. | Brandian | ISO-NE | This would be a change from current policy - address in Version 1.
15 |  | R5 | We agree that this is a correct translation of existing NERC policy. However, we are concerned that, as written, it requires the PSE to provide ANY information that a BA or TSP may request " in the name of reliable operations". Given the issues involved, we feel that the issue of scope of information required should be addressed later in a Version 1 type of revision to this standard. | Deanna Phillips | BPA | Agreed.
15 |  | R1 | Current policy is for data to be updated every 10 minutes, and is in Standard 15. This rate is too slow and should be increased (every 4-10 seconds) when possible. This should be addressed in Version 1. | Ed Riley | CAISO | version 1 issue.
15 |  | R4 | BALANCING AUTHORITIES and TRANSMISSION OPERATORS and shall provide the types of data as listed in Addendum A, unless otherwise agreed to by the BALANCING AUTHORITIES and TRANSMISSION OPERATORS with immediate responsibility for operational security. | Gerald Reahlt | Manitoba | Corrected.
15 |  |  | Is Operating Data the same as Electric Security Data? | Gerald Reahlt | Manitoba | Yes.
15 |  |  | Should it be Addendum or Appendix? | Gerald Reahlt | Manitoba | Corrected.
15 |  | R3 | Upon request, RELIABILITY AUTHORITIES shall, via the ISN, exchange with each other operating data that is necessary to allow the RELIABILITY AUTHORITIES to perform their operational reliability assessments and coordinate their reliable operations. RELIABILITY AUTHORITIES shall share with each other the types of data as listed in Attachment 1, unless otherwise agreed to. | Gerald Reahlt | Manitoba
15 |  | Applicability | Add Generator Owners and Load Serving Entities. Extend R5 to include these Functional Model entities. | Guy Zito | NPCC | This would be a change from current policy - address in Version 1.
15 |  | Applicability | Add Generator Owners and Load Serving Entities. Extend R5 to include these Functional Model entities. | Pete Henderson | IMO | This would be a change from current policy - address in Version 1.
15 |  | R4 | There is no Addendum A. The last sentence should read Attachment 1. | Raj Rana | AEP | Changed to "attachment 1".
15 |  | R1 and R3 | These two requirements refer to Appendix 4B (also refered to as Appedix A in the revised document). These items should be listed in the requirements rather than cause the reader to refer to an appendix. | Ray Morella | FirstEnergy | The drafting team has decided that large tables should be appended to the standard rather then severely alter the format of the standard.
15 |  |  | In Attachment 1, the generator data should include status of voltage control and power system stabilizer facilities. | Robert Snow |  | Version 1 issue.
15 |  | R2 | TXU Electric Delivery agrees that Electric System Security Data should not be made available to Purchasing/Selling entities in the wholesale merchant function. | Travis Bessier | TXU | R2 addresses this concern.
15 |  | R4 | Typographical error: The second "and" in the last sentence of this requirement is not necessary. | Travis Bessier | TXU | Corrected.
15 |  | Compliance Monitoring Process | "Entities" are specified in P4T2 |  | SRP | Made consistent with template.
15 |  | R1 | Existing Document References should include Compliance Template P4T2 |  | FRCC | Corrections made.
15 |  | Measures | I couldn't find a source/reference for this. |  | SRP | Reference corrected.
15 |  | R2 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Signing the ISN agreement obligates the parties to treat the information confidentially.
15 |  |  | Std 15 (34) , R3 (R3) - The requirement indicates that the operational data be exchanged "via the ISN". Better wording would be "via the ISN or other prevailing NERC sponsored exchange mechanism for a required type of operational data". This allows use of the SDX, Tagging, etc. that otherwise would be disallowed (or it would require redundant exchange of the same data via the ISN) in order to comply with R3. Policy 4B and the Appendix were written before SDX, Tagging, and RCIS when the ISN was expected to be the mechanism for the exchange of the data identified in the Standard 15 Appendix. Since NERC had developed alternative solutions to this, those solutions should be permitted in the Version 0. |  | Southern Company | Changed to "or equivalent".
15 |  | Levels of Non Compliance | The applicable entity is the Reliability Authority not the Reliability Coordinator. |  | FRCC | Corrected.
15 |  | Compliance Monitoring Process | The existing Compliance template uses the terminology “Monitoring Process” not “Exception Reporting”. |  | FRCC | Made consistent with template.
15 |  | R4 | There is no Addendum A. The last sentence should read Attachment 1. |  |  | Corrected.
16 |  | R1 | This requirement should be split and become two requirements one for the TOP and one for the BA to make it clear who is responsible for providing transmission and generation outage information to the RA. | Alan Boesch | NPPD | Requirement was split as suggested.
16 |  | CMP | Third paragraph - The RA should "direct" the cancellation of an outage, not "request". | Anita Lee | AESO | Version 1 issue.
16 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. | Brandian | ISO-NE | Will review compliance template information to ensure all appropriate information is captured.
16 |  | R1 | These requirements should be left to policy 9 in version 0 | Eric Grant | Progress | This requirement is intended to capture the reliability information reporting requirements of policy 4b that were until now applied to control areas.
16 |  | R1 | These requirements should be left to policy 9 in version 0 | Eric Grant | Progress Florida | This requirement is intended to capture the reliability information reporting requirements of policy 4b that were until now applied to control areas.
16 |  |  | “Operating Authorities” or should their obligations be addressed through service agreements? | Gerald Reahlt | Manitoba | See prior response on this issue.
16 |  |  | Agree with comment. | Gerald Reahlt | Manitoba
16 |  |  | At the discretion of the RRC RRO or NERC, an investigation may be initiated to review the planned outage process of monitored entity due to a complaint of non-compliance by another entity. Notification of an investigation must be made by the RRC RRO to the entity being investigated as soon as possible, but no later than 60 days after the event. The form and manner of the investigation will be set by NERC and/or the RRC RRO. | Gerald Reahlt | Manitoba | Corrected.
16 |  | R1 | Drafting Team assumes the time requirement is based on noon prevailing time of the RELIABILITY AUTHORITY, although it is not clear from Policy 4. Policy 9 states specific times for the Eastern and | Gerald Reahlt | Manitoba | The drafting team is interpreting what was meant and practiced.
16 |  |  | I believe Generator Operators obligations should be addressed through service agreements with the TO and or BA. | Gerald Reahlt | Manitoba | Drafting team will include generator operators only as necessary to interpret existing rules. The majority of respondents preferred this approach.
16 |  | Measures | Monitored entity shall report and coordinate scheduled generator and/or bulk transmission outages to its RELIABILITY AUTHORITY and others indicated in the requirements above. | Gerald Reahlt | Manitoba
16 |  |  | Monitored entity: The translation to standards is supposed to specifically identify entities. | Gerald Reahlt | Manitoba | Functions are identified in the requirements.
16 |  |  | The Regional Reliability Councils shall conduct a review every three years to ensure that each Operating Authority has a process in place to provide planned generator and/or bulk transmission outage information to their Reliability Coordinator Authority, and with neighboring Control Areas Transmission Operators and Balancing Authorities. | Gerald Reahlt | Manitoba | Corrected.
16 |  |  | The translation to standards is suppose to specifically identify entities. | Gerald Reahlt | Manitoba | Functions are identified in the requirements.
16 |  | Applicability | This standard provides another example of the question whether Generator Operators are intended to be part of | Gerald Reahlt | Manitoba | See prior response on this issue.
16 |  |  | Western Interconnections. The Drafting Team recommends using the Policy 9 time requirements. | Gerald Reahlt | Manitoba
16 |  |  | Operating and interconnection agreements can often fall into dispute over a number associated issues (e.g. re-imbursement, interpretation). Including the requirement in the Version 0 adds "regulatory requirement" that provide a better chance of ensuring compliance (leave the requirements for generation owners/operator in the Standard). | John Blazekovich | Exelon | Agreed.
16 |  |  | A Measure could be to "have evidence that outages were reported." | Mike Kormos | PJM | Corrected.
16 |  | M1 | The MEASUREMENT seems to be a Requirement. | Mike Kormos | PJM | Already stated as a requirement in R1.
16 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. | Pete Henderson | IMO | Will review compliance template information to ensure all appropriate information is captured.
16 |  | R2 | The language "may affect the reliability of Interconnected operations" needs to be added back into this standard. | Peter Burke | ATC | Unclear where this reference is.
16 |  | R1 | These requirements should be left to policy 9 in version 0 | Phil Creech | Progress | This requirement is intended to capture the reliability information reporting requirements of policy 4b that were until now applied to control areas.
16 |  |  | Outage information is needed by neighboring reliability authorities much sooner than one day pror to the outage. | Robert Snow |  | Version 1 issue.
16 |  | 1 | The requirement states the GO and TO provide outage information daily to their RA. Standard 14, Req. 1 says the GO informs the host BA and TO of all generation resources available for use. It seems these two should agree to make channels of communication clear. | Roman Carter | Southern Company | DT will modify Standard 16 to be consistent.
16 |  |  | A Measure could be to "have evidence that outages were reported." |  | PSE&G | Corrected.
16 |  |  | In addition, there was an incorrect translation from Compliance Template P4T4. R1 should be revised as follows: … that may collectively cause or contribute to an SOL or IROL violation or a regional operating area limitation, to their Reliability Authority, AND to neighboring Balancing Authorities and Transmission Operators… |  | FRCC | Corrected.
16 |  | Applicability | In reference to the comment about including generator operators in the requirements, we have found it helpful to be able to point to NERC requirments when developing service agreements so would prefer that they be included. See response to Question 6. |  | PG&E | Agreed.
16 |  | R2 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Policy markups corrected.
16 |  | Measures | Language in Draft and P4T4 don't match |  | SRP | Reviewed for consistency with template.
16 |  | Levels of Non Compliance | Level 4 language in Draft doesn't match P4T4. |  | SRP | Drafting team believes the language is the same.
16 |  | Applicability | Refer to the approach presented in Standard 014 - “… to have the standard apply only to BAs and TOs and assume that Generator Operator and other functions are obligated through service agreements or connection requirements …” With this approach, the applicable entities should be modified. |  | FRCC | See prior response on this issue.
16 |  | M1 | The MEASUREMENT seems to be a Requirement. |  | PSE&G | Already stated as a requirement in R1.
16 |  | R1 | This requirement should be revised to reflect the applicability of the standard to BAs and TOs. |  | FRCC | Revised to address functional relationships.
17 |  | R1, R3, R4, R5 and R6 | Balancing Authorities do not have any responsibilities for protection systems. Please remove them from the requirements. | Alan Boesch | NPPD | The drafting team agrees this is a close call. However, this standard does not entail relay coordination from a technical sense. It involves sharing relay information to understand reliability impacts, such as availability of facilities. From that perspective the drafting team has included the BA.
17 |  | R3 and R4 | In the fuctional model the Planning authority is responsible for coordinating system prtection systems. Please change the requirement accordingly. | Alan Boesch | NPPD | This standard does not address relay coordination. It addresses sharing of information that may affect reliable system operation. This is a translation of what was already defined in Operating Policy 4D.
17 |  | R2 | The proposed language is more proscriptive than the current language. There should be a chain of communication such that the GOP notifies his BA and the BA notifies the TOP and RA. | Alan Johnson | Mirant | The drafting team is proposing revisions to incorporate a clearer model of the relationships between functions. Generator operators are currently obligated to provide real-time information affecting reliability.
017 |  |  | Policy 4D Requirement 5.1 does not exist. R6 is covered by Policy 4D Requirement 6. | Brandian | ISO-NE | References corrected.
17 |  | R5 | We agree drafting team's position that the Generation Operator should report through either the Transmission Provider or the BA, as appropriate. | Deanna Phillips | BPA | Agreed.
17 |  | R5 | Additional work is required to clarify the reporting hierarchy. The Drafting Team does not believe the Generator Operator would report directly to the Reliability Authority, but would report through the Transmission Operator or Balancing Authority. This hierarchy question affects a number of requirements in several standards. | Gerald Reahlt | Manitoba | The drafting team is proposing revisions to incorporate a clearer model of the relationships between functions. Generator operators are currently obligated to provide real-time information affecting reliability.
17 |  |  | Agree with comment. | Gerald Reahlt | Manitoba
17 |  |  | Policy 4D Requirement 5.1 does not exist. R6 is covered by Policy 4D Requirement 6. | Guy Zito | NPCC | References corrected.
17 |  | R3 | Exelon Corporation suggests that Transmission Owners be included in the applicability of R3, R4 and R5. The Transmission Owners (in many cases) will be the entity that owns/installs/coordinate new protection systems. | John Blazekovich | Exelon | Since these requirements address sharing of reliability information, not the design, installation, testing, and maintenance of protection systems, the drafting team believes the transmission owners are not obligated by these requirements.
17 |  |  | Policy 4D Requirement 5.1 does not exist. R6 is covered by Policy 4D Requirement 6. | Pete Henderson | IMO | Reference corrected.
17 |  | R5 | Allegheny agrees with the Drafting Team that the Generator Operator should report through the Transmission Operator or Balancing Authority. | William Smith | Allegheny | Agreed.
17 |  | R5 | Generator Operator should not directly report to the RA. The GO should report through the TO or BA. |  | PEPCO | Agreed.
17 |  | R4 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Policy markups corrected.
17 |  | Applicability | Refer to the approach presented in Standard 014 - “… to have the standard apply only to BAs and TOs and assume that Generator Operator and other functions are obligated through service agreements or connection requirements …” With this approach, the applicable entities should be modified. |  | FRCC | See prior response on this issue.
17 |  | R1-R5 | These requirements should be revised to reflect the applicability of the standard to BAs and TOs. |  | FRCC | The drafting team believes the requirements apply to other functions as well.
17 |  | Applicability | This standard is not generally applicable to the Balancing Authority. Protection coordination is primariliy a Transmission Operator and Generation Operator function. The Balancing Authority should only be required to respond to situations requiring resource adjustments. |  | PG&E | The drafting team agrees this is a close call. However, this standard does not entail relay coordination from a technical sense. It involves sharing relay information to understand reliability impacts, such as availability of facilities. From that perspective the drafting team has included the BA.
18 |  | R2 | The Functional Model says the Balancing Authority “Implements emergency procedures as directed by the Reliability Authority”. Please change to requirement or revise the functional model. | Alan Boesch | NPPD | Version 1 issue.
18 |  | R3 | The Functional Model says the Reliability Authority issues corrective actions to Transmission Operators, Transmission Service Providers, Balancing Authorities, and Interchange Authorities. The Balancing Authority directs generators to implement redispatch. The Reliability Authority does not communicate directly with Generators for real-time operations including emergencies. Please revise. | Alan Boesch | NPPD | There is a hierarchy of authority defined in the functional model and the drafting team will attempt to clarify that in the second posting.
18 |  | R3 | Only the RA should be issuing reliability directives. | Anita Lee | AESO | There is a hierarchy of authority defined in the functional model and the drafting team will attempt to clarify that in the second posting.
18 |  |  | - Second point is covered by Policy 5A Requirement 6.1 and not Requirement 6.2. | Brandian | ISO-NE | Reference corrected.
18 |  |  | - Third point missing reference to Policy 5A Requirement 6.2. | Brandian | ISO-NE | Reference corrected.
18 |  |  | In 2nd paragraph, Policy 5A Requirement 2.2.1 does not exist. R3 is covered by Policy 5A Requirement 2.2. | Brandian | ISO-NE | References corrected.
18 |  |  | In 2nd paragraph, Policy 5A Requirement 5.1 does not exist. R5 is covered by Policy 5A Requirement 5. | Brandian | ISO-NE | Reference corrected.
18 |  |  | The DISTRIBUTION PROVIDER and LOAD SERVING ENTITY shall assist the requesting entity BA or TO, unless such actions would violate safety, equipment, regulatory or statutory requirements. | Gerald Reahlt | Manitoba | corrected.
18 |  |  | The policy states the operating authority shall inform other potentially affected operating authorities and it’s RC. The new standard makes it sound like any one of the RA, BA or TO can inform affected RA’s. The BA and TO should notify other TO’s and BA’s but should notify their own RA who in turn should notify other RA’s. | Gerald Reahlt | Manitoba | See prior response on this issue.
18 |  | R5 | The RELIABILITY AUTHORITY, BALANCING AUTHORITY, and TRANSMISSION OPERATOR shall render all available emergency assistance requested, provided that the requesting entity RA, BA or TO has implemented its comparable emergency procedures, unless such actions would violate safety, equipment, or regulatory or statutory requirements. | Gerald Reahlt | Manitoba | Emergency assistance is not limited to being requested by an RA.
18 |  |  | The translation to standards is supposed to specifically identify entities. | Gerald Reahlt | Manitoba | The drafting team has identified specific functions for each requirement.
18 |  |  | To facilitate emergency assistance, the OPERATING AUTHORITY shall inform other potentially affected OPERATING AUTHORITIES and its RELIABILITY COORDINATOR of real time or anticipated emergency conditions, and take actions to avoid when possible, or mitigate the emergency. | Gerald Reahlt | Manitoba
18 |  |  | - Second point is covered by Policy 5A Requirement 6.1 and not Requirement 6.2. | Guy Zito | NPCC | Reference corrected.
18 |  |  | - Third point missing reference to Policy 5A Requirement 6.2. | Guy Zito | NPCC | Reference corrected.
18 |  | #VALUE! | In 2nd paragraph, Policy 5A Requirement 2.2.1 does not exist. R3 is covered by Policy 5A Requirement 2.2. | Guy Zito | NPCC | Reference corrected.
18 |  |  | In 2nd paragraph, Policy 5A Requirement 2.2.1 does not exist. R3 is covered by Policy 5A Requirement 2.2. | Guy Zito | NPCC | Reference corrected.
18 |  |  | In 2nd paragraph, Policy 5A Requirement 5.1 does not exist. R5 is covered by Policy 5A Requirement 5. | Guy Zito | NPCC | Reference corrected.
18 |  |  | Operating/Service and Interconnection agreements can often fall into dispute over a number associated issues (e.g. re-imbursement, interpretation). Including the requirement in the Version 0 adds "regulatory requirement" that provide a better chance of ensuring compliance (leave the applicability requirements in the Standard). | John Blazekovich | Exelon | Agreed.
18 |  |  | Reference to Policy 5B Requirement 2 is missing. | Pete Henderson | IMO | References corrected.
18 |  |  | Reference to Policy 5B Requirement 2.2 is missing. | Pete Henderson | IMO | References corrected.
18 |  | R3 | Agree with translation of Operating Authority including the Generator Operator, and stating that "Generator Operator shall comply with Transmission Operator reliability directives." | Raj Rana | AEP | Agreed.
18 |  |  | Omitted Policy 5A - R3, R7, R8, R9, R10 and R12 from this standard. | Raj Rana | AEP | These requirements are included in other standards. Need to make sure they address the Policy 5 requirements (e.g. add IROL/SOL) and make links are marked in Policy 5 markup.
18 |  | R3 | Item 2.2.1 should be added to standard 008 R10. | Ray Morella | FirstEnergy | Unclear where this reference is.
18 |  |  | Page P5-2 item 3 refers to a time limit of 30 minutes, this is adequate for IROL and SOL but should reflect 15 minutes for DCS issues. | Ray Morella | FirstEnergy | It is not clear what item is being referenced.
18 |  | 3 | Market Operator should be included in the list of entities that shall comply with the RA directives. This also means that the MO would have to be added as an entity that would be included under the Operating Authority category. | Roman Carter | Southern Company | The drafting team does not believe current operating policies are addressed to market operators. All requirements can be assigned to the functions indicated, such as TOP, BA, RA, GOP, etc.
18 |  | General | Policy 5A 1. was not included in the V-0 Standard. It states " The RA and TO shall operate within the IROLs and SOLs". Appears it was overlooked. | Roman Carter | Southern Company | Will review and correct this omission.
18 |  | 1 | This req. states "The RA, BA, and TO shall have the responsibility…". The original language in Policy 5 for this requirement uses Operating Authority and this includes entities such as the GO, TO, and BA but not the Reliability Coordinator. Throughout this V-0 Standard the RA is subsituted for the RC even within this requirement. Since the original policy says RCs are excluded, this poses a conflict for this requirement. This is also in Req's 2,4,5. | Roman Carter | Southern Company | The drafting team agrees there is some potential redundancy here but would prefer to sort out those redundancies in a more deliberate pace in Version 1 to avoid leaving out essential requirements. There would be some consolidation and reorganizing of standards in Version 1 also.
18 |  |  | Why doesn't the Generator Operator have to follow the directives of the Balancing Authority? It seems more appropriate to have the GO accountable to the TO and BA rather than taking direction from the RA | Terry Bilke | MISO | In general that is true. There are some ocassions that require an RA to direct actions such as shifting generation or shedding load and that authority is meant to be addressed here.
18 |  |  | Policy 5.A.3 that addressed unknown operating states has been incorrectly omitted from the Version 0 Standards. TXU Electric Delivery suggests including that Policy in the Version 0 Standards to achieve a correct translation. | Travis Bessier | TXU | This requirement will be added back in to Version 0.
18 |  | Title | (Emergency) Reliability Responsibilities and Authorities Should be modified to include the Emergency Operations. For example : Emergency Reliability Responsibilities and Authorities. As written, you have to read the body of the standard to understand that it applies to emergency operations only. Note that these standards will not be associated with Policy 5 – Emergency Operations in the future and should have stand alone descriptive titles. |  | Southern Company | Corrected.
18 |  | Applicability | Agree with the approach presented in this standard and Standard 014 - “… to have the standard apply only to BAs and TOs and assume that Generator Operator and other functions are obligated through service agreements or connection requirements …” With this approach, the applicable entities should be modified. |  | FRCC | The majority of respondents to Question 6 supported being more expansive in the identification of functions, as needed to complete a good translation of the intent and scope of existing policies. The drafting team is proposing this approach in the second posting: include all functions needed to implement today's rules and don't include any functions unnecessary to meeting a reliability requirement.
18 |  | R3 | Agree with translation of Operating Authority including the Generator Operator, and stating that "Generator Operator shall comply with Transmission Operator reliability directives." |  |  | Agreed.
18 |  | R3 | Consider adding Market Operator to the list of Operating Authorities. Specifically, it should be included in R3 as being required to comply with all reliability directives and, perhaps, in R5 as being required to provide emergency assistance as requested. |  | Southern Company | The drafting team does not believe current operating policies are addressed to market operators. All requirements can be assigned to the functions indicated, such as TOP, BA, RA, GOP, etc.
18 |  | General Comments – Missing requirements from existing policy | It appears that in the translation from the existing policy to Version 0, Policy 5A 1, 3, 7, 8, 9, and 10 were not included and although redundant should be added to this standard as additional requirements. |  | FRCC | Will review and correct this omission.
18 |  | General | It would be useful to include an explicit explanation of why Policy 5A Requirement 1 was not included in Standard 018. We assume it is because it is redundant with Standard 008, but, as a general rule, any time a redundant section of policy is not included as a standard an explanation of why should be included in the comment section (business practice reference, reference document number or an explanation of why it is not applicable). |  | Southern Company | Will review and correct this omission.
18 |  |  | Modify title to include the word Emergency as noted in Std. 018 above. |  | Southern Company | Corrected.
18 |  |  | Omitted Policy 5A - R3, R7, R8, R9, R10 and R12 from this standard. |  |  | Reviewed to incorporate missing requirements.
18 |  | R4 and R6 | Should specify that the local RA will handle all communications with other potentially impacted Reliability Coordinators. As written (Reliability Authority or … ), these requirements could lead to multiple notifications and potential confusion as to exactly what action is going to happen or has taken place. In general, all communications with adjacent Reliability Authorities should be through the local Reliability Coordinator. (Note that R4 may intend that RA contact other RAs, etc., but this is not clear and could easily be misinterpreted.) |  | Southern Company | Version 1 issue.
18 |  | R3 and R6 | These requirements should be revised to reflect the applicability of the standard to BAs and TOs. |  | FRCC | The drafting team believes there are reliability obligations in current policy on the other functions identified.
18 |  | All | This section could be be simplified to eliminate some of the redundant wording. The concepts and responsibilities are OK. |  | PG&E | Will review for that purpose.
18 |  | R3 | With the Service Agreement approach, the second paragraph in requirement should be removed and incorporated as part of the agreement. |  | FRCC | The drafting team is not proposing a service agreement approach.
18 |  | R5 | With the Service Agreement approach, the second paragraph in requirement should be removed and incorporated as part of the agreement. In addition, this paragraph was not included in the existing policy used for the Version 0 translation and should be removed. |  | FRCC | See prior response on this issue.
19 |  | R4 | Even though this is a direct translation of the existing Policy, NPCC requests a clarification of the repeat back requirements, specifically are they for emergency, abnormal, normal, all of the above, provide specific examples | Brandian | ISO-NE | Version 1 issue.
19 |  | R1 | We feel that if the Generation Operator is obligated to respond to real time requests from a BA or TP, etc. to modify their operations (i.e. congestion Management, IOS Services, etc), then they must have the necessary voice and data communications links. Otherwise, it may not be necessary for the Generation Operator to have this type of comminications available. | Deanna Phillips | BPA | Agreed.
19 |  | R1 | In general, with the large amount of merchant generators, how can we ensure they will register as generator operators and thus comply with these standards? | Eric Grant | Progress | Generators will still be obligated to follow NERC rules, as they are today. Eventually it is expected that registration and compliance program will cover all functions in standards.
19 |  | R1 | In general, with the large amount of merchant generators, how can we ensure they will register as generator operators and thus comply with these standards? | Eric Grant | Progress Florida | Generators will still be obligated to follow NERC rules, as they are today. Eventually it is expected that registration and compliance program will cover all functions in standards.
19 |  | R1 | The BALANCING AUTHORITY, TRANSMISSION OPERATOR, and GENERATOR OPERATOR shall have communications (voice and data links) with appropriate RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS. Such communications shall be staffed and available for addressing a realtime emergency condition. | Gerald Reahlt | Manitoba
19 |  |  | The meaning is changed with this statement. It’s not the communications that shall be staffed, it’s the Operating authority (RA, BA or TO) which shall be staffed to address the real time emergency condition. | Gerald Reahlt | Manitoba | The drafting team believes the staffing of communications facilities is a correct interpretation of Policy 5B1.
19 |  |  | The OPERATING AUTHORITY shall have communications (voice and data links) to appropriate entities within its OPERATING AUTHORITY AREA, which are staffed and available to act in addressing a real time emergency condition. | Gerald Reahlt | Manitoba
19 |  | R4 | Even though this is a direct translation of the existing Policy, NPCC requests a clarification of the repeat back requirements, specifically are they for emergency, abnormal, normal, all of the above, provide specific examples | Guy Zito | NPCC | Version 1 issue.
19 |  |  | Reference to Policy 5B Requirement 1 is missing. | Guy Zito | NPCC | References corrected.
19 |  | R1 | Exelon Corporation believes that a minimum standard of communication equipment must be in place between a balancing authority and generator operators that will be responding to dispatch signals (from the BA). We feel that "appropriate" properly captures that requirement. | John Blazekovich | Exelon | Agreed.
19 |  | R1 | Change generator voice communications requirement with RA to "voice OR data" instead of "voice AND data" | Mike Kormos | PJM | Changing to not require generator communications with RA. Generator must communicate with BA and TOP. The drafting team believes both voice and data would be required.
19 |  |  | In Market environment voice communication with generators is not necessarily required | Mike Kormos | PJM | Version 1 issue.
19 |  | R1 | In general, with the large amount of merchant generators, how can we ensure they will register as generator operators and thus comply with these standards? | Phil Creech | Progress | Generators will still be obligated to follow NERC rules, as they are today. Eventually it is expected that registration and compliance program will cover all functions in standards.
19 |  | R2 | Omitted conditions that require notification. | Raj Rana | AEP | Corrected omission.
19 |  | R2 | All groups active in the industry should be required to report sabotage incidents and security breaches. | Ray Morella | FirstEnergy | Version 1 issue.
19 |  | 1 | R equirement states the GO shall have communications (voice and data links) to the RA. Does this mean the GO will be required to have Communication equipment? | Roman Carter | Southern Company | GOP is not required to communicate directly with the RA - that will be clarified in the second posting. However, GOP is required to communicate with the BA and TOP and will therefore be required to have some communications equipment for reliability purposes.
19 |  | R2 | Balancing Authority and Transmission Operator should only have to notify the Reliability Authority. That Reliability Authority would then provide other notification as needed. | Travis Bessier | TXU | Within an RA, TOP or BA may need to notify neighboring systems.
19 |  | R1 | Change generator voice communications requirement with RA to "voice OR data" instead of "voice AND data" |  | PSE&G | Changing to not require generator communications with RA. Generator must communicate with BA and TOP. The drafting team believes both voice and data would be required.
19 |  |  | In Market environment voice communication with generators is not necessarily required |  | PSE&G | version 1 issue.
19 |  | General Comments – Missing requirements from existing policy | It appears that in the translation from the existing policy to Version 0, Policy 5b 2.1, 2.1.1, 2.1.2, 2.1.3, and 2.1.4 were not included and although redundant with other policies should be added to this standard as additional requirements. |  | FRCC | Reviewed these requirements for inclusion.
19 |  | R2 | Omitted conditions that require notification. |  |  | Corrected omission.
19 |  | R2 | Reliability Authorities are also responsible for notifying other Reliability Authorities. |  | PG&E | Addressed in a later standard under reliability coordinaion.
19 |  | R1 | Reliability Authority should be included in this requirement. |  | FRCC | RA communications requirements are covered in standard 034 - another example of opportunity to better organize standards in Version 1.
19 |  |  | The requirements in this standard are incorrectly numbered. (R3 missing) |  | FRCC | Corrected.
19 |  | Applicability | The standard requirements should apply to entities that impact the reliability of the bulk electric system, therefore, the Version 0 standards should impose the requirements on the entities that are designated “Reliability Entities” which are the Reliability Authority, Balancing Authority, and Transmission Operator. With this philosophy, Generator Operator should be removed from the applicable entities list and requirements of this standard revised accordingly. |  | FRCC | The drafting team believes that generators have some particular obligations defined in current operating policy. LSE's and distribution providers have obligations to shed load when directed in emergencies.
20 |  | R1 | The Transmission Operator is not responsible for implementing a Capacity and Energy Emergency. Please revise. | Alan Boesch | NPPD | Will ask for comment in second posting.
20 |  |  | R6 should come before R5. | Anita Lee | AESO | The order can work either way - each requirement can stand on its own.
20 |  | R5 | Some Emergency Energy Alerts are issued before coming to the end of the list. | Anita Lee | AESO | Agreed.
20 |  |  | The Attachment 1 needs to have all references made to the functional model. | Anita Lee | AESO | Corrected.
20 |  | R5 | Change the last bullet of R5, from Attach 5C to Attachment 1 and clarify that if the first 5 bullets cannot be completed in a timely fashion then you must move to manual load shedding immediately | Brandian | ISO-NE | Corrected.
20 |  | -Attachment 1- | Under (1.) ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Brandian | ISO-NE | Corrected.
20 |  | R6 | First sentence is confusing. It should state “The Reliability Authority that has any Balancing Authority within its Reliability Authority Area experiencing a potential or actual Energy Emergency shall initiate…” The way it’s written now insinuates that the Reliability Authority is experiencing the Energy Emergency. The standard should be written to say that the BA should be responsible for issuing the EEA. | Ed Riley | CAISO | Revised as requested.
20 |  | Levels of Noncompliance | Level 4 Non-compliance needs to define what the time frame for a “delay or gap in communications” is. It’s too vague to measure for compliance. | Ed Riley | CAISO | Version 1 issue.
20 |  | Attachment 1 | NERC defines what counts as "Reserves" differnetly than the WECC Minimum Operating Reliability Criteria. A regional difference may be necessary. | Ed Riley | CAISO | Only existing waivers are being translated into Version 0. A Version 1 regional difference may be submitted in a SAR.
20 |  | Attachment 1 | Section 1, 1.1 should read “The LSE cannot schedule the resources necessary to provide its customers energy requirements due to, for example…” | Ed Riley | CAISO | Version 1 issue.
20 |  | Attachment 1 | Section 1, 2 “Balancing Authorizes” should be Balancing Authorities and the reference to “his” should be changed to “within its”. | Ed Riley | CAISO | Corrected.
20 |  | M1 | At the discretion of the Regional Reliability Council Organization or NERC, an investigation may be initiated to review the operation of a Balancing Authority or Transmission Operator when they have implemented their Capacity and Energy Emergency plans. Notification of an investigation must be made by the Regional Reliability Council Organization to the BALANCING AUTHORITY OR TRANSMISSION OPERATOR being investigated as soon as possible, but no later than 60 days after the event. | Gerald Reahlt | Manitoba | Corrected.
20 |  |  | The Balancing Authority and Transmission Operator is required to maintain operational data, logs and voice recordings relevant to the implementation of the Capacity and Energy Emergency Plans for 60 days following the implementation. After an investigation is completed, the Regional Reliability Council Organization is required to keep the report of the investigation on file for two years. | Gerald Reahlt | Manitoba | Corrected.
20 |  | R2 | The BALANCING AUTHORITY and TRANSMISSION OPERATOR shall communicate their current and future system conditions to neighboring BALANCING AUTHORITY and TRANSMISSION OPERATORS and their RELIABILITY COORDINATOR Authority if they are experiencing an operating emergency. | Gerald Reahlt | Manitoba | Corrected.
20 |  | R5 | Change the last bullet of R5, from Attach 5C to Attachment 1 and clarify that if the first 5 bullets cannot be completed in a timely fashion then you must move to manual load shedding immediately | Guy Zito | NPCC | Revised as requested.
20 |  |  | Reference to Policy 5C is missing. | Guy Zito | NPCC | References corrected.
20 |  | -Attachment 1- | Under (1.) ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Guy Zito | NPCC | Corrected.
20 |  | R6 | Based on the requirement listed in R6 - Reliability Authority should be included in the "Applicability" section. | John Blazekovich | Exelon | Corrected.
20 |  | M1 & M2 | M1 - The MEASUREMENT seems to be a Requirement on Compliance Manager | Mike Kormos | PJM | This is a translation of an existing template and can be improved in Version 1.
20 |  |  | M2 - The MEASUREMENT is not measurable. Level of Assessment is totally subjective. | Mike Kormos | PJM | Version 1 issue - this is the current measure in the compliance template.
20 |  |  | Reference to Policy 5C is missing. | Pete Henderson | IMO | References corrected.
20 |  |  | Reference to Policy 5C Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
20 |  |  | Reference to Policy 5C Requirement 2.1 is missing. | Pete Henderson | IMO | References corrected.
20 |  | -Levels of Non Compliance | Reference to Template P5T1 is missing. | Pete Henderson | IMO | Corrected.
20 |  | -Attachment 1- | Under (1.) ‘RELIABILITY COORDINATOR’ should be replaced with ‘Reliability Authority’. | Pete Henderson | IMO | Corrected.
20 |  | R5 | Balancing Authority cannot shed load. This needs to have some wording that indicates that the BA would direct the appropriate entities to shed load. | Raj Rana | AEP | The BA can direct shedding of load to balance its area in an emergency.
20 |  | R2 | This should be an RA to BA notification process, which is not clearly defined in this standard. | Raj Rana | AEP | The deficient BA should notify the RA and other affected systems.
20 |  |  | The procedure for raising priority level from bucket 6 to 7 in Policy 5, Section C.3. appears to be missing. If this is a business practice, NERC should notify NAESB. | Roman Carter | Southern Company | Omission corrected.
20 |  |  | This standard refereces appedicies that will not exist in the future. | Terry Bilke | MISO | Corrected.
20 |  | R5 | Balancing Authority cannot shed load. This needs to have some wording that indicates that the BA would direct the appropriate entities to shed load. |  |  | The BA can direct shedding of load to balance its area in an emergency.
20 |  | R2 | In the translation of existing policy, the term Reliability Coordinator remained in this requirement. It should be replaced with Reliability Authority. |  | FRCC | Corrected.
20 |  | R6 | It appears that the Drafting Team consolidated existing Policy 9 requirements with the translation of existing Policy 5 in this requirement. As stated earlier, it is important that no changes are made to existing policy with the translation to Version 0.The removal of redundancy should be considered in Version 1, therefore this requirement should be moved to the Version 0 Standards related to existing Policy 9. |  | FRCC | This consolidation was done as part of the Policy 5, 6, and 9 revisions approved by the Board in June.
20 |  | M1 & M2 | M1 - The MEASUREMENT seems to be a Requirement on Compliance Manager |  | PSE&G | This is a translation of an existing template and can be improved in Version 1.
20 |  |  | M2 - The MEASUREMENT is not measurable. Level of Assessment is totally subjective. |  | PSE&G | Version 1 issue - this is the current measure in the compliance template.
20 |  | Title | Modify title to read “Implementation of Emergency Capacity and Energy Plans” |  | Southern Company | Revised as requested.
20 |  |  | R3 should be applied to RA since BA may not have transmission overload information. |  | PSE&G | Version 1 issue.
20 |  | Purpose | The Drafting Team believes this standard is one with potential redundancy with an opportunity for consolidation. Although we agree, as stated earlier, it is important that no changes are made to existing policy with the translation to Version 0.The removal of redundancy should be considered in Version 1. |  | FRCC | Agreed.
20 |  | R3-R5 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
20 |  | R3 | The following excerpt from Standard 020 was from the existing policy introduction: If the Balancing Authority cannot comply with the Control Performance and Disturbance Control Standards, then it shall immediately implement remedies to do so. These remedies include, but are not limited to: Requesting assistance from other Balancing Authorities; Declaring an Energy Emergency through its Reliability Authority; and Reducing load, through procedures such as public appeals, voltage reductions, curtailing interruptible loads and firm loads. With this now a requirement, it is too broad and appears to apply to more than emergency situations. This requirement should be revised to clarify applicability only during emergencies. |  | FRCC | Since it was a "shall" statement in existing policy, it is an existing reliability obligation. Parties are required to follow the operating policies, not certain sections of the policies.
20 |  | R5 | The last bullet references Attachment 5C. With the Version 0 translation, this should be Attachment 1 to Standard 020. |  | FRCC | Corrected.
20 |  | R5 | This policy should be reviewed for version 1. Reliability is jeopardize if all reserves are exhausted before load is shed. |  | PG&E | Agreed.
20 |  | R2 | This should be an RA to BA notification process, which is not clearly defined in this standard. |  |  | The deficient BA should notify the RA and other affected systems.
21 |  | R3 | The BA cannot disconnect equipment. Remove the BA from this requirement. | Alan Boesch | NPPD | Corrected.
21 |  | R1 | The RA is responsible for IROLs in the functional model. The TOP is responsible for local reliability. The BA and TOP take direction from the RA. Please change the requirement or change the functional model. | Alan Boesch | NPPD | Corrected.
21 |  | R3 | May need to include DP since it is the entity that actually sheds load. Also, GOPs should be notified of transmission overloads that will impact its operation | Alan Johnson | Mirant | Drafting team does not believe this requirement applies to a DP.
21 |  |  | Reference to Policy 5D Requirement 1 is missing. | Guy Zito | NPCC | Reference corrected.
21 |  |  | R3 should be applied to RA since BA may not have transmission overload information. | Mike Kormos | PJM | Corrected.
21 |  | R3 | RA vs. BA | Mike Kormos | PJM | Corrected.
21 | 021 |  | Reference to Policy 5D Requirement 1 is missing. | Pete Henderson | IMO | Reference corrected.
21 |  |  | Reference to Policy 5D Requirement 2 is missing. | Pete Henderson | IMO | Reference corrected.
21 |  |  | Reference to Policy 5D Requirement 5 is missing. | Pete Henderson | IMO | Reference corrected.
21 |  |  | References to Policy 5D Requirement 3 and Requirement 4 are missing. | Pete Henderson | IMO | Reference corrected.
21 |  | 1 | The original Policy said the Operating Authority shall take immediate steps to relieve condition. V-0 Standard now states the RA and the TO shall be responsible. The original Policy included Operating Authority entities such as the BA; however V-0 Standard does not include the BA, it is recommended the BA be included. | Roman Carter | Southern Company | The RA and TOP are responsible for taking and directing actions to relieve an SOL or IROL. The BA would follow instructions.
21 |  | R1-R4 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | Reference corrected.
21 |  | R1 | Using both the Transmission Operator and the Balancing Authority as the responsible entities make sense, since each of them can impact SOL/IROL conditions on the transmission network. It is not clear at all, however, how the Balancing Authority will know what to do or when to do it unless directed by the Transmission Operator or the Reliability Authority. In fact, independent operation to manage SOL/IROL conditions on the transmission network without explicit direction from the Transmission Operator or the Reliability Authority would seem to be counter productive, if not down right dangerous. |  | Southern Company | Corrected to RA and TOP.
21 |  | General | We suggest that this standard be rewritten to direct the Transmission Operator to act independently to relieve SOL/IROL conditions in an emergency, up to and including directing the appropriate Balancing Authority(ies) to change reactive or real power output. Note that I assume that this should be done under the independent authority of the Transmission Operator rather than at the direction of the Reliability Authority only under emergency conditions. (May require Ver. 1 Standard) |  | Southern Company | Language revised - please review again.
22 |  | R1 | Each Regional Council Organization shall establish and maintain a Regional reporting procedure to facilitate preparation of preliminary and final disturbance reports. | Gerald Reahlt | Manitoba | Corrected.
22 |  |  | In such cases, the affected RELIABILITY AUTHORITY, BALANCING AUTHORITY, or TRANSMISSION OPERATOR shall notify its Regional Council(s) Organization and NERC promptly and verbally provide as much information as is available at that time. The affected RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS shall then provide timely, periodic verbal updates until adequate information is available to issue a written Preliminary Disturbance Report. If in the judgment of the Regional Council Organization, after consultation with the RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS in which a disturbance occurred, a final report is required, the affected RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS shall prepare this report within 60 days. | Gerald Reahlt | Manitoba | Corrected.
22 |  | Purpose | It is important that the facts surrounding a disturbance shall be made available to RELIABILITY AUTHORITIES, TRANSMISSION OPERATORS, Regional Councils Organizations, NERC, and regulatory agencies entitled to the information. | Gerald Reahlt | Manitoba | Corrected.
22 |  | R3 | RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS responsible for investigating an incident shall provide a preliminary written report to their Regional Council Organization and NERC…. | Gerald Reahlt | Manitoba | Corrected.
22 |  | R5 | The Regional Council Organization shall track and review the status of all final report recommendations at least twice each year to ensure they are being acted upon in a timely manner. If any recommendation has not been acted on within two years, or if Regional Council Organization tracking and review indicates at any time that any recommendation is not being acted on with sufficient diligence, the Regional Council Organization shall notify the NERC Planning Committee and Operating Committee of the status of the recommendation(s) and the steps the Regional Council Organization has taken to accelerate implementation. | Gerald Reahlt | Manitoba | Corrected.
22 |  | R4 | When a BULK ELECTRIC SYSTEM disturbance occurs, the Regional Council’s Organization’s OC and DAWG representatives shall make themselves available to the RELIABILITY AUTHORITIES, BALANCING AUTHORITIES, and TRANSMISSION OPERATORS immediately affected to provide any needed assistance in the investigation and to assist in the preparation of a final report. | Gerald Reahlt | Manitoba | Corrected.
22 |  |  | Reference to Policy 5F Requirement 1 is missing. | Guy Zito | NPCC | References corrected.
22 |  |  | R4 references the NERC OC and DAWG (The reference should be to the Standards Developer) | Mike Kormos | PJM | References corrected.
22 |  | R4 | Replace OC and DAWG with STANDARDS DEVELOPER | Mike Kormos | PJM | Standards Developer does not measure compliance.
22 |  |  | Reference to Policy 5F Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
22 |  |  | Reference to Policy 5F Requirement 2 is missing. | Pete Henderson | IMO | References corrected.
22 |  |  | Reference to Policy 5F Requirement 6 is missing. | Pete Henderson | IMO | References corrected.
22 |  |  | Reference to Policy 5F Requirement 7 is missing. | Pete Henderson | IMO | References corrected.
22 |  |  | References to Policy 5F Requirement 3, Requirement 3.1, Requirement 3.2 and Requirement 3.3 are missing. | Pete Henderson | IMO | References corrected.
22 |  | R1 - R3 | The answer to the question of, "Can we replace reference to RA, BA, and TO by the use of responsible entity?" is NO. The entities and their responsibilities need to be clearly spelled out throughout this document to be effective. | Ray Morella | FirstEnergy | Agreed.
22 |  | 3 | Original Policy stated that the OA who is responsible for investigating incidents submit a preliminary report. OA could mean any one of several entities. Therefore, it is suggesting the entity with the highest responsibility for reliability submit the report, i.e., the RA. | Roman Carter | Southern Company | The drafting team believes it is all named functions that are responsible.
22 |  | R3 | Current wording seems to indicate that the Reliability Authority, Transmission Operator and Balancing Authority must all report independently on each disturbance. We do not believe that was the intent of the original language. Note that the DOE EIA-417 form does not use functional model terminology and refers to Control Areas and Reliability Coordinators. |  | Southern Company | The standard does not state the reports need to be independent.
22 |  | R3 | Making the Reliability Authority, Transmission Operator and Balancing Authority all responsible for disturbance reporting seems to be prone to causing confusion over who is doing what. We suggest making the Reliability Authority responsible for Disturbance Reporting with the Transmission Operator and Balancing Authority responsible for 1) identifying potential disturbances for reporting and 2) supporting the Reliability Coordinator in the data collection and analysis phases of the reporting. (May require Ver. 1 Standard) |  | Southern Company | Should be considered a Version 1 change.
22 |  |  | R4 references the NERC OC and DAWG (The reference should be to the Standards Developer) |  | PSE&G | Standards Developer does not measure compliance.
22 |  | R4 | Replace OC and DAWG with STANDARDS DEVELOPER |  | PSE&G | Standards Developer does not measure compliance.
22 |  | Purpose | Statement too wordy and broad. Should be shortened and kept to a functional description of the reason that the standard is required. For instance: To ensure that disturbances and unusual events that threaten the reliability of the Bulk Electric System are reported to the appropriate entities in sufficient detail for post analysis and to minimize the likelihood of similar events in the future. |  | Southern Company | Shortened as requested.
22 |  | R1-R5 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
23 |  | R3 | Shouldn't the DP be included? | Alan Johnson | Mirant | Possibly - that will be considered.
23 |  | R1 | Change “operating personnel” to “its operating personnel.” | Brandian | ISO-NE | Added "their"
23 |  | R1 | Change “operating personnel” to “its operating personnel.” | Guy Zito | NPCC | Added "their"
23 |  |  | Reference to Policy 5G Requirement 1 is missing. | Guy Zito | NPCC | References corrected.
23 |  | R10 | Exelon Corporation believes the objective of R10 is to address the over/under generation situations that occur at the on/off peak boundaries, R10 should remain in place in the Version 0 Standards, the ambiguity associated with the requirement should be dealt with in Version 1. | John Blazekovich | Exelon | Agreed.
23 |  | R15 | We do not have a problem with eliminating redundancies in Version 0 (R15). We agree with the comment of the drafting team associated with R18. | John Blazekovich | Exelon | Agreed.
23 |  | R1 | Change “operating personnel” to “its operating personnel.” | Pete Henderson | IMO | Added "their"
23 | 23 |  | Reference to Policy 5G Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
23 |  |  | Reference to Policy 5G Requirement 2 is missing. | Pete Henderson | IMO | References corrected.
23 |  |  | Reference to Policy 5G Requirement 3 is missing. | Pete Henderson | IMO | References corrected.
23 |  | R1-R3 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
23 |  | Applicability | The standard requirements should apply to entities that impact the reliability of the bulk electric system, therefore, the Version 0 standards should impose the requirements on the entities that are designated “Reliability Entities” which are the Reliability Authority, Balancing Authority, and Transmission Operator. With this philosophy, Generator Operator should be removed from the applicable entities list and requirements of this standard revised accordingly.. |  | FRCC | The drafting team believes the functional model intends for the generator operator to also be an operating entity responsible for bulk electric facilities - namely generators.
24 |  | R5 | According to the functional model BAs and TOPs coordinate current day and next day operations with RAs and RAs coordinate with each other. This requirement does not follow the relationships defined in the functional model. Either this requirement or the functional model should be change so the two are consistent. | Alan Boesch | NPPD | The drafting team also believes that BAs and TOPs coordinate with each other.
24 |  | R12 | In the functional model the BA’s only involvement in this process is to “Complies with reliability requirements specified by Reliability Authority.” Many BA’s today are associated with the marketing function of the company. The BA should not get the results of studies but it should comply with the reliability requirements of the RA. | Alan Boesch | NPPD | A BA must sign a confidentiality agreement to receive reliabiity data. The drafting team is not changing existing practice with regard to sharing reliability data.
24 |  | R9 | In the functional the RA and TOP are responsible for reactive requirements to support voltage. Please remove the BA from this requirement. | Alan Boesch | NPPD | The BA must also dispatch generation to respect reactive limits.
24 |  | R16 | Remove (e.g. a seven-day forecast of real output). Unless a seven-day forecast is required by another standard. If you want to keep the example change it to a next forecast to be consistent with standard 037. | Alan Boesch | NPPD | Leave in - same as Policy 6.
24 |  | R11 | The BA’s involvement in this process is limited to following the directions of the RA. Please modify this requirement to be consistent with the functional model. | Alan Boesch | NPPD | A BA must respect transmission limits in achieving its balancing function.
24 |  | R1 and R2 | These measures are general statements that came from the Introduction section of the policy and cannot be practically measured. The details assocciated with these statements are contained in the measurements of the policy. These requirements should be deleted. | Alan Boesch | NPPD | The drafting team believes these requirements can be verified, even though they are not quantitative.
24 |  | R17 | This requirement does not conform to FERC requirements. Information should not be sent to the BA. Many BA’s are associated with the parent companies market and should not be provided transmission information. | Alan Boesch | NPPD | A BA must sign a confidentiality agreement to receive reliabiity data. The drafting team is not changing existing practice with regard to sharing reliability data.
24 |  | R7 | This requirement is inconsistent with the Functional Model. In the functional model the RA is responsible to “Perform reliability analysis (actual and contingency) for the Reliability Authority Area”. The BA “Implements emergency procedures as directed by the Reliability Authority. | Alan Boesch | NPPD | The reference to BA is with regard to generation dispatch.
24 |  | R18 | This requirement is only applicable to the TOP. The BA is not responsible for transmission information. Many BA’s are associated with the parent companies market and will not have transmission information | Alan Boesch | NPPD | There is some information in the previous requirements related to generator operating information that must be sent to the RA.
24 |  | R4 | What information would a Transmission Service provider coordinate with a Balancing Authority? Remove the TSP. | Alan Boesch | NPPD | The TSP commits transmission service by approving tags.
24 |  | R4 | This proposed requirement appears to be a new requirement. Policy 6A, Requirement 1.1 only references transmission and generation owners coordinating with their Control Area(s) | Alan Johnson | Mirant | Functionally, the TSP, GOP and LSE are commiting uses of the transmission system.
24 |  | R10 | "All Generator Operators shall operate their plant(s) so as to adhere to ramp schedules." This is not correct, by contract, generators have to perform to meet specifications that are required by their control area. This may or may not include ramp schedules. Non-dispatched generation (ie. wind generation) would not meet this by practice. Grant's thoughts on this would be to have the BA adhere to the ramp schedules only. | Bill Dearing | Grant PUD | Deleted that requirement.
24 |  | R14 | We recommend removing this Requirement which references Planning Standard II.B, which has not been field tested. Although NPCC believes II.B has merit, it should go through the SAR process. | Brandian | ISO-NE | Reference to planning standard is not included.
24 |  | R10 | Yes, we feel that this requirement is both necessary and enforcable. | Deanna Phillips | BPA | Left requirement with BA.
24 |  | R10 | Adherance to ramp schedules should be required. This requirement is a good example of where developing a meaningful measure may be difficult. | Eric Grant | Progress | Left requirement with BA.
24 |  |  | Agree with comments. | Gerald Reahlt | Manitoba
24 |  |  | Does this refer to the Interchange schedule or the unit’s ramp rate? If the Interchange schedule, then wouldn’t this fall under the Balancing Authority? | Gerald Reahlt | Manitoba | Left requirement with BA.
24 |  | R10 | Each BALANCING AUTHORITY shall plan to meet Interchange Schedules. All GENERATOR OPERATORS shall operate their plant(s) so as to adhere to ramp schedules. | Gerald Reahlt | Manitoba | Left requirement with BA.
24 |  |  | It may be more appropriate to add this requirement to each applicable requirement above. | Gerald Reahlt | Manitoba
24 |  |  | The Drafting Team questions the meaning of this requirement and whether it is necessary or enforceable. | Gerald Reahlt | Manitoba
24 |  |  | This may be redundant with a similar requirement in Standard 009. | Gerald Reahlt | Manitoba
24 |  |  | Update standard 009 to include this section. | Gerald Reahlt | Manitoba
24 |  |  | Policy 6A Requirement 1 1.2 does not exist. R5 is covered by Policy 6A Requirement 1.2. | Guy Zito | NPCC | References corrected.
24 |  | R14 | We recommend removing this Requirement which references Planning Standard II.B, which has not been field tested. Although NPCC believes II.B has merit, it should go through the SAR process. | Guy Zito | NPCC | Reference to planning standard is not included.
24 |  | 13 | Standard 024 should be immediately moved to Version 1 to address the ambiguous wording of R13, which may (as currently worded) provide a loophole that could allow a Transmission Service Provider to set up a process (based on filed tariffs or a "regional" process) that specifically does not include SOLs or IROLs of neighboring areas by setting its own standards. | John Blazekovich | Exelon | Agreed.
24 |  | R10 & R14 | PJM agrees that R10 is unenforceable (i.e. that generators shall adhere to ramp schedules) | Mike Kormos | PJM | Left requirement with BA. GOP removed.
24 |  |  | R14 is not a reliability issue as written (Testing of generators on request) | Mike Kormos | PJM | The word verify was intentionally used instead of 'test'.
24 |  | R10 | Adherance to ramp schedules should be required. This requirement is a good example of where developing a meaningful measure may be difficult. | Phil Creech | Progress | Left requirement with BA. GOP removed.
24 |  | R1 | OPERATING AUTHORITY replaced with RELIABILITY AUTHORITY, BALANCING AUTHORITY, TRANSMISSION OPERATOR, and GENERATOR OPERATOR. Original definition of OPERATING AUTHORITY in Policy 5 stated it didn't include Reliability Coordinators. Should RELIABILITY AUTHORITY be deleted since Policy 9 handles RC functions and these were translated to standards 33-40? | Raj Rana | AEP | See general response on RA-RC issue.
24 |  | R18 | R18 only needs to state that the BALANCING AUTHORITIES shall, without any intentional time delay, communicate the information described in the requirement R15 above to their RELIABILITY AUTHORITY, or add such statement to R15. R17 already requires notification to the RA, and these were the activities that Policy today requires notification to the RA, as referenced in Policy 6A R6.1 - 6.5. | Raj Rana | AEP | Version 1.
24 |  | R7 | Need to explicitly and preciselydefine what N-1 contingency means. | Ray Morella | FirstEnergy | Version 1.
24 |  | 4,5 | Requirement says LSE, TSP, and GO coordinate with BA (where confidentiality agreements allow). Under the F.M., the BA can delegate certain tasks that prevent the BA from meeting the Conf. Agreement in order for the BA to meet the obligations of the BA. Version-0 Standard should recognize this ability. | Roman Carter | Southern Company | Version 1.
24 |  | 15,17,18 | Requirement states without intentional delay. How is this enforceable? The burden of proof is with the enforcement organization. | Roman Carter | Southern Company | Version 1.
24 |  | 14 | The requirement says that the Gen. Operator shall perform tests at the request of the RA, TO, and BA. It is recommended that the GO test at the request of the RA only. If the BA and TO request testing, they should forward their request and ask the RA to officially contact the GO for the test. | Roman Carter | Southern Company | Testing is not specifically mentioned in the requirement, only verification.
24 |  | 10 | This requirement includes the following "All Generator Operators shall operate their plant(s) so as to adhere to ramp schedules." It should be pointed out that ramping requirements are viewed on a BA level and many individual Generators are not capable of adhering to a ramp schedule associated with a particular transaction, e.g. 10 minute ramp in the Eastern Interconnect. Generators should have agreements with BAs to assist. | Roman Carter | Southern Company | GOP removed.
24 |  | R18 | Allegheny Power agrees with the Drafting Team, that "it would be more appropriate to add this requirement to each applicable requirement above". | William Smith | Allegheny | Left as is for now.
24 |  | R11 | Allegheny Power recommends that the wording "shall plan to respect all System " be changed to "shall plan with respect to all System". | William Smith | Allegheny | The intent is to plan so as to meet …
24 |  | R9 | Allegheny Power recommends that the wording "shall plan to respect voltage" be changed to "shall plan with respect to voltage". | William Smith | Allegheny | The intent is to plan so as to meet …
24 |  | R6 | Not all Transmission Operators have access to Interchange Information. | William Smith | Allegheny | Only the applicable items apply to each function.
24 |  | R3 | The coordination with neighboring entities need to be further clarified. It can be interpreted that each entity needs to coordinate with all other neighboring entities. | William Smith | Allegheny | They do.
24 |  | R5 | The coordination with neighboring entities need to be further clarified. It can be interpreted that each entity needs to coordinate with all other neighboring entities. | William Smith | Allegheny | They do.
24 |  | R10 | Generation Operators do not arrange interchange schedules or interchange ramp rates. Rather, the Balancing Authority must limit net interchange schedules to the combined equivalent ramp capabilities of connected generators. |  | PEPCO | Removed GOP from requirement.
24 |  | General | Hierarchical structure seems to be implied, but not explicitly defined in the translation of Control Area and Reliability Coordinator language to functional model language. May want to consider writing requirements such that all Balancing Authorities and Transmission Operators within a given Reliability Authority’s area should coordinate their operations planning, etc. Reliability Authorities would then be responsible for coordination between each other, etc. Seems confusing and/or difficult to follow as written. |  | Southern Company | Agree that translation is awkward and may need to review in Version 1.
24 |  | R2 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Standard language is what is used.
24 |  | R6 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Standard language is what is used.
24 |  | R7 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Standard language is what is used.
24 |  | R12 | Language in Draft and Operating Policy Markup don't match. |  | SRP | Standard language is what is used.
24 |  | Title | Needs to be re-written to be more indicative of what the standard is about. We suggest “Operations Planning for Normal Conditions.” |  | Southern Company | Corrected.
24 |  | R17 | Notification of transmission status or rating changes to Balancing Authorities should be limited to those that materially impact the Balancing Authority and may not be allowed under FERC order 889 if Balancing Authority is a market participant (in such cases only notification of limits on generation output will be permitted). |  | Southern Company | Agreed.
24 |  | R16, R17, R18 | Operating Policy Markup says "immediately" instead of "without any intentional delay." |  | SRP | Standard 24 has the final language adopted.
24 |  | R10 & R14 | PJM agrees that R10 is unenforceable (i.e. that generators shall adhere to ramp schedules) |  | PSE&G | GOP removed.
24 |  |  | R14 is not a reliability issue as written (Testing of generators on request) |  | PSE&G | Does not say test; says verify.
24 |  | R9 | Should "Contingency" be all upper case? |  | SRP | Yes - it is a defined term in the glossary.
24 |  | R10 | Should "Interchange Schedules" be all upper case? |  | SRP | Yes - it is a defined term in the glossary.
24 |  | R10 | The Drafting Team questioned the meaning of R10 and whether it was necessary or enforceable. We agree and suggest removing the second sentence of this requirement. |  | FRCC | Removed.
24 |  | R3, R4 & R5 | The parentheticals "where confidentiality agreements allow" imply that confidentiality agreements trump coordination of operational plans needed to assure system reliability. They should be eliminated. |  | PG&E | The rules are not intended to conflict with laws or legal obligations. This is a translation of existing policy. Can be reviewed in Version 1.
24 |  | R3-R5, R12 | The reference to confidentiality agreements was a change for the existing policy used for the translation to Version 0. If some Regional Reliability Councils cannot implement this standard without a reference to confidentiality agreements, a Regional difference should be submitted NERC. |  | FRCC | Drafting team will consider removing these parentheticals.
24 |  | Applicability | The standard requirements should apply to entities that impact the reliability of the bulk electric system, therefore, the Version 0 standards should impose the requirements on the entities that are designated “Reliability Entities” which are the Reliability Authority, Balancing Authority, and Transmission Operator. With this philosophy, Generator Operator and Load Serving Entity should be removed from the applicable entities list and requirements of this standard revised accordingly. Transmission Service Providers must remain because of role in Operations Planning. |  | FRCC | The drafting team believes these other functions must also coordinate their operations with reliability entities.
24 |  | R14 | There was an incorrect translation from existing Policy 6A 5. R14 should be revised as follows: … shall perform generating real AND reactive capability verification that shall include… |  | FRCC | Corrected.
24 |  | R10 | This requirement includes the following "All Generator Operators shall operate their plant(s) so as to adhere to ramp schedules." It should be pointed out that ramping requirements are viewed on a BA level and many individual Generators are not capable of adhering to a ramp schedule associated with a particular transaction, e.g. 10 minute ramp in the Eastern Interconnect. Generators should have agreements with BAs to assist. |  | Southern Company | Removed.
24 |  | R11 | This requirement was modified from the existing policy used for translation to Version 0. The existing policy stated that the applicable entity would “plan to meet” the associated requirement. During the conversion process. “meet” was changed to “respect”. The following should be considered as an alternative: Each Reliability Authority, Balancing Authority, and Transmission Operator shall plan to remain within established System Operating Limits (SOLs). |  | FRCC | Corrected.
24 |  | R9 | This requirement was modified from the existing policy used for translation to Version 0. The existing policy stated that the applicable entity would “plan to meet” the associated requirement. During the conversion process. “meet” was changed to “respect”. This modification changes the intent of the planning for voltage/reactive limits. The following should be considered as an alternative: Each Reliability Authority, Balancing Authority, and Transmission Operator shall plan to consider voltage and/or reactive limits, including the deliverability/capability for any single contingency. |  | FRCC | Changed back to 'meet'.
24 |  | R14 | We suggest that the authority to require real or reactive power testing be centralized at the Reliability Authority level only. Any Transmission Operator or Balancing Authority requiring such tests should coordinate through the Reliability Authority. (May require Ver. 1 Standard) |  | Southern Company | Testing is not specifically mentioned in the requirement, only verification.
25 |  | R1 | Any agreement for assitance would include transmission arrangements. BA's are not responsible for transmission. Please modify to include appropriate transmission entities. | Alan Boesch | NPPD | This is a standard on capacity and energy shortages.
25 |  | R4 | The BA will not develop emergency transmission procedures. TOPs will not develop procedures associated with insufficient generating capacity. Please correct the requirement accordingly. Please change the last two bullets to read “Develop, maintain a set of plans to implement load shedding for operating emergencies.” and “Develop, maintain a set of plans to implement System Restoration.” | Alan Boesch | NPPD | This is a standard on capacity and energy shortages.
25 |  | R5 | In response to the Drafting Team's question, Yes, include the list of potential requirements | Alan Johnson | Mirant | Done.
25 |  | CMP | Why isn't Compliance Template P6T1 incorporated into this standard? | Alan Johnson | Mirant | Done.
25 |  |  | Potential additional elements of Requirement R5: We are of the opinion that at a minimum, critical existing requirements from “noted potential additional elements” should be made a part of Requirement R5, although they may included as guides in Policy 6B. Existing Template P6T1 outlines most of these requirements as mandatory. | Brandian | ISO-NE | Added these elements.
25 |  | R5 | Remove 1, 2, 3, 7, 8 and 9. NPCC recommends that the fuel related guides are not considered for translation into requirements. | Brandian | ISO-NE | Kept list intact from Compliance Template - can revise in Version 0. Fuel criteria here are in context of a system emergency.
25 |  | R2 | In the “Comments” section, the Drafting Team asks about adding the attached “must” statements to the R5 requirement. My answer would be “no” because there are elements to that additional list that not everyone faces such as “Optimizing fuel supply” and “Interruptible and curtailable loads” Keep R5 to a minimum as it’s currently written. | Ed Riley | CAISO | Added for now based on comments.
25 |  |  | List of “must” statements should be included. | Gerald Reahlt | Manitoba | Agreed.
25 |  |  | The Drafting Team asks whether the list of “must” statements describing the emergency plans in Compliance Template P6T1 should be included here. Those items are listed in Policy 6B as guides, but then shown as requirements in the Compliance Template. | Gerald Reahlt | Manitoba | Added.
25 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. Existing P6T1 outlines the levels of non-compliance. | Guy Zito | NPCC | Corrected.
25 |  |  | Does the term “as applicable” allow the Functional Model entities to choose which bullets apply to them? | Guy Zito | NPCC | Not to choose, but to identify which apply to them or not. Would be reviewed by compliance.
25 |  |  | Reference to Policy 6B Requirement 1 is missing. | Guy Zito | NPCC | References corrected.
25 |  | R5 | Remove 1, 2, 3, 7, 8 and 9. NPCC recommends that the fuel related guides are not considered for translation into requirements. | Guy Zito | NPCC | Kept list intact from Compliance Template - can revise in Version 0. Fuel criteria here are in context of a system emergency.
25 |  | R5 | It is the understanding of Exelon Corporation that the drafting team would use the most recent version of the source document(s) as the "overriding" document in the case of conflict. In this case we believe the version of Policy 6 (approved on 6/15/04) should provide the basis for this Standard. | John Blazekovich | Exelon | Agreed. That was used.
25 |  |  | Business activity | Mike Kormos | PJM | Capacity/energy shortages are current NERC policy requirements. Can review in Version 1.
25 |  |  | R4 (second bullet) should be applied to RA since BA may not have transmission information. | Mike Kormos | PJM | RA included.
25 |  |  | R5 many are Generator Operator responsibilities (Delivers, fuel switching, fuel optimization) and are outside RA/BA responsibility. | Mike Kormos | PJM | Drafting team believes these are RA and BA responsibilities in current policy.
25 |  | R7 | R7 (last bullet) has RA/BA "arranging for fuel deliveries" This is outside the responsibility of such entities | Mike Kormos | PJM | Included in current policy 6B 7.4.
25 |  | R4 & R5 & R7 | RA vs. BA | Mike Kormos | PJM | See prior response on this issue.
25 |  | Potential additional elements of requirements R5 | Potential additional elements of Requirement R5: We are of the opinion that at a minimum, critical existing requirements from “noted potential additional elements” should be made a part of Requirement R5, although they may included as guides in Policy 6B. Existing Template P6T1 outlines most of these requirements as mandatory. | Pete Henderson | IMO | Added P6T1 elements.
25 |  | R1 | Reference to Policy 6B Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
25 |  | R5 | Remove 1, 2, 3, 7, 8 and 9. We recommend that the fuel related guides are not considered for translation into requirements. | Pete Henderson | IMO | Kept list intact from Compliance Template - can revise in Version 0. Fuel criteria here are in context of a system emergency.
25 |  | R3 | "BALANCING AUTHORITY" in markup removed from matrix and not required to have emergency load reduction plan for IROLs. Why was the BA removed fom this requirement? | Raj Rana | AEP | BA does not implement load reduction.
25 |  | R5 | Compliance Template P6 T1 states "The Capacity and Energy Emergency Plan must address the following requirements" but goes on to clarify that "Some of the items may not be applicable, as the responsibilities for the item may not rest with the entity being reviewed, and therefore, they should not be penalized for not having that item in the plan." Some of the "13" items in P6 T1 may be more cost effective than others. We need to have the ability to pick the most cost effective solution(s)! The "Plans" should include the 13 items from the compliance template, but that should not mean you must do each of these items during an event. Solutions to Emeregencies and Capacity Deficiency events are not a once size fits all. The operator needs a host of options to choose from. | Raj Rana | AEP | The requirement states the entity must consider the elements in a plan, but leaves flexibility for which elements are implemented.
25 |  | R2 | This requirement is inconsistent with the recently published NERC Continuing Education Hours White paper. | Ray Morella | FirstEnergy | Do not understand the conflict. The training requirement here is from the existing compliance templates.
25 |  | 5 | It is not recommended that the additional elements be included. Origional Policy had them only as Guides and and they should stay as Guides. Also they have not been approved to be requirements (except by Board Adoption as part of a template) by Reg. Ballot Body. | Roman Carter | Southern Company | Elements have been added, but with flexibility in implementation.
25 |  | R5 | The responsibilities associated with the emergency plans in Compliance Template P6T1 should be assigned to the specific responsible entity rather than broadly assigning them to Ras, TOPs and BAs. | William Smith | Allegheny | Do not understand the comment.
25 |  | R3 | BALANCING AUTHORITY in markup removed from matrix and not required to have emergency load reduction plan for IROLs. Why was the BA removed fom this requirement? |  |  | BA does not implement load reduction.
25 |  | R5 | Compliance Template P6 T1 states "The Capacity and Energy Emergency Plan must address the following requirements" but goes on to clarify that "Some of the items may not be applicable, as the responsibilities for the item may not rest with the entity being reviewed, and therefore, they should not be penalized for not having that item in the plan." Some of the "13" items in P6 T1 may be more cost effective than others. We need to have the ability to pick the most cost effective solution(s)! The "Plans" should include the 13 items from the compliance template, but that should not mean you must do each of these items during an event. Solutions to Emeregencies and Capacity Deficiency events are not a once size fits all. The operator needs a host of options to choose from. |  |  | List was provided in attachment for consideration with implementation flexible.
25 |  | R5 | Most of the items appear to be needed in any emergency plan to assure system reliability. Those that are should be included in the requirement. |  | PG&E | Added list.
25 |  | Title | Needs to be re-written to be more indicative of what the standard is about. We suggest “Operations Planning for Emergency Conditions.” Existing title seems to imply that it is for Operations Planning that you do only during an Emergency, not in preparation for the emergency. |  | Southern Company | The drafting team believes the title and the requirements clearly indicate preparations for an emergency, not response during an emergency.
25 |  | R4 | New language added. |  | SRP
25 |  | R3 | Not clear that Operating Authority, as used in the Operating Policy Manual, refers only to Reliability Authority and Transmission Operator, although the use of IROL language does imply this. The Balancing Authority must also have a plan for shedding load to match generation to load and this should be part of his operations planning, however, this may be redundant with Policy 1 or R4 requirements and may not be considered an IROL. Also seems that Distribution Provider and/or Load Serving Entity should be involved in the implementation phase. |  | Southern Company | BA does not implement load reduction.
25 |  | Purpose | Operating Policy Markup says "shall develop" and "These plans shall. . . ." instead of "need s to develop" and "These plans need. . . ." |  | SRP | The revision is to make the statement an active requirement.
25 |  |  | R4 (second bullet) should be applied to RA since BA may not have transmission information. |  | PSE&G | BA may have to be part of emergency response.
25 |  |  | R5 many are Generator Operator responsibilities (Delivers, fuel switching, fuel optimization) and are outside RA/BA responsibility. |  | PSE&G | Translated from existing policy.
25 |  | R7 | R7 (last bullet) has RA/BA "arranging for fuel deliveries" This is outside the responsibility of such entities |  | PSE&G | Translated from existing policy.
25 |  | R1 | Reference should be Policy 6, Section B, Requirement 1. |  | Southern Company | Reference corrected.
25 |  | Drafting Team Comments - R5 | The Drafting Team asked if the list of “must” statements from Compliance Template P6T1 should be included. We think these elements should be included, however the list attached is from the existing Guide not Compliance Template P6T1. Only the elements from the template should be included. |  | FRCC | Added the full list, with the requirement stating the elements need to be considered as applicable.
25 |  | R1 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
25 |  | Purpose | The reference to “ with NERC Operating Policies” should be removed. |  | FRCC | Corrected.
25 |  | R4 – R5 | We suggest combining the two requirements and reword for clarity. |  | FRCC | Version 1.
26 |  | Purpose | We believe that the load shedding implementation requi­rement should be moved to another standard in order to differentiate planning requirements (load shedding capa­city, technical considerations,…) and implementation procedure. (separate the "what" from the "when"). | Boisvert | TransEnergie | Not part of the purpose.
26 |  | R2, 3, 4, 5, & 7 | The Requirements cited are “planning related “ and should not appear in the “operations related” requirements | Brandian | ISO-NE | These are operations planning requirements from current operating policies.
26 |  | Purpose | The purpose statement needs to indicate that this standard is for plans associated with frequency, voltage, and overload conditions. | Ed Riley | CAISO | Operating emergencies is used as a more general term.
26 |  | R1 | Implementation of load shedding should be moved to policy 5 and 9 requirements | Eric Grant | Progress | This standard addresses planning and preparation.
26 |  | Purpose | After taking all other remedial steps, a RELIABILITY AUTHORITY, BALANCING AUTHORITY and TRANSMISSION OPERATOR operating with insufficient generation or transmission capacity shall shed customer load rather than risk an uncontrolled failure of components or cascading outages of the INTERCONNECTION.” | Gerald Reahlt | Manitoba | Corrected.
26 |  |  | The purpose statement is the same as the first requirement; the purpose should talk about load shedding plans not actions. | Gerald Reahlt | Manitoba | Corrected.
26 |  |  | Exelon Corporation believes that the "confusion" described should be dealt with in Version 1 (not Version 0). | John Blazekovich | Exelon | Agreed.
26 |  |  | Exelon Corporation suggests that Transmission Owner be included in the "Applicability" section. We believe in most cases that the Transmission Owner will be the entity installing and coordinating automatic load shedding schemes (R2, R3). | John Blazekovich | Exelon | Drafting team assumes TOP is responsible for load shedding plans, although owner may provide facilities.
26 |  |  | R3 (coordination of load shedding) should be applied to RA since BA may not have wide area information. | Mike Kormos | PJM | RA included.
26 |  |  | R7 (coordination of load shedding) should be applied to RA since BA may not have wide area information. | Mike Kormos | PJM | RA included.
26 |  |  | RA vs. BA | Mike Kormos | PJM | RA included.
26 |  | R1 | Implementation of load shedding should be moved to policy 5 and 9 requirements | Phil Creech | Progress | Extracted from Policy 6C - can reorganize in Version 1.
26 |  | R7 | Add UVLS to this requirement. | Ray Morella | FirstEnergy | Version 1.
26 |  | 4 | It does not appear that Policiy 6C 1.2, and 1.2.1 were adequately replicated into V-0 Standard. It is recommended that the two sections be copied exactly as written and included as requirement 4. | Roman Carter | Southern Company | Addressed in R4.
26 |  | R1 | Concept is certainly redundant. However, we couldn’t find where the specific wording is set forth so succinctly in any other requirement. |  | Southern Company | Left as is for now.
26 |  | R4 | Language of the standard does not appear to faithfully replicate the meaning of the original policy (Policy 6, Section C, Requirement 1.2.1). Policy says that automatic load shedding shall be “related to one of the following” conditions whereas the standard states that the operating authority “shall initiate automatic load shedding” upon one of the conditions occurring. This is a definite change in policy, whether intended or not. MAJOR ISSUE. |  | Southern Company | Corrected.
26 |  |  | R3 (coordination of load shedding) should be applied to RA since BA may not have wide area information. |  | PSE&G | Corrected.
26 |  |  | R7 (coordination of load shedding) should be applied to RA since BA may not have wide area information. |  | PSE&G | Corrected.
26 |  | General | Requirements R5 through R8 for Standard 026 follow standard 027 in my copy of the PDF document. Standard 21 and 22 are out of order. |  | Southern Company | Corrected.
26 |  | Purpose | Seems more like a requirement than a purpose. Shorten and simplify. Minor Issue. We agree with the Ver. 0 SDT that both the operations planning and implementation stages of load shedding are mingled in Policy 6, Section C. We recommend that they be separated into two distinct standards. |  | Southern Company | Corrected.
26 |  |  | The Drafting Team asked if the implementation requirements should be moved to other standards focused on emergency operations. As stated earlier, it is important that no changes are made to existing policy with the translation to Version 0.This modification should be considered in Version 1. |  | FRCC | Agreed.
26 |  | Drafting Team Comments - RI | The Drafting Team asked if this requirement was redundant with the purpose statement. As we stated above, the purpose should be more general and R1 the specific requirement. |  | FRCC | Corrected.
26 |  | Purpose | The purpose should be more general with the specifics addressed in R1. |  | FRCC | Corrected.
26 |  | Purpose | This standard should address requirments of automatic schemes and operaional plans. Implementation of plans should be covered in other requirments as long as they require adherence to the plans. |  | PG&E | Translated from existing policy.
27 |  |  | Does the term “as applicable” allow the Functional Model entities to choose which bullets apply to them? | Brandian | ISO-NE | Not choose, but identify. Will be subject to compliance review.
27 |  | R4 | NPCC’s participating members are concerned that elements of Policy 5, Section E have not been sufficiently addressed in this translation. | Brandian | ISO-NE | Added in R10.
27 |  | R1 | “Load Serving Entities” need to also be identified in the Standard as their restoration plans impact others. | Ed Riley | CAISO | Current policy does not specify LSE having a restoration plan.
27 |  | Regional Differences | “None Identified” doesn’t take into account the WECC automatic load restoration feature to prevent frequency overshoot required as part of the coordinated plan. | Ed Riley | CAISO | Not a current waiver of NERC policy approved by the OC.
27 |  | R4 | The CAISO agrees with the Drafting Team comment, but this needs to be addressed in Version 1. | Ed Riley | CAISO | Agreed.
27 |  | R7 | Training of personnel should be on an annual basis to align with the requirement in R3. | Ed Riley | CAISO | Translated from existing policy.
27 |  |  | Agree with comments. | Gerald Reahlt | Manitoba
27 |  |  | The Drafting Team believes this requirement should be clarified to indicate the restoration plan should have as a priority restoring the integrity of the Interconnection. | Gerald Reahlt | Manitoba | Version 1.
27 |  |  | This is the same statement as R5, either this sentence should be removed from R1 or remove R5. | Gerald Reahlt | Manitoba | Corrected.
27 |  | R1 | This plan shall be coordinated with other RELIABILITY AUTHORITIES, TRANSMISSION OPERATORS, and BALANCING AUTHORITIES in the INTERCONNECTION to ensure a consistent INTERCONNECTION restoration plan. | Gerald Reahlt | Manitoba
27 |  | R4 | NPCC’s participating members are concerned that elements of Policy 5, Section E have not been sufficiently addressed in this translation. | Guy Zito | NPCC | Added in R10.
27 |  |  | Potential additional elements of Requirement R5: We are of the opinion that at a minimum, critical existing requirements from “noted potential additional elements” should be made a part of Requirement R5, although they may included as guides in Policy 6B. Existing Template P6T1 outlines most of these requirements as mandatory. | Guy Zito | NPCC
27 |  |  | Reference to Policy 6D Introduction is missing. | Guy Zito | NPCC | References corrected.
27 |  | R2, 3, 4, 5, & 7 | The Requirements cited are “planning related “ and should not appear in the “operations related” requirements | Guy Zito | NPCC | These are operations planning requirements from current operating policies.
27 |  | R4 | Exelon Corporation believes that requirement should remain as written, any required clarification should be addressed in Version 1. | John Blazekovich | Exelon | Agreed and corrected.
27 |  |  | R8 - Verification of Restoration Plans may be simulated but it can't be tested without severe consequences (Isolating NY to test the Plans for NY may not be smiled upon) | Mike Kormos | PJM
27 |  | R8 | RA vs. BA | Mike Kormos | PJM | See prior response on this issue.
27 |  |  | Requirements must be practical | Mike Kormos | PJM | Version 1.
27 |  |  | Restoration requires transmission information that BA is not required (by the Functional Model) to have. | Mike Kormos | PJM
27 |  |  | Does the term “as applicable” allow the Functional Model entities to choose which bullets apply to them? | Pete Henderson | IMO | Will be verified by compliance monitoring.
27 |  | R4 | We are concerned that elements of Policy 5, Section E have not been sufficiently addressed in this translation. | Pete Henderson | IMO | Corrected.
27 |  | R9 | While the TO and BA should know the status of their black start resources and the RA should have an understanding of their location and intended use, we're not sure how the RA would "ensure the availability" of the black start resources in its footprint. | Terry Bilke | MISO | Should be considered a part of restoration planning by the RA.
27 |  |  | Allegheny Power would support the creation of a Reference Document for the Guides in Policy 6D. | William Smith | Allegheny | Added as attachment to standard for Version 0.
27 |  | R8 | Actual testing of many restoration procedures is not practical. Operating experience or simulation are frequently the only measures possible without actual shutdown. |  | PEPCO | Simulation is allowed. Statement is from current policy.
27 |  | R4 | Concur with comment. |  | PG&E
27 |  | R1 | Language from Policy 6 applying to Control Areas does not fit well with functional model entities. Balancing Authorities and their associated Transmission Operators can not logically and independently develop plans to “reestablish its electric system.” Wording needs to be modified to reflect the interdependencies between functional model entities. |  | Southern Company
27 |  | R2 | New language added. |  | SRP | Drafting team believes this is a straightforward translation of 6D1.1
27 |  | General | Overall, these requirements seem to miss the interdependent nature of restoration planning or implementation in a functional model environment. In particular, the close coupling between black start units and transmission line switching and load pickup following a blackout is not well addressed (if it is addressed at all). This section needs major work. (May require Ver. 1 Standard) |  | Southern Company
27 |  | R2 | R1 comment above also applies to restoration planning. |  | Southern Company
27 |  |  | R8 - Verification of Restoration Plans may be simulated but it can't be tested without severe consequences (Isolating NY to test the Plans for NY may not be smiled upon) |  | PSE&G | Simulation is allowed. Statement is from current policy.
27 |  | R9 | Recommend the following revision for clarity: The Reliability Authority, Transmission Operator, and Balancing Authority shall ensure the availability and location of black start capability within its respective Area to meet the needs of the restoration plan. |  | FRCC | Version 1.
27 |  |  | Requirements must be practical |  | PSE&G | Version 1.
27 |  |  | Restoration requires transmission information that BA is not required (by the Functional Model) to have. |  | PSE&G | Version 1.
27 |  | R4 | Should "Interconnection" be "INTERCONNECTION"? |  | SRP | Global correction made in format.
27 |  | Applicability | Should the requirement for Generation Operators to have restoration plans for units that require black start capability be included here? A set of minimum restoration plan elements similar to those being considered for emergency plans should be added. |  | PG&E | Version 1.
27 |  | Drafting Team Comments - R4 | The Drafting Team believed the restoration plan should include as a priority, restoring the integrity of the Interconnection. As stated earlier, it is important that no changes are made to existing policy with the translation to Version 0.This modification should be considered in Version 1. |  | FRCC | This is a simple translation of 6D1.2 from passive to active voice.
27 |  | R2 | The Existing Document References include the Compliance Template P6T2. |  | FRCC | References corrected.
27 |  | R1 | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
27 |  | R4 | We concur with the Ver. 0 SDT comment to R4 that the restoration of the integrity of the Interconnection should be explicitly emphasized as the penultimate goal of restoration activities. |  | Southern Company
28 |  | LNC | The levels of non-compliance shown in the standard comes from P6T2. Believe P6T3 levels of non-compliance fit here. | Alan Johnson | Mirant
28 |  | Purpose | NPCC’s participating members request clarification of this purpose. | Brandian | ISO-NE
28 |  | Purpose | Please replace "reliability entity needs to Authorities" with the appropriate language. This sentence does not make sense as written. | Deanna Phillips | BPA
28 |  | Purpose | "Each reliability entity needs to Authorities shall have a plan to continue…” Something is missing to make this statement make sense but I’m not sure what that is. | Ed Riley | CAISO
28 |  | R1 | 3rd bullet on the second page needs to have “are” inserted after “The functions” | Ed Riley | CAISO
28 |  | R1 | "AREAS" needs to be redefined in terms of the functional entities. | Eric Grant | Progress
28 |  |  | 1. The necessary operating instructions and procedures for restoring loads, including identification of critical load requirements. | Gerald Reahlt | Manitoba
28 |  |  | 2. A set of procedures for annual review and updated for simulating and, where practical, actual testing and verification of the plan resources and procedures (at least every three years). | Gerald Reahlt | Manitoba
28 |  |  | 3. Documentation must be retained in the personnel training records that operating personnel have been trained annually in the implementation of the plan and have participated in restoration exercises. | Gerald Reahlt | Manitoba
28 |  | Purpose | Each reliability entity needs to AUTHORITIES shall have a plan to continue reliability operations in the event its control center becomes inoperable. | Gerald Reahlt | Manitoba
28 |  | Purpose | Each reliability entity needs to AUTHORITIES shall have a plan to continue reliability operations in the event its control center becomes inoperable. | Gerald Reahlt | Manitoba
28 |  | Levels of non compliance | Level 1 — Plan exists but is not reviewed annually. | Gerald Reahlt | Manitoba
28 |  | Levels of non compliance | Level 2 — Plan exists but does not address one of the 10 requirements. | Gerald Reahlt | Manitoba
28 |  | Levels of non compliance | Level 3 — N/A | Gerald Reahlt | Manitoba
28 |  | Levels of non compliance | Level 4 — Plan exists but does not address two or more of the nine requirements or there is no Restoration Plan in place. | Gerald Reahlt | Manitoba
28 |  | Existing Document references | Operating Policy 6 – Operations Planning | Gerald Reahlt | Manitoba
28 |  |  | Requires rewording. | Gerald Reahlt | Manitoba
28 |  |  | Section E – Loss of Primary Control Facilities Continuity of Operations | Gerald Reahlt | Manitoba
28 |  |  | Section E – Loss of Primary Control Facilities Continuity of Operations | Gerald Reahlt | Manitoba
28 |  | Compliance monitoring process. | Self-Certification: Each RELIABILITY AUTHORITY, TRANSMISSION OPERATOR, and BALANCING AUTHORITY shall annually, self-certify to the Regional Reliability Organization that the following criteria have | Gerald Reahlt | Manitoba
28 |  |  | These are from compliance template P6T2 dealing with restoration plans not P6T3 dealing with loss of primary control facility. | Gerald Reahlt | Manitoba
28 |  | Levels of non compliance | These levels of non compliance refer to restoration not loss of primary control facilities. | Gerald Reahlt | Manitoba
28 |  | Purpose | NPCC’s participating members request clarification of this purpose. | Guy Zito | NPCC
28 |  | Purpose | NPCC’s participating members request clarification of this purpose. | Guy Zito | NPCC
28 |  |  | Reference to Template P6T3 is missing | Guy Zito | NPCC | Corrected for Draft 3.
28 |  | Levels of Non Compliance | The Compliance Monitoring requirements appear to be related to System Restoration as opposed to Control Center Recovery requirements. NPCC would like the Drafting Team to review this section. | Guy Zito | NPCC | Corrected for Draft 3.
28 | 28 | -Standard 028 | Reference to Template P6T3 is missing | Pete Henderson | IMO | Corrected for Draft 3.
28 |  |  | Reference to Template P6T3 is missing belonging to bulleted items 1-7. | Pete Henderson | IMO | Corrected for Draft 3.
28 |  | Levels of Non Compliance | The Compliance Monitoring requirements appear to be related to System Restoration as opposed to Control Center Recovery requirements. We would like the Drafting Team to review this section. | Pete Henderson | IMO | Corrected for Draft 3.
28 |  | R1 | "AREAS" needs to be redefined in terms of the functional entities. | Phil Creech | Progress | Areas is defined in glossary. Control area no longer applicable.
28 |  | Requirements | 4th bullet item has "AREAS". P6 T3 uses the term "control areas." | Raj Rana | AEP | Areas is defined in glossary. Control area no longer applicable.
28 |  | Purpose | Description is not a complete sentence. Markup document has BALANCING AUTHORITIES, TRANSMISSION OPERATOTRS, and RELIABILITY AUTHORITIES shall have a plan to continue reliability operations in the event its control center becomes inoperable. | Raj Rana | AEP
28 |  |  | Matrix uses template P6 T2 as a referance. It should referance template P6 T3. | Raj Rana | AEP | Corrected for Draft 3.
28 |  |  | There needs to be a requirement on how the operating staff knows that they have lost control center functionality. | Robert Snow
28 |  |  | Under R1, the continency plan should addresses how monitoring and control of facilities will be achieved and provide a maximum time for restoration of the monitoring and control function. | Robert Snow
28 |  |  | Compliance Monitoring Process - The Self-Certification statement do not apply to "Plans for Loss of Control Center Functionality". Levels of Non Compliance - These levels to do appear to apply to "Plans for Loss of Control Center functionality". Levels of Non Compliance - Level 4 should read "two or more of the ten requirements". | William Smith | Allegheny
28 |  | R1 | The RA, TOP and BA do not all have responsibility for all of the bullet points. The 8th bullet should be changed to read "The plan shall include the functions to be coordinated with and among neighboring AREAS. The 9th bullet should be changed to read "The plan shall include plans for notification to other operating entities as the steps of the restoration plan are implemented". | William Smith | Allegheny
28 |  |  | The words "needs to Authorities" should be stricken from the Purpose. | William Smith | Allegheny | Corrected.
28 |  | Various | Compliance Template P6T2 is given as the reference for several requirements but it should be P6T3. |  | SRP | Corrected for Draft 3.
28 |  | Purpose | Description is not a complete sentence. Markup document has BALANCING AUTHORITIES, TRANSMISSION OPERATOTRS, and RELIABILITY AUTHORITIES shall have a plan to continue reliability operations in the event its control center becomes inoperable.
28 |  | Levels of Non-Compliance | Draft states there are 10 requirements.Template states there are 9. |  | SRP | There are 10.
28 |  | General | Follows Compliance Template P6T2 which does not follow Operating Policy 6, Section D, but which was approved by the NERC Board of Trustees. There is no support in policy for this. Old Issue |  | Southern Company | Drafting team tasked to include compliance templates also, not limited to policy.
28 |  |  | Matrix uses template P6 T2 as a referance. It should referance template P6 T3. |  |  | Corrected.
28 |  | R1 | PTT3 specifies that the plan is written and kept current. |  | SRP
28 |  | Purpose | Recommend the following revision for clarity: Each Reliability Authority, Transmission Operator, and Balancing Authority shall have a plan to continue reliability operations in the event its control center becomes inoperable. |  | FRCC
28 |  | Existing Document References | The Compliance Template for translation is P6T3 not P6T2. Because of this error, there are considerable changes required to correct this standard to achieve an accurate translation. |  | FRCC | Corrected for Draft 3.
28 |  | Levels of Non Compliance | The following is an accurate translation of Compliance Template P6T3 provided as a recommended revision for clarity: |  | FRCC
28 |  | R1 | The following is an accurate translation of Compliance Template P6T3 provided as a recommended revision for clarity: |  | FRCC
28 |  | Compliance Monitoring Process | The following is an accurate translation of Compliance Template P6T3 provided as a recommended revision for clarity: Periodic Review Review and evaluate the loss of Primary Control Facility contingency plan as part of the three-year on-site audit process. The audit must include a demonstration of the plan by the Reliability Authority, Transmission Operator, and Balancing Authority. Self-Certification Reliability Authority, Transmission Operator, and Balancing Authority must annually, self-certify to the Regional Reliability Council that Requirements 5, 6 and 7 have been done, that is, the Plan has been tested, the Shift Operators have been trained as planned, and the Plan has been reviewed. Reset Period: One calendar year. Data Retention: The contingency plan for loss of primary control facility must be available for review at all times. |  | FRCC
29 |  | R-1 | Add the following to the applicability of the requirement: TRANSMISSION OWNERS, GENERATOR OWNERS, GENERATOR OPERATORS, LOAD SERVING ENTITIES. | Bonnie Bushnell | NERC TWG
29 |  | R-2 | Change to "Adequacy, redundancy, reliability and applicability are determined by the requirements of applications such as RAIS, ICCP and IDC." | Bonnie Bushnell | NERC TWG
29 |  |  | In many cases the references to few of existing policies are either missing or are not mapped correctly within the new version 0 requirements. We are facilitating NERC SDT in this matter by identifying some of the inconsistencies or needs of references. The specifics are mentioned later: | Brandian | ISO-NE | Reference corrected.
29 |  | R1 Thru R5 | Add “Transmission Owners, Generator Owners, Generator Operators and Load Serving Entities” to the list of FM entities this applies to. | Brandian | ISO-NE
29 |  |  | 1. Operating within limits. The OPERATING AUTHORITY shall operate within the SYSTEM OPERATING LIMITS (SOLs) and INTERCONNECTION RELIABILITY OPERATING LIMITS (IROLs). | Gerald Reahlt | Manitoba
29 |  |  | Disagree. Policy 5 A. deals with operating within limits not providing adequate and reliable telecommunications. | Gerald Reahlt | Manitoba
29 |  | R1 | Each RELIABILITY AUTHORITY, TRANSMISSION OPERATOR, and BALANCING AUTHORITY shall provide adequate and reliable telecommunications facilities internally and with other RELIABILITY AUTHORITIES, TRANSMISSION OPERATORS, and BALANCING AUTHORITIES for the exchange of INTERCONNECTION and operating information necessary to maintain reliability. | Gerald Reahlt | Manitoba
29 |  |  | There may be redundancy here with Policy 5A Requirement 1. | Gerald Reahlt | Manitoba
29 |  |  | Where applicable, these facilities shall be redundant and diversely routed. | Gerald Reahlt | Manitoba
29 |  | R1 Thru R5 | Add “Transmission Owners, Generator Owners, Generator Operators and Load Serving Entities” to the list of FM entities this applies to. | Guy Zito | NPCC | Policy 7 addressed ISN participants and did not necessarily impose requirements on generator operators and owners and LSEs and transmission owners. If needs to expand in the future, SAR can be introduced.
29 |  |  | R4 (which talks about the language of communication used) refers Policy 7B Requirement 2 as its corresponding existing document. Whereas, the Policy 7B Requirement discusses a different topic, Inter Regional Security Network. | Guy Zito | NPCC
29 |  | R1 | Exelon Corporation cannot find the apparent redundancy (Policy 5A Req. 1) cited "Comments" section, we suggest leaving R1 as written. | John Blazekovich | Exelon
29 | 29 |  | R4 (which talks about the language of communication used) refers Policy 7B Requirement 2 as its corresponding existing document. Whereas, the Policy 7B Requirement discusses a different topic, Inter Regional Security Network. | Pete Henderson | IMO
29 |  | R3 | Need definition of Areas and Regions | Raj Rana | AEP | Glossary added.
29 |  |  | Reference should be to Policy 5B-R1, not 5A-R1. | Raj Rana | AEP | References corrected.
29 |  |  | Identify that for a telecommunications circuit to be adequate and reliable, it must also be secure from interactions with other entities (hackers). While cyber security has been a new topic with NERC, it is not new to anyone involved in real time operations. | Robert Snow |  | Being considered in cyber security standard; not part of an existing policy.
29 |  |  | In section R1, for all but the smallest areas, redundancy and diversely routed telecommunications is required. | Robert Snow
29 |  | R5 | Add to Existing Document Reference: “Policy 7 – C1” |  | Southern Company | References corrected.
29 |  |  | Also, in searching the new standards a specific instance of the old Policy 5A Requirement 1 could not be found. |  | Southern Company
29 |  | R3 | Need definition of Areas and Regions
29 |  |  | Reference should be to Policy 5B-R1, not 5A-R1.
29 |  | R1 | The reference in the comment column is that “There may be redundancy here with Policy 5A Requirement 1” is not understood. The section referenced in Policy 5A – 1 concerns operating within SOL and IROL limits and does not address telecommunications facilities. Please clarify. |  | Southern Company
30 |  | M-1 | Additionally, in element #1 of the M1 measures, the use of the term "operating position" and "position" cause ambiguity/confusion, whereby the notion of a System Operator and System Personnel are clearly delineated in the old version of P8T1. Clarification of what was intended is requested or use the words as they appear in the Template. | Brandian | ISO-NE | The drafting team believes operating personnel is clearer. In the functional model, system operator or system personnel are not used.
30 |  | Measure & Level of non-compliance: | Existing template outlines a clause related to “Interview Verification” requirements. Moreover, non-compliance level 4 in existing template P8T1 refers to the following: ".or the interview verification items 1 and 2 do not support the authority of the Reliability Authority....”. Such interview related items referred to in the existing P8T1 should be translated in the new language measures and in level 4 non-compliance for completeness/correctness. | Brandian | ISO-NE
30 |  |  | Reference to Policy 6B Requirement 1 is missing. | Brandian | ISO-NE | Reference corrected.
30 |  | Levels of Non Compliance | The Compliance Monitoring requirements appear to be related to System Restoration as opposed to Control Center Recovery requirements. NPCC would like the Drafting Team to review this section. | Brandian | ISO-NE
30 |  | M-1 | Additionally, in element #1 of the M1 measures, the use of the term "operating position" and "position" cause ambiguity/confusion, whereby the notion of a System Operator and System Personnel are clearly delineated in the old version of P8T1. Clarification of what was intended is requested or use the words as they appear in the Template. | Guy Zito | NPCC | The drafting team believes operating personnel is clearer. In the functional model, system operator or system personnel are not used.
30 |  |  | Clarification from the Drafting Team on the intended meaning of “current” in the Measures. | Guy Zito | NPCC
30 |  | Measure & Level of non-compliance: | Existing template outlines a clause related to “Interview Verification” requirements. Moreover, non-compliance level 4 in existing template P8T1 refers to the following: ".or the interview verification items 1 and 2 do not support the authority of the Reliability Authority....”. Such interview related items referred to in the existing P8T1 should be translated in the new language measures and in level 4 non-compliance for completeness/correctness. | Guy Zito | NPCC
30 |  | M-1 | Additionally, in element #1 of the M1 measures, the use of the term "operating position" and "position" cause ambiguity/confusion, whereby the notion of a System Operator and System Personnel are clearly delineated in the old version of P8T1. | Pete Henderson | IMO | The drafting team believes operating personnel is clearer. In the functional model, system operator or system personnel are not used.
30 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. Existing P6T1 outlines the levels of non-compliance. | Pete Henderson | IMO
30 |  | Measure & Level of non-compliance: | Existing template outlines a clause related to “Interview Verification” requirements. Moreover, non-compliance level 4 in existing template P8T1 refers to the following: ".or the interview verification items 1 and 2 do not support the authority of the Reliability Authority....”. Such interview related items referred to in the existing P8T1 should be translated in the new language measures and in level 4 non-compliance for completeness/correctness. | Pete Henderson | IMO
30 |  | M1 | Documentation item number 4 from the Current P8 T1 is missing from M1. | William Smith | Allegheny
30 |  | Measures | M1 – Bullet 2 – Reference to NERC Operating Policies should be replaced with NERC Reliability Standards |  | FRCC | Missed for Draft 2, but fixed for Draft 3.
30 |  | Compliance Monitoring Process | The Data Retention requirement for this standard should be 1 year. The probability exists that over time, the job description and perhaps other documentation will be modified. There should not be a requirement to keep past versions of authorizing documents for an indefinite period of time. |  | Southern Company
30 |  | Compliance Monitoring Process | With the addition of the omitted requirement from the existing Compliance Template P8T1 used for translation the following revision is required: |  | FRCC
31 |  | R1 | In bullet 5, reference is made to Attachment 1, which is Appendix 8B1. However, the appendix was not attached to the standard. | Alan Johnson | Mirant | Corrected.
31 |  |  | R1 may also need to include corresponding existing document Policy 8B’s Requirements 1.5, 1.6 and 1.7. | Brandian | ISO-NE
31 |  | Levels of non compliance | Level 3 — The RELIABILITY AUTHORITY, TRANSMISSION OPERATOR, and BALANCING AUTHORITY have not completed Criterion 2 of Requirement 1. Is this not referring to requirement 2? | Gerald Reahlt | Manitoba
31 |  |  | Attachment 1 referred to in this Requirement, bullet 5 does not exist in the materials. | Guy Zito | NPCC | Corrected.
31 |  |  | R1 may also need to include corresponding existing document Policy 8B’s Requirements 1.5, 1.6 and 1.7. | Guy Zito | NPCC | References corrected.
31 |  |  | Measure could be that one has a documented program. | Mike Kormos | PJM
31 |  |  | Measure could be that one has a documented program. | Mike Kormos | PJM
31 |  | M1 | The MEASUREMENT seems to be a Requirement (shall review program) | Mike Kormos | PJM
31 |  | M1 | The MEASUREMENT seems to be a Requirement (shall review program) | Mike Kormos | PJM
31 |  |  | R1 may also need to include corresponding existing document Policy 8B’s Requirements 1.5, 1.6 and 1.7. | Pete Henderson | IMO
31 |  | R1 | Attachment 1 to describe elements to be included in the training program is missing. | Raj Rana | AEP
31 |  | R1 | There appears to be missing items in this requirement as well as secctions on "Regional Differences", "Compliance Monitoring Process", etc. | William Smith | Allegheny
31 |  |  | Measure could be that one has a documented program. |  | PSE&G
31 |  | Measures | Should have an M2 indicating that training records shall be reviewed to ensure that the required 40 hours of training and drills in system emergencies was provided. |  | Southern Company
31 |  | General Comments | The Existing Document References should be included to provide clarity of translation. |  | FRCC | References corrected.
31 |  | M1 | The MEASUREMENT seems to be a Requirement (shall review program) |  | PSE&G
32 |  | R1 | It is not clear what proper certification requirements for each funtion. Grant is concerned of the ever increasing burden of training and certifying of System Operators. How will the current Certification structure meld with the proposed Version 0? | Bill Dearing | Grant PUD
32 |  | R1.2 | “Positions that are directly responsible for complying with NERC” should be changed to: “Operating Per­sonnel in positions that are directly responsible for complying with NERC.” | Boisvert | TransEnergie
32 |  | M1.2 | A very good measure which should be kept in the new standard. | Boisvert | TransEnergie
32 |  |  | To be consistent with the existing template P8T2. The Operating Position certification is not a measure­ment in the new Operating Policy translation, but P8T2 requires such reporting. | Boisvert | TransEnergie
32 |  | Applicability; | Transmission Operators should be replaced by System Operators as in the present Policy 8. Failing this, the TOs should be changed to Inter­change Authority, because these requirements are applicable to all three Authorities. | Boisvert | TransEnergie | System operator is not a defined term in the functional model.
32 |  |  | “Operating Personnel in positions that are directly responsible for complying with NERC.” | Brandian | ISO-NE
32 |  | R1.2 | “Positions that are directly responsible for complying with NERC.” Should be changed to; | Brandian | ISO-NE
32 |  |  | Associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing and needs to be defined in this standard simultaneously. Existing P6T1 outlines the levels of non-compliance. | Brandian | ISO-NE
32 |  |  | Clarification from the Drafting Team on the intended meaning of “current” in the Measures. | Brandian | ISO-NE | Version 1.
32 |  |  | Operating Position certification also is not a measurement in the new Operating Policy translation but P8T2 requires such reporting. | Brandian | ISO-NE
32 |  |  | R1’s existing document references have been given as Policy 8C Requirements 1, 1.1 and 1.2 whereas these requirements do NOT exist in the original Policy 8C. In fact, the Version 0 standard 032 Requirement R1 has been derived from Policy 8C Standard 1. | Brandian | ISO-NE
32 |  |  | Requirement should apply only to positions that are directly responsible for complying with NERC. Please clarify | Brandian | ISO-NE
32 |  |  | To be consistent with the existing template P8T2 | Brandian | ISO-NE
32 |  | R1 | Policy 8C Standard 1 is satisfactorily represented by Standard 032 Requirement 1. However, their was a one word change from "both" to "either", that can change the meaning of the statement, depending upon interpretation. In the interest of keeping the continuity between Policy 8C and Standard 32, the wording should be kept consistant and any changes be make through the normal process as part of version 1. | David Carlson | NERC PCGC
32 |  | M1 | Policy 8C Standard 2 exception is satisfactorily represented by Standard 032 Measurement 1. | David Carlson | NERC PCGC
32 |  | R1 | Suggestion to be incorporated into the next version (version 1): The operating position is to be filled by a person holding the appropriate level certification. For Example; a person that is acting as the Reliability Coordiator will need to hold a Reliability Coordinator Operator Certification and a person acting as a Transmission Operator would need to hold a Transmission Operator Certification. | David Carlson | NERC PCGC
32 |  |  | The "Effective Date" is listed as February 8, 2004, which is an error, it should be February 8, 2005. | David Carlson | NERC PCGC
32 |  | R1 | Policy 8C Standard 1 is satisfactorily represented by Standard 032 Requirement 1. However, their was a one word change from "both" to "either", that can change the meaning of the statement, depending upon interpretation. In the interest of keeping the continuity between Policy 8C and Standard 32, the wording should be kept consistant and any changes be make through the normal process as part of version 1. | Doug Hils | Cinergy
32 |  | M1 | Policy 8C Standard 2 exception is satisfactorily represented by Standard 032 Measurement 1. | Doug Hils | Cinergy
32 |  | R1 | Suggestion to be incorporated into the next version (version 1): The operating position is to be filled by a person holding the appropriate level certification. For Example; a person that is acting as the Reliability Coordiator will need to hold a Reliability Coordinator Operator Certification and a person acting as a Transmission Operator would need to hold a Transmission Operator Certification. | Doug Hils | Cinergy
32 |  |  | The "Effective Date" is listed as February 8, 2004, which is an error, it should be February 8, 2005. | Doug Hils | Cinergy | Corrected.
32 |  |  | “Operating Personnel in positions that are directly responsible for complying with NERC.” | Guy Zito | NPCC
32 |  | R1.2 | “Positions that are directly responsible for complying with NERC.” Should be changed to; | Guy Zito | NPCC
32 |  |  | A reference of Policy 8C Standard 2 needs to be mentioned. | Guy Zito | NPCC | References corrected.
32 |  |  | Operating Position certification also is not a measurement in the new Operating Policy translation but P8T2 requires such reporting. | Guy Zito | NPCC
32 |  |  | R1’s existing document references have been given as Policy 8C Requirements 1, 1.1 and 1.2 whereas these requirements do NOT exist in the original Policy 8C. In fact, the Version 0 standard 032 Requirement R1 has been derived from Policy 8C Standard 1. | Guy Zito | NPCC | References corrected.
32 |  |  | Requirement should apply only to positions that are directly responsible for complying with NERC. Please clarify | Guy Zito | NPCC
32 |  |  | To be consistent with the existing template P8T2 | Guy Zito | NPCC
32 |  | R1 | Exelon Corporation suggests that Version 1 of this Standard be initiated to address the requirement to have NERC Certified Operators that perform functions that are formally delegated similar to the requirement of Policy 9B Req. 3. | John Blazekovich | Exelon
32 |  |  | Measure could be that one has documentation of Certification of all personnel. | Mike Kormos | PJM
32 |  | M1 | The MEASUREMENT seems to be a Requirement (shall have certified personnel) | Mike Kormos | PJM
32 |  | R1 | Policy 8C Standard 1 is satisfactorily represented by Standard 032 Requirement 1. However, their was a one word change from "both" to "either", that can change the meaning of the statement, depending upon interpretation. In the interest of keeping the continuity between Policy 8C and Standard 32, the wording should be kept consistant and any changes be make through the normal process as part of version 1. | Paul Rocha | CenterPoint
32 |  | M1 | Policy 8C Standard 2 exception is satisfactorily represented by Standard 032 Measurement 1. | Paul Rocha | CenterPoint
32 |  | R1 | Suggestion to be incorporated into the next version (version 1): The operating position is to be filled by a person holding the appropriate level certification. For Example; a person that is acting as the Reliability Coordiator will need to hold a Reliability Coordinator Operator Certification and a person acting as a Transmission Operator would need to hold a Transmission Operator Certification. | Paul Rocha | CenterPoint
32 |  |  | The "Effective Date" is listed as February 8, 2004, which is an error, it should be February 8, 2005. | Paul Rocha | CenterPoint | Corrected.
32 |  |  | “Operating Personnel in positions that are directly responsible for complying with NERC.” | Pete Henderson | IMO
32 |  | R1.2 | “Positions that are directly responsible for complying with NERC.” Should be changed to; | Pete Henderson | IMO
32 |  |  | It should be consistent with the existing template P8T2 | Pete Henderson | IMO
32 |  |  | Operating Position certification also is not a measurement in the new Operating Policy translation but P8T2 requires such reporting. | Pete Henderson | IMO
32 |  |  | R1’s existing document references have been given as Policy 8C Requirements 1, 1.1 and 1.2 whereas these requirements do NOT exist in the original Policy 8C. In fact, the Version 0 standard 032 Requirement R1 has been derived from Policy 8C Standard 1. | Pete Henderson | IMO
32 |  |  | Reference to Policy 5B Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
32 |  |  | Reference to Policy 5B Requirement 1 is missing. | Pete Henderson | IMO | References corrected.
32 |  | R1 | The original Policy language stated that NERC-certified staffing should occur for positions that meet both criteria while changing the Version 0 Standard to say "either" changes the intent of the original policy. TXU Electric Delivery proposes that the Version 0 require meeting both criteria and any changes should be taken up with the development of Version 1. | Travis Bessier | TXU
32 |  |  | Measure could be that one has documentation of Certification of all personnel. |  | PSE&G
32 |  | Existing Document References | Should include Compliance Template P8T2. |  | FRCC | Corrected.
32 |  | M1 | The MEASUREMENT seems to be a Requirement (shall have certified personnel) |  | PSE&G
32 |  | Levels of non-compliance | The measures should apply to the Reliability Authority, Balancing Authority and Transmission Operator, separately. As written, only one of the three would need to meet the criteria. Change "and" to "or". |  | PG&E
33 |  | R6 | The proposed translation appears to be much tighter than the original intent. Current language calls for the OAs and entities to ensure delegated tasks are carried out by NERC certified operators. The proposed language shifts this responsibility to the RA. | Alan Johnson | Mirant
33 |  | R8 | At the end of R8, the inability to perform the directive AND WHY should be communicated to the RA. | Brandian | ISO-NE
33 |  |  | Attachment 1 referred to in this Requirement, bullet 5 does not exist in the materials. | Brandian | ISO-NE | Corrected.
33 |  | R9 | Please clarify and provide example(s) of what is meant by the “interest of other entity”. | Brandian | ISO-NE | Version 1.
33 |  | R6 | The statement is inconsistent with the Functional Model. NPCC does not believe that in all cases an entity needs to be certified at the Reliability Authority level when they are carrying out a “delegated task”. i.e. a distribution operator carrying out load shedding on distribution feeders as delegated by the RA. | Brandian | ISO-NE | Directing shedding load is not delegation; giving LSE the authority to evaluate and order load shedding, then would be delegation and require certification.
33 |  | R2 | Reliability Plan does not have to be an individual RA plan; it can be Regional Reliability Plan. This should be made clear in the Standard | Ed Riley | CAISO | There is no restriction on this being a shared plan. This translations assumes the RC requirements shifted to the RA. Changed to "regional".
33 |  | R2 | Reliability Plan does not have to be an individual RA plan; it can be Regional Reliability Plan. This should be made clear in the Standard | Ed Riley | CAISO
33 |  | R1 | This Standard presents a challenge because of the way Reliability Coordination has been implemented in the WECC. Empowerment Agreements will need to be modified, along with funding mechanism currently in place. This will likely take a considerable length of time to agree upon and then transition to. | Ed Riley | CAISO
33 |  | R4 | RELIABILITY AUTHORITIES that delegate tasks to other entities shall have formal operating agreements with entity to which tasks are delegated. The RELIABILITY AUTHORITY shall verify that all delegated tasks are understood, communicated, and addressed by all BA, TO, GO, TSP, LSE and PSE within its RELIABILITY AUTHORITY AREA. All responsibilities for complying with NERC and regional standards shall remain with the RELIABILITY AUTHORITY. | Gerald Reahlt | Manitoba
33 |  |  | The translation to standards is supposed to specifically identify entities. | Gerald Reahlt | Manitoba
33 |  | R8 | At the end of R8, the inability to perform the directive AND WHY should be communicated to the RA. | Guy Zito | NPCC
33 |  | R9 | Please clarify and provide example(s) of what is meant by the “interest of other entity”. | Guy Zito | NPCC
33 |  | R6 | The statement is inconsistent with the Functional Model. NPCC does not believe that in all cases an entity needs to be certified at the Reliability Authority level when they are carrying out a “delegated task”. i.e. a distribution operator carrying out load shedding on distribution feeders as delegated by the RA. | Guy Zito | NPCC
33 |  | R1 | Exelon Corporation agrees with the logic used by the drafting team. | John Blazekovich | Exelon
33 |  |  | R2 references the NERC OC (The reference should be to the Standards Developer) | Mike Kormos | PJM | Standards Developer does not monitor compliance.
33 |  | R2 | Replace OC with STANDARDS DEVELOPER | Mike Kormos | PJM | Standards Developer does not monitor compliance.
33 |  |  | Attachment 1 referred to in this Requirement, bullet 5 does not exist in the materials. | Pete Henderson | IMO | Corrected.
33 |  | R1 | OK. For reference, this is taken from Section C of "Introduction to the Operating Policies." | Raj Rana | AEP | References corrected.
33 |  | R6 | This is not a correct translation of Policy 9 B R3. The Policy says that the entity that has been delegated a reliability coordinator task must ensure that the tasks are carried out by NERC Certified Reliability Coordinator operators and that they, the delegated to entity, will have those delegated tasks audited under the NERC RC audit program. Thus, the "cop" is NERC and/or the Regions and the burden is on the delegated entity. Version 0 standard 033 R6 places the burden of verification on the Reliability Authority and makes him the "cop" as opposed to NERC/Regions. When the RCWG and ORS re-wrote Policy 9, they were very careful to ensure that NERC/Regions remained the "reliability standards police." The wording 033 R6 should be revised to maintain this improtant concept. | Raj Rana | AEP | NERC still certifies. This requirement is only that the RA ensure any delegated tasks are performed by a NERC-certified operator.
33 |  | 3,8 | These requirements are including the LSE and PSE as entities which qualify as Operating Authorities. Original Policy stated Operating Authority as entities such as Control Areas (BA, TO) and GO's. Has policy changed to include the PSE or LSE? | Roman Carter | Southern Company
33 |  | Applicability | Because there is information that must be provided to the Reliability Authority for other entities, the Transmission Operator and Balancing Authority should be included in the applicable entities list. No references should be made to entities other than the Reliability Authority, Transmission Operator, or Balancing Authority. The service agreement approach as stated in other standards for defining obligations should be utilized and the requirements modified to reflect this proposed change. |  | FRCC
33 |  | General Comment | If there is a conflict between a NAESB Business Standard and a NERC Reliability Standard, the NERC Reliability Standard should always be followed. |  | FRCC | That is a policy issue outside the scope of the standards.
33 |  | R1 | OK. For reference, this is taken from Section C of "Introduction to the Operating Policies." |  |  | References corrected.
33 |  |  | R2 references the NERC OC (The reference should be to the Standards Developer) |  | PSE&G | Standards Developer does not monitor compliance.
33 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Responsibilities, Authorities, and agreements. |  | FRCC | Changed back to RC.
33 |  | R2 | Replace OC with STANDARDS DEVELOPER |  | PSE&G | Standards Developer does not monitor compliance.
33 |  |  | Std 33, R8 - It appears the Reliability Authority (RA) will have agreements not only with the Balancing Authority (BA) and Transmission Operator (TO) as today, but also the Transmission Provider, Generation Owner, Generation Operator and Load Serving Entity. Requiring an agreement with the Generation Owner, Generation Operator and Load Serving Entity is a new twist. The reason for our interpretation is Policy 9 redline, A, 1.2 requires the RA to have clear decision making authority to act and to direct actions to be taken by BA, TO, Transmission Provider (TP), Generation Owner (GOw), Generation Operator (GOp), Load Serving Entity (LSE), and the Purchasing and Selling Entity (PSE). Several other sections refer to these same model entities in dealing with reliability. However, it appears to us from this re-write is the only two model entities that really provide any assistance to the RA are the TO and BA. Therefore, we question why the other model entities were required to have an agreement with the RA? |  | Southern Company
33 |  | R6 | This is not a correct translation of Policy 9 B R3. The Policy says that the entity that has been delegated a reliability coordinator task must ensure that the tasks are carried out by NERC Certified Reliability Coordinator operators and that they, the delegated to entity, will have those delegated tasks audited under the NERC RC audit program. Thus, the "cop" is NERC and/or the Regions and the burden is on the delegated entity. Version 0 standard 033 R6 places the burden of verification on the Reliability Authority and makes him the "cop" as opposed to NERC/Regions. When the RCWG and ORS re-wrote Policy 9, they were very careful to ensure that NERC/Regions remained the "reliability standards police." The wording 033 R6 should be revised to maintain this improtant concept.
34 |  | R3 | Believe the proposed change weakens the standard as the current language specifies use of the ISN or RCIS. | Alan Johnson | Mirant
34 |  | R1 | NPCC’s participating members believe this is appropriately in this Standard and NOT in 029. | Brandian | ISO-NE
34 |  | R7 | Please clarify/define what constitutes “adequate” analysis tools and “wide-area overview”. | Brandian | ISO-NE
34 |  | R5 | Please clarify/define what is ”synchronized information system.” | Brandian | ISO-NE
34 |  | R3 | The drafting team posed a question regarding whether TOs and BAs had an obligation to supply RA info. through SDX. This is not in existing policy and NPCC believes this is “out of the scope” of the version zero effort. | Brandian | ISO-NE
34 |  | R8 | “The RELIABILITY AUTHORITY shall have provisions for backup facilities that shall be exercised if the main monitoring system is unavailable.”Not clear in this Standard or Policy 9 if this requirement is for a backup facility or a backup EMS. The RELIABILITY AUTHORITY shall ensure SOL and IROL monitoring and derivations continue if the main monitoring system is unavailable. | Ed Riley | CAISO
34 |  | R1 | Should be moved to Standard 29. | Ed Riley | CAISO
34 |  | R3 | Should be moved to Standard 29. As for the Drafting teams question “Do TO’s & BA’s have obligations to supply RA’s through the NERC SDX?” The SDX should not become a poor man’s ISN, although this is an Eastern Interconnection issue and of no consequence to WECC operations. | Ed Riley | CAISO
34 |  |  | A clearer version of this requirement may be: Upon request, RELIABILITY AUTHORITIES shall, via the ISN, exchange with each other operating data that is necessary to allow the RELIABILITY AUTHORITIES to perform their operational reliability assessments and coordinate their reliable operations. RELIABILITY AUTHORITIES shall share with each other the types of data as listed in Attachment A, unless otherwise agreed to. | Gerald Reahlt | Manitoba
34 |  |  | Agree with comments. | Gerald Reahlt | Manitoba
34 |  |  | Disagree with comments, standard 029 deals with telecommunications not type of data required. | Gerald Reahlt | Manitoba
34 |  |  | How does Appendix 4B, “Electric System Security Data, Section A, Electric System Security Data”, tie into this requirement? | Gerald Reahlt | Manitoba
34 |  |  | I agree with the highlighted section but the statement precludes the Balancing Authorities and Transmission Operators which need to be included as in R3. | Gerald Reahlt | Manitoba
34 |  |  | Related to Standard 029. | Gerald Reahlt | Manitoba
34 |  |  | requirements to support its reliability coordination tasks and shall request such data from its BALANCING AUTHORITIES, TRANSMISSION OPERATORS, TRANSMISSION OWNERS, GENERATION OWNERS, GENERATION OPERATORS, and LOADSERVING ENTITIES or ADJACENT RELIABILITY AUTHORITIES. | Gerald Reahlt | Manitoba
34 |  |  | The Drafting Team asks: do TRANSMISSION OPERATORS and BALANCING AUTHORITIES have obligations to supply RELIABILITY AUTHORITY information through the NERC SDX? | Gerald Reahlt | Manitoba
34 |  | R2 | The RELIABILITY AUTHORITY shall determine the data | Gerald Reahlt | Manitoba
34 |  |  | They have to supply data to their Reliability Authority through a secure network. | Gerald Reahlt | Manitoba
34 |  |  | This requirement could be moved to Standard 029. | Gerald Reahlt | Manitoba
34 |  | R1 | NPCC’s participating members believe this is appropriately in this Standard and NOT in 029. | Guy Zito | NPCC
34 |  | R7 | Please clarify/define what constitutes “adequate” analysis tools and “wide-area overview”. | Guy Zito | NPCC | Version 1.
34 |  | R5 | Please clarify/define what is ”synchronized information system.” | Guy Zito | NPCC | This is a term currently used in policy - clarify in Version 1.
34 |  | R3 | The drafting team posed a question regarding whether TOs and BAs had an obligation to supply RA info. through SDX. This is not in existing policy and NPCC believes this is “out of the scope” of the version zero effort. | Guy Zito | NPCC
34 |  | R3 | Although the NERC Reliability Coordinator Reference Document currently states that the "Control Area" is the entity required submit the data to the SDX, Exelon Corporation believes that including the Transmission Operator and Balancing Authorities is a reasonable and logical interpretation. | John Blazekovich | Exelon
34 |  | R1 | It is not clear whether the drafting team is suggesting that the requirements are redundant and should be deleted or more suitably moved to Standard 029. Exelon Corporation would prefer to see the requirements moved into Standard 029 and any redundancies removed. | John Blazekovich | Exelon
34 |  | R1 | It is not clear whether the drafting team is suggesting that the requirements are redundant and should be deleted or more suitably moved to Standard 029. Exelon Corporation would prefer to see the requirements moved into Standard 029 and any redundancies removed. | John Blazekovich | Exelon
34 |  |  | R7 - adequate analysis tools is not a 'crisp' requirement | Mike Kormos | PJM | Version 1.
34 |  | R7 | Requirements must be practical | Mike Kormos | PJM | Version 1.
34 |  | R1 | This should also be addressed in std 029. | Pete Henderson | IMO
34 |  | R-3 | A provision should be added to this requirement that the data be provided/exchanged “as requested”. |  | FRCC
34 |  | Applicability | Because there is information that must be provided to the Reliability Authority for other entities, the Transmission Operator and Balancing Authority should be included in the applicable entities list. |  | FRCC
34 |  |  | R7 - adequate analysis tools is not a 'crisp' requirement |  | PSE&G | Version 1.
34 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Facilities |  | FRCC | Changed back to RC.
34 |  | R7 | Requirements must be practical |  | PSE&G | Version 1.
35 |  |  | R3 - shall KNOW of all facilities that COULD result in IROL. This is not a 'crisp' requirement | Mike Kormos | PJM
35 |  | R3 | Requirements must be practical | Mike Kormos | PJM
35 |  | R1 | Change "The RELIABILITY AUTHORITY shall monitor all BULK ELECTRIC SYSTEM facilities, including sub-transmission information, within its RELIABILITY AUTHORITY AREA . . ." to "The RELIABILITY AUTHORITY shall monitor all BULK ELECTRIC SYSTEM facilities, and sub-transmission information, within its RELIABILITY AUTHORITY AREA . . ." The "including sub-transmission" phrase implies that sub-transmission faciltities is a subset of Bulk Electric System faciltites, which is not always true. | Raj Rana | AEP | Changed to "may include"
35 |  | 1 | The original policy says the RC shall monitor all Bulk Electric System facilities within its RC area, etc. However, under the V-0 Std the words "including sub-transmission information" was added. This appears to be a new requirement and, thus, a Policy change which is not appropriate under V-0. The phrase in quotes above should be removed. The original policy had the RC MAY require sub-transmission info be received. Big difference. | Roman Carter | Southern Company
35 |  | R1 | Change "The RELIABILITY AUTHORITY shall monitor all BULK ELECTRIC SYSTEM facilities, including sub-transmission information, within its RELIABILITY AUTHORITY AREA . . ." to "The RELIABILITY AUTHORITY shall monitor all BULK ELECTRIC SYSTEM facilities, and sub-transmission information, within its RELIABILITY AUTHORITY AREA . . ." The "including sub-transmission" phrase implies that sub-transmission faciltities is a subset of Bulk Electric System faciltites, which is not always true. |  |  | Changed to "may include"
35 |  |  | R3 - shall KNOW of all facilities that COULD result in IROL. This is not a 'crisp' requirement |  | PSE&G
35 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Wide Area View |  | FRCC
35 |  | R3 | Requirements must be practical |  | PSE&G
35 |  | R1 | The wording here changes Policy. Policy 9 used the word “may” when referring to monitoring of sub-transmission. Version 0 has replaced this with “shall” making it mandatory that the RA monitor sub-transmission. This is a change in policy. |  | Southern Company
36 |  | R1 | The requirement that states that the Reliability Authority shall staff with personnel that have a Reliability Coordinator Operator Certification needs to be incorporated into Standard 032 "Operating Personnel Credentials" as opposed to standard 036. The requirements for operating personnel credentials needs to be in the one section that addresses that topic. | David Carlson | NERC PCGC
36 |  | R1 | The requirement that states that the Reliability Authority shall staff with personnel that have a Reliability Coordinator Operator Certification needs to be incorporated into Standard 032 "Operating Personnel Credentials" as opposed to standard 036. The requirements for operating personnel credentials needs to be in the one section that addresses that topic. | Doug Hils | Cinergy
36 |  | R1 | The requirement that states that the Reliability Authority shall staff with personnel that have a Reliability Coordinator Operator Certification needs to be incorporated into Standard 032 "Operating Personnel Credentials" as opposed to standard 036. The requirements for operating personnel credentials needs to be in the one section that addresses that topic. | Paul Rocha | CenterPoint
36 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Staffing |  | FRCC
36 |  | R1 | The requirement for 24/7/365 staffing should apply to Balancing Authority and Transmission Operator, as well. |  | PG&E
36 |  |  | The training requirement is redundant with Standard 25, R2 and Standard 31, R2 and should be deleted. |  | PG&E
37 |  | R7 & R8 | Standard 037 skips R7 and R8. Is this just a numbering error? | Raj Rana | AEP
37 |  |  | Reliability Authorities shall coordinate their next-day analyses to assure consistent assumptions and boundary conditions (reasonable power flows on both ends of the same line). | Robert Snow
37 |  | 9 | Requirement uses the term "as deemed appropriate". This is subjective and can be viewed differently by Industry participants. How do you enforce? | Roman Carter | Southern Company
37 |  | 5 | States that the BA and GO's must sign Confidentiality Agreements. Is this in current Policy? | Roman Carter | Southern Company
37 |  | R8 | RAs should notify TOs and BAs about GMDs. It should be up to the BA or perhaps TO to notify their appropriate Generator Operators (not the RA). | Terry Bilke | MISO
37 |  | Applicability | Because there is information that must be provided to the Reliability Authority for other entities, the Transmission Operator , Transmission Service provider, and Balancing Authority should be included in the applicable entities list. No references should be made to entities other than the Reliability Authority, Transmission Operator , Transmission Service provider, or Balancing Authority. The service agreement approach as stated in other standards for defining obligations should be utilized and the requirements modified to reflect this proposed change. |  | FRCC
37 |  | R7 and R8 | Conversion document skips from R6 to R9 with no explanation. Is R7 and R8 left blank intentionally? |  | SRP | Corrected.
37 |  | General Comments | R7 and R8 are not included in this standard. |  | FRCC | Corrected.
37 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Operations Planning |  | FRCC | Changed back to RC.
37 |  | Compliance Monitoring Process | Self- Certification references Compliance Assessment Notes which where included in the Compliance Template P9T1 used for translation. The Drafting Team should revise this portion of the standard to reflect the requirements that are to be measured for compliance. |  | FRCC
37 |  | R7 & R8 | Standard 037 skips R7 and R8. Is this just a numbering error?
37 |  | R2 | The Existing Document References should be included to provide clarity of translation. |  | FRCC
37 |  | R4 | The Existing Document References should be included to provide clarity of translation. |  | FRCC
37 |  | Levels of Non Compliance | The Levels of Non Compliance reference requirements included in the Compliance Assessment Notes which where included in the Compliance Template P9T1 used for translation. The Drafting Team should revise this portion of the standard to reflect the requirements that are to be measured for compliance. |  | FRCC | Requirement was stated as a shall statement.
38 |  | R11 | Under the Functional Model, don't see the RA working directly with the GOP. Should be communicating with the TOP and BA, who then communicates with the GOP. | Alan Johnson | Mirant
38 |  | R17 | The Drafting Team comment appears to be making an incorrect reference. The correct reference is to Std 019. NPCC, at this juncture, does not agree to consolidate at this time. | Brandian | ISO-NE
38 |  | R1 | 1.3.9 Planned generation dispatches: The term “generation dispatches” needs clarification; does this mean the AGC set points? Generation hourly schedules? This level of detail is best left to the BA. | Ed Riley | CAISO
38 |  | R17 | R17 is about issuing directives, but in the comments section I find this statement; ”This requirement is identical to one in Standard 029 and should be deleted in Version 0. R17 is NOT included in S-029, which is about telecommunications. | Ed Riley | CAISO
38 |  | R10, R11, R12 | Regarding directing BA’s to return to CPS and DCS compliance, what Standard (or Policy) will empower the RA to do this? The BA could tell the RA “I’m having a bad CPS day, but I will be O.K. for the year (CPS1) and the month (CPS2)” Is the RA expected to direct the TO they must manually shed load to help the BA meet DCS? At what point in the post disturbance recovery does the RA issue this directive? T+15? Or T+10 so no violation occurs? These actions, if that is what this Standard is saying, will require re-writing the Empowerment Agreements that are currently in place, which will be a lengthy process with uncertain results. | Ed Riley | CAISO | We translated existing policy; these are issues with the policy.
38 |  |  | COORDINATOR to act as the Interconnection Time Monitor to monitor time error for each of the | Gerald Reahlt | Manitoba
38 |  |  | Disagree with comments. | Gerald Reahlt | Manitoba
38 |  |  | Is this new? I cannot find anything that translates to this. | Gerald Reahlt | Manitoba
38 |  | R7 | Only the INTERCONNECTION TIME MONITOR shall be able to issue a modifyied scheduled Interconnection frequency to implement a time error correction, and only a RELIABILITY AUTHORITY can be the Interconnection Time Monitor. | Gerald Reahlt | Manitoba
38 |  |  | Policy 1 D intro The Operating Reliability Subcommittee shall designate, on February 1st of each year, a RELIABILITY | Gerald Reahlt | Manitoba
38 |  |  | Policy 9E - Current-Day OperationsStates that all resources, including load shedding shall be available to the Reliability Authority. | Gerald Reahlt | Manitoba
38 |  |  | The meaning changes when you say “shall be able to utilize” as opposed to “shall be available to”. | Gerald Reahlt | Manitoba
38 |  | R3 | The RELIABILITY AUTHORITY shall be able to utilize all resources, including load shedding, in addressing a potential or actual IROL violation. | Gerald Reahlt | Manitoba
38 |  | R17 | The RELIABILITY AUTHORITY shall issue directives in a clear, concise, definitive manner. The RELIABILITY AUTHORITY shall receive a response from the person receiving the directive that repeats the information given. The RELIABILITY AUTHORITY shall acknowledge the statement as correct or repeat the original statement to resolve misunderstandings. | Gerald Reahlt | Manitoba
38 |  |  | This requirement is identical to one in Standard 029 and should be deleted in Version 0. | Gerald Reahlt | Manitoba
38 |  | R17 | The Drafting Team comment appears to be making an incorrect reference. The correct reference is to Std 019. NPCC, at this juncture, does not agree to consolidate at this time. | Guy Zito | NPCC
38 |  | R17 | Exelon Corporation believes this requirement is identical to Standard 19 R4 (not Standard 29 as listed in the comments), and endorses removing the redundancy. | John Blazekovich | Exelon
38 |  | R8 | The interpretation of the Team places an added burden on the RA in that R8 requires them to notify the generation operators regarding GMD events. Today, the RC notifies the Control Areas, which notify the generation operators. Would not a better translation to the Functional Model have the RA notify the Transmission Operators and Balancing Authorities and let the Balancing Authorities notify the generation operators? | Raj Rana | AEP
38 |  | R7 | This contains a new requirement not found in current Policy and thus should be modified. Existing Policy 9 E Requirement 1.4.5 does not state that only a Reliability Coordinator can be the Interconnection Time Monitor, thus R7 should have such statement removed. It should only state: "Only the INTERCONNECTION TIME MONITOR shall be able to modify scheduled Interconnection frequency to implement a time error correction." The NERC OC presently approves the selection of the Interconnection Time Monitor based upon the ORS's recomme dation. If it is desired to change Policy such that only an RA can perform this fucntion, then such change should go through the Standards Process. | Raj Rana | AEP
38 |  | 15 | Same as above in Standard 033. | Roman Carter | Southern Company
38 |  | 7 | This requirement does not appear to come directly from Policy 9E 1.4.5 as the Standard says. The requirement is not the same as original Policy. | Roman Carter | Southern Company
38 |  | Applicability | Any references to Generation Operators, Generator Operators, Load-Serving Entities, and Purchasing-Selling Entities should be removed from the requirements of this standard. The service agreement approach as stated in other standards for defining obligations should be utilized and the requirements modified to reflect this proposed change. |  | FRCC
38 |  | R17 | Concur with comment. |  | PG&E
38 |  | R19 | Policy 9C is referenced here when in fact it should be 9E |  | Southern Company
38 |  | R15 | Recommend the following revision to properly reflect applicable entities: |  | FRCC
38 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Current Operations |  | FRCC
38 |  | Drafting Team Comments - R17 | The Drafting team stated that this requirement was identical to one in Standard 029 and should be deleted . It is important that no changes are made to existing policy with the translation to Version 0.The removal of redundancy should be considered in Version 1. |  | FRCC
38 |  | R8 | The interpretation of the Team places an added burden on the RA in that R8 requires them to notify the generation operators regarding GMD events. Today, the RC notifies the Control Areas, which notify the generation operators. Would not a better translation to the Functional Model have the RA notify the Transmission Operators and Balancing Authorities and let the Balancing Authorities notify the generation operators? |  |  | Corrected.
38 |  | 7 | The requirements here do not appear to come out of current NERC policy. This appears to be an instance where Version 0 is attempting to make policy. |  | Southern Company | Requirements come from policy 1 and have been moved to standard 004 for a better fit with policy.
38 |  | R7 | This contains a new requirement not found in current Policy and thus should be modified. Existing Policy 9 E Requirement 1.4.5 does not state that only a Reliability Coordinator can be the Interconnection Time Monitor, thus R7 should have such statement removed. It should only state: "Only the INTERCONNECTION TIME MONITOR shall be able to modify scheduled Interconnection frequency to implement a time error correction." The NERC OC presently approves the selection of the Interconnection Time Monitor based upon the ORS's recomme dation. If it is desired to change Policy such that only an RA can perform this fucntion, then such change should go through the Standards Process.
39 |  | R2 | After "For a transmission system", insert " that is experiencing a potential or actual SOL or IROL violation" | Alan Johnson | Mirant
39 |  | R2 | The specifics of the WECC Unscheduled Flow Mitigation Plan are governed by a contract amongst WECC members that has been filed with FERC. This contract provides for a specific committee to manage all operational aspects of this Unscheduled FLow Relief Plan. Therefore, we feel that the WECC UFMP should remain a WECC Regional Curtailment Procedure and NOT be included as a part of Version 0 standards. | Deanna Phillips | BPA
39 |  | Purpose | Should be changed to “…until adequate relief is obtained through the use of any Interconnection wide, Regional, Interregional or subregional congestion relief process.” | Ed Riley | CAISO
39 |  | R7 | The column “Existing Document References” lists Policy 9F4, which is about interconnection frequency error. It appears that this Standard is taken from Policy 9F3.1, 9F3.2, and 9F3.3, with TO used in place of RA. | Ed Riley | CAISO | References corrected.
39 |  |  | 1.1 Selecting transmission loading relief procedure. The RELIABILITY COORDINATOR experiencing a potential or actual SOL or IROL violation on the transmission system within its RELIABILITY COORDINATOR AREA shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or an INTERCONNECTION-wide procedure, such as those listed in Appendix 9C1, 9C2, or 9C3 | Gerald Reahlt | Manitoba
39 |  |  | Changing from Reliability Coordinator to Transmission Operator changes the requirement rather than translating it. | Gerald Reahlt | Manitoba | Changed back to RC.
39 |  | Levels of non compliance | Complying with interchange policies. During the implementation of relief procedures, and up to the point that emergency action is necessary, RELIABILITY AUTHORITIES and operating entities shall comply with the Interchange Scheduling Standards. | Gerald Reahlt | Manitoba
39 |  |  | Operating entities should be specified. | Gerald Reahlt | Manitoba
39 |  | R7 | The TRANSMISSION OPERATOR experiencing a potential or actual SOL violation on the transmission system within its AREA shall, at its discretion, select from either a “local” (Regional, Interregional, or subregional) transmission loading relief procedure or may request it’s RELIABILITY AUTHORITY to issue an INTERCONNECTION-wide procedure. | Gerald Reahlt | Manitoba
39 |  |  | The reference should be Policy 9F Requirement 3.1 and 3.4 instead of Requirement 4 | Guy Zito | NPCC
39 |  |  | M1 - The MEASUREMENT seems to be a Requirement (shall conduct an investigation) Measure could be that one has evidence that IROL was relieved in 30 minutes. | Mike Kormos | PJM
39 |  |  | R4 references the NERC OC (The reference should be to the Standards Developer) | Mike Kormos | PJM | Standards Developer does not measure compliance.
39 |  | R4 & M1 | Replace OC with STANDARDS DEVELOPER | Mike Kormos | PJM | Standards Developer does not measure compliance.
39 |  | R7 | What is the correct reference for this requirement? You list Polciy 9F Requirement 4 but that is incorrect. I can not find the R7 requirement as worded anywhere in existing Policy and thus recommend R7 be deleted. | Raj Rana | AEP | Reference corrected.
39 |  | 7 | It appears that the V-0 team used Policy 9F from an earlier version for developing this requirement. When comparing requirement 7 to Policy 9 posted on the NERC website which was approved on June 15, 2004, they do not match. Does the V-0 need to revise this requirement to match the most current Policy or make this Standard dependent on a version of Policy that is no longer applicable, which is what has taken place here. | Roman Carter | Southern Company
39 |  |  | The majority of Policy 9.C.1.1 seems to have been omitted from the Version 0 Standards and a comment box in the Operating Policies Markup asks whether potential SOLV's can be forecast. Version 0 should not omit these requirements. Potential SOLV's can be identified. Version 1 should address and clarify concerns expressed in comment box. | Travis Bessier | TXU | Need to check where this went
39 |  |  | M1 - The MEASUREMENT seems to be a Requirement (shall conduct an investigation) Measure could be that one has evidence that IROL was relieved in 30 minutes. |  | PSE&G
39 |  | Levels of Non | Need introduction added that states the following: |  | FRCC
39 |  |  | R4 references the NERC OC (The reference should be to the Standards Developer) |  | PSE&G
39 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - Transmission Loading Relief |  | FRCC
39 |  | R4 & M1 | Replace OC with STANDARDS DEVELOPER |  | PSE&G
39 |  | Purpose | The existing policy used for translation to Version 0 was modified. It is important that no changes are made to existing policy with the translation to Version 0. This modification should be considered in Version 1. |  | FRCC
39 |  | R7 | We cannot find where in current policy this requirement comes from. This appears to be an instance where Version 0 is attempting to make policy. |  | Southern Company
40 |  |  | Disagree with comments, this requirement is not stated in standard 027. | Gerald Reahlt | Manitoba
40 |  | R1 | The RELIABILITY AUTHORITY shall be aware of the restoration plan of each TRANSMISSION OPERATOR in its RELIABILITY AUTHORITY AREA in accordance with NERC and regional requirements. | Gerald Reahlt | Manitoba
40 |  |  | This requirement is redundant with Standard 027. | Gerald Reahlt | Manitoba
40 |  |  | Exelon Corporation would not have any issues with combining Standard 040 and 027. | John Blazekovich | Exelon
40 |  |  | Exelon Corporation would not have any issues with combining Standard 040 and 027. | John Blazekovich | Exelon
40 |  | Title | References Reliability Coordination, but should reference, Reliability Authority - System Restoration |  | FRCC
14 - 017 |  |  | Standards need to line up better with functional model. These are Transmission planning standards for the most part and should be included in the Planning Standards not Operating Standards. Also, the guidelines should be considered for additions as standards as they reflect good business practices. | Ray Morella | FirstEnergy
14, 19, 24 |  |  | For many TAPS members, the reporting under 014 (and 016,017,018,019,024 & 065) would be a new burden. | Gayle Mayo | TAP
14, 19, 24 |  | Applicability | The hierarchy of the Functional Model requires Generator Operators to report to BAs and TOs even though they may not be required to do this today through reliability rules. Most small generator operators are obigated to provide information through service agreements, only. | Gayle Mayo | TAP
14, 19, 24 |  | Continued | The translation to Version 0 should cover current standards and not add new requirements. | Gayle Mayo | TAP
16 - 18 |  | various | For impact on TAPS small generator operators see discussion above. This provision also can add a new burden to Distribution Providers such as municipals, cooperatives and members of Joint Action Agencies. The small utilities may depend upon others for reliability conformance such as load shedding. | Gayle Mayo | TAP
16 - 18 |  | Continued | Since Version 0 is not supposed to change existing rules, this translation to the Functional Model needs to be revised to not place extra burdens on Distribution Providers. For Version 1 of NERC standards, there ought to be flexibility in how smaller distribution utilities participate. There could be a cut-off size thereby exempting small distribution utilities from requirements that do not add to reliability. | Gayle Mayo | TAP
22 - 23 |  |  | Still refers to System Operators. This classification is not in the functional model. | Ray Morella | FirstEnergy
24 - 25 |  |  | These standards appear to assume that Balancing Authority is equivalent to Control Area. Also, the term NERC operating policies needs changed to NERC Standards. | Ray Morella | FirstEnergy
33 - 40 |  |  | In comparing Policy 9 to Standards 33 – 40 in Version 0, it was determined that the following requirements of Policy 9 were either omitted from Version 0, or not translated clearly enough for me to make a connection: |  | TVA
33, 18 |  | R8 & R3 | There is duplication or redundancy of requirements between policy 5 and 9. Standard 033 Requirement 8 and Standard 018 Requirement 3 appear to be the same. | Brandian | ISO-NE
33, 18 |  | R8 & R3 | There is duplication or redundancy of requirements between policy 5 and 9. Standard 033 Requirement 8 and Standard 018 Requirement 3 appear to be the same. | Guy Zito | NPCC
33, 18 |  | R8 & R3 | There is duplication or redundancy of requirements between policy 5 and 9. Standard 033 Requirement 8 and Standard 018 Requirement 3 appear to be the same. | Pete Henderson | IMO
33, 18 |  | R8 & R3 | There is duplication or redundancy of requirements between policy 5 and 9. Standard 033 Requirement 8 and Standard 018 Requirement 3 appear to be the same. | Pete Henderson | IMO
34, 15 |  | 3,3 | Policy states information should be exchanged through a secure network, via the ISN. | Roman Carter | Southern Company
42 - 43 |  |  | Training requirements should apply to all industry entities. | Ray Morella | FirstEnergy
7, 017, 018, 019, 021, 022, 023, 024 |  | Measures: Compliance Monitoring Process, -Levels of Non Compliance | Note that the associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing from the above noted standards. We suggest that these standards should be reassessed in near future to determine the requirements for their associated measures and levels of non-compliance. Accordingly, these should then be specified where applicable | Pete Henderson | IMO
7, 8 |  | Definitions | The terms System Operating Limits (SOL) and Interconnected Reliability Operting Limit (IROP) need definition either in a glossary or in the standard. | Gayle Mayo | TAP | Included in glossary posted with Draft 2.
ALL |  |  | Note that the Markup version of the Policy provided doesn't match the Policy currently in use. Certain terms have been replaced (CA by BA, TP by TSP), footnotes have been dropped (e.g. Footnote 1 on the first page of the current Policy 3), and some sections changed without explanation (Policy 3A Section 2.2). As a result, I have no confidence that the Markup Policy can be trusted as a true representation of Current Policy.
General |  |  | Levels of Non-Compliance - there is need of a higher level review consistency of the levels of non-compliance for the measures that involve multiple items that must be complied with. In some instances, for example, the levels are identified as: L1 - one of eight requirements not met; L2 - two of eight, etc.; In other instances, we have L1 - N/A; L2 - Less than 2 of 8 requirements not met; L3 - N/A; L4 - More than 2 of 8 not met. Overall consistency desired. | Charles Matessa | BG&E
General |  | ALL | Where possible, please give each Requirement and Measure a descriptive name (i.e. access to contingency reserves, having contingency reserve policies, deployment of contingency reserves, DCM compliance, etc). This will assist operators to be better able to discern which requirement and measure is which and be able to find the specific one(s) that are applicable most quickly and efficiently. | Deanna Phillips | BPA
General |  |  | "Standards" without measures should not be standards as it is not possible to identify compliance/ non - compliance. This should be addressed in Version 1. | Ed Riley | CAISO
General |  |  | There is an inconsistent usage of capitalization in Standards 20-29 in phrases such as Transmission Operator, Generator Operator, Reliability Authority, and Balancing Authority. | Ed Riley | CAISO
General |  |  | For Version 1, NERC rules ought to have a cut-off size where small generators would be exempt. In addition, generation behind the meter should be exempt. | Gayle Mayo | TAP
General |  |  | At a recent Resources Subcommittee meeting, the RS interpreted the second contingency rule to exclude off line resources that were activated to provide contingency reserve. Basically, if a resource is started up to provide contingency reserve and trips off while providing it, this is not a second contingency. This was always the intent, and to add a sentence now to make it explicit would be useful and is not a change in policy. | Guy Zito | NPCC | This would require a Version 1 change.
General |  |  | In the existing policy the overall role of monitoring of SOL or IROL was assigned to a Control Area. In the applicable version 0 standards a clarification on the role and relationship between Reliability Authority and Transmission Operator should be made with regards to the monitoring of SOL & IROL. standard 7, R-3 | Guy Zito | NPCC
General |  |  | NPCC believes that in the Planning Translations, the removal of the S1, S2 etc. language has introduced vagaries to the Standards that may lead to misinterpretations. NPCC suggests that the drafting team review each translation and consider the reintroduction of the “S” statement from the existing Templates to provide clarity and recapture details that may have been lost in this translation. NPCC suggests the “S” statement language appear at the beginning of the Requirement Section for each Standard. | Guy Zito | NPCC
General |  |  | NPCC's participating members suggest that with regards to Version 0 standards, an updated glossary of terms and definitions should be developed and made available to the industry. | Guy Zito | NPCC
General |  |  | Overall the NPCC's participating members support the NERC Version 0 Reliability Standards and the efforts of NERC-SDT involved in it. | Guy Zito | NPCC
General |  |  | std 007, 017, 018, 019, 021, 022, 023, 024 -Measures: Compliance Monitoring Process, Note that the associated Measure, Compliance Monitoring Process and Levels of Non Compliance are missing from the above noted standards. We suggest that these standards should be reassessed in near future to determine the requirements for their associated measures and levels of non-compliance. Accordingly, these should then be specified where applicable and considered necessary. | Guy Zito | NPCC
General |  |  | These Standards must clearly identify, define and provide examples of what a SOL and IROL are. The reason for this is that this is not consistently interpreted by industry. | Guy Zito | NPCC
General |  |  | We suggest that in version 0 standard, a reference or a link to the associated NAESB BPS should also be provided, as and where applicable (especially in standards related to Policy ). | Guy Zito | NPCC
General |  |  | ** Table I: Comments related to either missing or inconsistent references. | Pete Henderson | IMO
General |  |  | In the existing policy the overall role of monitoring of SOL or IROL was assigned to a Control Area. In the applicable version 0 standards a clarification on the role and relationship between Reliability Authority and Transmission Operator should be made with regards to the monitoring of SOL & IROL. standard 7, R-3 | Pete Henderson | IMO
General |  |  | Overall we support the NERC Version 0 Reliability Standards and the efforts of NERC-SDT involved in it. | Pete Henderson | IMO
General |  |  | Please note that the comments in Table I below are based on the original posting of Ver 0 Operating Standards-matrix. A few of the concerns mentioned below may have already been addressed/corrected in later published reference document (re: operating policy mark-ups). This information is provided to facilitate NERC SDT for its purposes. | Pete Henderson | IMO
General |  |  | We suggest that in version 0 standard, a reference to the associated NAESB BPS should also be provided, as and where applicable (especially in standards related to Policy 3). | Pete Henderson | IMO
General |  |  | We suggest that with regards to Version 0 standards, an updated glossary of terms and definitions should be developed and made available to the industry. | Pete Henderson | IMO | Provided in Draft 2.
General |  |  | Note that the Markup version of the Policy provided doesn't match the Policy currently in use. Certain terms have been replaced (CA by BA, TP by TSP), footnotes have been dropped (e.g. Footnote 1 on the first page of the current Policy 3), and some sections changed without explanation (Policy 3A Section 2.2). As a result, I have no confidence that the Markup Policy can be trusted as a true representation of Current Policy. | Raj Rana | AEP
General |  |  | Policy 9C R1.2: Determining IROLs. The Version 0 Standards state that the RA must determine IROLs. But, what is missing is the piece from 9C R1.2 that states "determine IROLs based on local, regional, and interregional studies." This is a minor ommission in my opinion. | Raj Rana | AEP
General |  |  | Policy 9J R1.3: Standards of Conduct. I believe this to be a significant omission. 9J R1.3 requires the RA to sign and adhere to the NERC Reliability Coordinator Standards of Conduct, as listed in the NERC Operating Manual. One could argue that the RA certification standards will adress this issue, which is true. However, the RA certification standards have not been approved nor implemented. Thus, correct conversion of existing Policy would require inclusion of 9J R1.3 at this time. When the RA certification standards are approved, they would replace this provison in the Version 0 standards. | Raj Rana | AEP
General |  |  | SDX, Tagging, etc. should also be an acceptable means or other prevailing NERC sponsored exchange mechanism for a required type of perational data. | Roman Carter | Southern Company
General | Various | Various | MEC supports the detailed comments provided by MAPP in response to Question 13 with the exception of the MAPP comment on Standard 059. For brevity, MEC does not repeat the comments on the other standards here. | Tom Mielnik | MidAmerican
General |  |  | In the "Operating Policies Markup", page P1-12, The section labeled "Guides", dealing with governor droop settings, doesn't seem to show up in the V0 standard. Will this be located in a reference document or some stand-alone guide in the future? |  | Southern Company
General |  |  | In the "Operating Policies Markup", page P1-23, The section labeled 2.1.3 "FRS Surveys" doesn't seem to show up in the V0 standard. Will this be located in a reference document or some stand-alone guide in the future? |  | Southern Company
General |  |  | Some of the current Planning Standards list reporting requirements in "days" while others list it in "business days." A minor revision could be made in Version 0 to resolve this inconsistency. |  | Southern Company
General - 033 through 040 |  | Multiple | Redundancies exist with these and other Standards. The reduncancies need to be identified and eliminated. | Bill Dearing | Grant PUD
General - General |  | Measures | In many cases the measures have been removed. FOr version 0 they should be retained for clarity. An example is old policy 8A (new standard 30). The red line standard is one sentence. The measures give the details. | Alan Adamson | NY State Reliability Council
General - Operating Policies |  |  | Many of the introductions were deleted. The introductions serve as a short summary of the standard and should be included in version 0 | Alan Adamson | NY State Reliability Council | Standards do not provide background information. Needs to be in a separate reference.
General - Operating Policies |  |  | Many of the standards omit the guides. These guides provide usefull and pertinent information and should remain as part of the standsards, at least in version 0 | Alan Adamson | NY State Reliability Council
General - Operating Policies |  |  | The business items assigned to NAESB should be included in the NERC version 0 standards. NERC should not be relying on NAESB to meet the NERC defined dates. | Alan Adamson | NY State Reliability Council
General - Policy 2, Section A, 008-R4 |  | 008-R4 | Reword as “The Reliability Authority shall evaluate actions taken to address an SOL or IROL violation. If the actions taken are not appropriate or sufficient, the RA shall direct actions, as required, to the TO or BA to return the system to within limits.” | Alan Adamson | NY State Reliability Council
General - Policy 2, Section A, 009-R6 (3.2) &009-R10 (4.1) |  | 009-R6 & 009-R10 | These sections should be elaborated to address pockets of inadequate reactive reserve that are solved by an SPS after the first contingency. | Alan Adamson | NY State Reliability Council
General - Policy 2, Section A, item 1.1 |  | R2 | The term “credible nature” is overly vague. Some clearer terms or definition must be included in version 0. Waiting for version 1 will allow months of uncertainty. | Alan Adamson | NY State Reliability Council
General - Policy 4, Section A, |  | 014-R1 | Add to end of sentence “…use and generation derates” | Alan Adamson | NY State Reliability Council
General - Policy 4, Section B |  | 015-R1 | Reference is made to Attachment A and Appendix 4B yet they are not part of the red line standard. | Alan Adamson | NY State Reliability Council
General - Policy 4, Section B |  | 015-R4, Data section 5.1 | Section 5.1 refers to an Addendum A, yet that is not part of the red line standard. | Alan Adamson | NY State Reliability Council
General - Policy 4, Section C |  | 016-R1 | Add to end of first sentence “…as well as the local transmission system.” | Alan Adamson | NY State Reliability Council
General - Policy 5, Section B |  | n/a | A section should be added defining the responsibilities of the generator owners, LSEs and distribution providers to notify the transmission operator of any problems that could impact the transmission system. | Alan Adamson | NY State Reliability Council
General - Policy 5, Section D |  | Introduction item 1.1 | Replace “Operating Authorities” with “Reliability Authority and Transmission Operator” | Alan Adamson | NY State Reliability Council
General - Policy 5, Section E |  | Introduction | The term Operating Authority is obsolete. | Alan Adamson | NY State Reliability Council
General - Policy 5, Section E, Section F & Section G |  | General | Replace “System Operators” with “Transmission Operators” | Alan Adamson | NY State Reliability Council
General - Policy 6, Section A |  | 024-R4 | The LSE, TSP and GOP should coordinate with their host Transmission Operator who will be the interface with the BA. | Alan Adamson | NY State Reliability Council
General - Policy 6, Section D |  | 027-R1, R2, R3 | I disagree with the note to delete the second paragraph of the introduction. The first two sentences of the paragraph are not covered in requirements 3 and 4 as stated. | Alan Adamson | NY State Reliability Council
General - Policy 7, Section A |  | First Paragraph | What does this mean? The first part is not a sentence and the second part is a comment. Also, provide “appendix 7A” | Alan Adamson | NY State Reliability Council
General - Policy 7, Section A-D |  | General | This standard has a number of comments and questions in the red line document. It is impossible to adequately review the document when it is clearly incomplete. | Alan Adamson | NY State Reliability Council
General - Policy 8, Section A |  | 030-M1 | State the details that are to be included in the control room job description document | Alan Adamson | NY State Reliability Council
General - Surveys Standard |  | R2 | Old section 2.1.3 (FRS Surveys) is deleted without explanation except to say that it is contingent upon approval of Section C (Policy 1-003). This is unclear since section C defines how to determine and use the frequency bias and 2.1.3 specifies that the data needed to calculate the frequency bias is collected. | Alan Adamson | NY State Reliability Council
MISSING FROM VERSION 0 |  |  | Policy 9C R1.2: Determining IROLs. The Version 0 Standards state that the RA must determine IROLs. But, what is missing is the piece from 9C R1.2 that states "determine IROLs based on local, regional, and interregional studies." This is a minor ommission in my opinion.
MISSING FROM VERSION 0 |  |  | Policy 9C R1.4: Operating under known conditions. I believe this to be a significant omission. 9C R1.4 requires the RA to ensure that Transmision Operators always operate under known and studied conditions. This was added to Policy after the August 14 Blackout and needs to remain.
MISSING FROM VERSION 0 |  |  | Policy 9J R1.3: Standards of Conduct. I believe this to be a significant omission. 9J R1.3 requires the RA to sign and adhere to the NERC Reliability Coordinator Standards of Conduct, as listed in the NERC Operating Manual. One could argue that the RA certification standards will adress this issue, which is true. However, the RA certification standards have not been approved nor implemented. Thus, correct conversion of existing Policy would require inclusion of 9J R1.3 at this time. When the RA certification standards are approved, they would replace this provison in the Version 0 standards.
Policy 3A |  | introduction | Policy 3 makes a distinction (in footnote 1) between Interchange Transactions and Transactions (which can be entirely within a CA). This distinction is dropped in the Reliability Standards without explanation. | Raj Rana | AEP
Policy 3A |  | 1.4 | Policy 3A 1.4 - Receiving information about the change in a tags status is a serious reliability issue and should be included in the standard. What will happen if the responsible party is 9-5 only and the tag has to be curtailed? | Raj Rana | AEP
Policy 3A |  | 2.0 | Policy 3A 2.0 - requires adherence to Etag Spec. The Reliability Standards do not mention Etag spec. This is a dropped requirement. | Raj Rana | AEP
Policy 3A |  | 2.3 | Policy 3A 2.3 is highlighted to show that the tag format will be a NAESB issue. But 2.3.1 is highlighted to indicate that tags crossing interconnection boundaries are a Reliability Issue. These two things are inconsistent. They should both be Reliability concerns. | Raj Rana | AEP
Policy 3A |  | 1.3 | Policy 3A.1.3 - Requiring contact personnel is a serious reliability issue and should be included in the standard. | Raj Rana | AEP
Policy 3A |  | 2.5 | The confirmation of tag receipt should not be left to a business practice. If the PSE is not assured that other entities received the tag, this may cause reliabilty issues. | Raj Rana | AEP
Policy 3A |  | 4.0 | The Markup Policy drops reference to Generation Providing Entities. | Raj Rana | AEP
Policy 3A |  | 3.0 | The Markup Policy drops the requirement for specifically verifying with all Control Areas on the scheduling path. This may or may not be a problem depending on the role of the Balancing Authority. | Raj Rana | AEP
Policy 3A |  | 2.0 | The Policy Markup says the tag is the official request from the load-serving PSE to the Sink BA. The Current Policy says the tag is the official request from the PSE to the Control Areas (plural). This is a change in the requirements. | Raj Rana | AEP
Policy 3A |  | 6.0 | This section has been dropped from the Reliability Standards | Raj Rana | AEP
Policy 3A |  | 7.0 | This section has been highlighted as being a NAESB issue, but there are serious reliability implications for having a consistent practice for what to do with a tag after a curtailment has ended. The "default" action should be included in the Reliability Standard. | Raj Rana | AEP
Policy 3A |  | introduction | Policy 3 makes a distinction (in footnote 1) between Interchange Transactions and Transactions (which can be entirely within a CA). This distinction is dropped in the Reliability Standards without explanation.
Policy 3A |  | 1.4 | Policy 3A 1.4 - Receiving information about the change in a tags status is a serious reliability issue and should be included in the standard. What will happen if the responsible party is 9-5 only and the tag has to be curtailed?
Policy 3A |  | 2 | Policy 3A 2.0 - requires adherence to Etag Spec. The Reliability Standards do not mention Etag spec. This is a dropped requirement.
Policy 3A |  | 2.3 | Policy 3A 2.3 is highlighted to show that the tag format will be a NAESB issue. But 2.3.1 is highlighted to indicate that tags crossing interconnection boundaries are a Reliability Issue. These two things are inconsistent. They should both be Reliability concerns.
Policy 3A |  | 1.3 | Policy 3A.1.3 - Requiring contact personnel is a serious reliability issue and should be included in the standard.
Policy 3A |  | 2.5 | The confirmation of tag receipt should not be left to a business practice. If the PSE is not assured that other entities received the tag, this may cause reliabilty issues.
Policy 3A |  | 4 | The Markup Policy drops reference to Generation Providing Entities.
Policy 3A |  | 3 | The Markup Policy drops the requirement for specifically verifying with all Control Areas on the scheduling path. This may or may not be a problem depending on the role of the Balancing Authority.
Policy 3A |  | 6 | This section has been dropped from the Reliability Standards
Policy 3A |  | 7 | This section has been highlighted as being a NAESB issue, but there are serious reliability implications for having a consistent practice for what to do with a tag after a curtailment has ended. The "default" action should be included in the Reliability Standard.
Policy 3B |  | 3.0 | The Policy indicates that information regarding the interchange transaction tag should be provided to the RA electronically. The "electronically" requirement has been dropped in the standards and will create a serious problem with adequately communicating the information. | Raj Rana | AEP
Policy 3B |  | 4.1.2 | The requirement that Control Areas must operate such that schedules do not knowingly cause harm has been dropped. There is a note in the Markup Policy about it being the TPs responsibility, but there is no reference to where this responsibility is stated. | Raj Rana | AEP
Policy 3B |  | 4.1.1 | The requirement to adhere to Interchange Schedule standards has been dropped | Raj Rana | AEP
Policy 3B |  | 5 | This section on Maximum Scheduled Interchange has been dropped from the Reliability Standards | Raj Rana | AEP
Policy 3B |  | 3 | The Policy indicates that information regarding the interchange transaction tag should be provided to the RA electronically. The "electronically" requirement has been dropped in the standards and will create a serious problem with adequately communicating the information.
Policy 3B |  | 4.1.2 | The requirement that Control Areas must operate such that schedules do not knowingly cause harm has been dropped. There is a note in the Markup Policy about it being the TPs responsibility, but there is no reference to where this responsibility is stated.
Policy 3B |  | 4.1.1 | The requirement to adhere to Interchange Schedule standards has been dropped
Policy 3B |  | 5 | This section on Maximum Scheduled Interchange has been dropped from the Reliability Standards
Policy 3C |  | 4.0 | The Current Policy requirement to use block accounting has been dropped. | Raj Rana | AEP
Policy 3C |  | 4.0 | The Current Policy requirement to use block accounting has been dropped. | Raj Rana | AEP
Policy 3D |  | 1.0 | This section on Market Related modifications has been dropped from the Reliability Standards. | Raj Rana | AEP
|  |  | - Third point missing reference to Policy 5A Requirement 6.2. | Guy Zito | NPCC | Reference corrected.
|  |  | In 2nd paragraph, Policy 5A Requirement 5.1 does not exist. R5 is covered by Policy 5A Requirement 5. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 2A Requirement 2.1.1 does not exist. R5 is covered by Policy 2A Standard 2.1 | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.1 does not exist. R6 is covered by Policy 6A Requirement 2.1. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.2 does not exist. R7 is covered by Policy 6A Requirement 2.2. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.3 does not exist. R8 is covered by Policy 6A Requirement 2.3. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.4 does not exist. R9 is covered by Policy 6A Requirement 2.4. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.5 does not exist. R10 is covered by Policy 6A Requirement 2.5. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 2 2.6 does not exist. R11 is covered by Policy 6A Requirement 2.6. | Guy Zito | NPCC | Reference corrected.
|  |  | Policy 6A Requirement 6.6 does not exist. R20 is covered by Policy 6A Requirement 7. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5B Requirement 2 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5B Requirement 2.2 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5C Requirement 1 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5C Requirement 2.1 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5D Requirement 2 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5F Requirement 2 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5F Requirement 6 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5F Requirement 7 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5G Requirement 2 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 5G Requirement 3 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Policy 6A Requirement 6.4 is missing. | Guy Zito | NPCC | Reference corrected.
| -Levels of Non Compliance |  | Reference to Template P5T1 is missing. | Guy Zito | NPCC | Reference corrected.
|  |  | Reference to Template P6T3 is missing belonging to bulleted items 1-7. | Guy Zito | NPCC | Reference corrected.
|  |  | References to Policy 5D Requirement 3 and Requirement 4 are missing. | Guy Zito | NPCC | Reference corrected.
|  |  | References to Policy 5F Requirement 3, Requirement 3.1, Requirement 3.2 and Requirement 3.3 are missing. | Guy Zito | NPCC | Reference corrected.
|  |  | References to Policy 6A Requirement 6.3.1 and Requirement 6.3.2 are missing for points 1 and 2 respectively. | Guy Zito | NPCC | Reference corrected.
|  |  | The reference should be Policy 3B, Requirement 1 instead of Policy 3B, Requirement 4.1.3 | Guy Zito | NPCC | Reference corrected.
|  |  | Near term load forecast is an essential element for performing advanced application studies (power flow) and is a reliability requirement. The requirement should be left in the Version 0 standard. | John Blazekovich | Exelon
|  |  | WECC concerned that including TO as required for certification changes the requirement from Control Areas today. | Kenneth | WECC | The qualifiers limit applicability to Tos that have responsibility for bulk electric system operation and/or complying with NERC reliability standards.
|  |  | #2 - This requirement should reference “NERC Reliability Standards” not “NERC Planning Standards” |  | FRCC | Corrected.
|  |  | #4 – Recommend the following revision for clarity:“coordinate and cooperate” , more clarity should be included in this requirement as to which entities. |  | FRCC
|  |  | … process it uses, the Reliability Authority SHALL direct its Balancing Authorities and Transmission Operators to return the transmission system … |  | FRCC
|  |  | 1. A written current job description exists which states in clear and unambiguous language the responsibilities and authorities of each operating position of a Reliability Authority, Transmission Operator, and Balancing Authority. The position description identifies personnel subject to the authority of the Reliability Authority, Transmission Operator, and Balancing Authority. |  | FRCC
|  |  | 2. Written current job description states operating personnel are responsible for complying with the NERC Operating Policies. |  | FRCC
|  |  | 3. Written current job description is readily accessible in the control room environment to all operating personnel. |  | FRCC
|  |  | 4. Written operating procedures state that during normal operating conditions, each operating position of a Reliability Authority, Transmission Operator, and Balancing Authority has the authority to take or direct timely and appropriate real-time actions without obtaining approval from higher level personnel within each Reliability Authority, Transmission Operator, and Balancing Authority. |  | FRCC
|  |  | 5. Written operating procedures state that during emergency conditions operating personnel have the authority to take or direct timely and appropriate real-time actions, up to and including shedding of firm load to prevent or alleviate System Operating Limit violations. These actions are performed without obtaining approval from higher-level personnel within the Reliability Authority, Transmission Operator, or Balancing Authority. |  | FRCC
|  |  | Data Set is posted after the established due date. Violations will not be assessed for Data Sets posted by the scheduled dates. |  | FRCC
|  |  | evaluate system performance in accordance with Reliability Standard |  | FRCC
|  |  | Evidence that the assessment included steady-state, |  | FRCC
|  |  | Functional Model does not require T-Oper to have wide-area data, therefore R1 and R2 should be assigned to RA category. |  | PSE&G
|  |  | In addition, Requirement 4 from the existing Compliance Template P8T1 was omitted. As stated earlier, it is important that no changes are made to existing policy with the translation to Version 0.This modification should be considered in Version 1. |  | FRCC
|  |  | Is RAIS the same as the existing RCIS or SCIS? |  | FRCC | Yes.
|  |  | It seems redundant for both the Planning Authority and the Transmission Planner to provide a written summary of its plans. The Planning Authority is ultimately responsible, and should keep all the documentation. At a minimum, the wording should be changed to “or” instead of “and”. |  | FRCC
|  |  | Level 1 — The Reliability Authority, Transmission Operator, or Balancing Authority has written documentation that includes four of the five items in M1. |  | FRCC
|  |  | Level 2 — A contingency plan has been implemented and tested, but has not been reviewed in the past year, or the contingency plan has not been tested in the past year or there are no records of Shift Operating personnel training. |  | FRCC
|  |  | Level 2 — The Reliability Authority, Transmission Operator, or Balancing Authority has written documentation that includes three of the five items in M1. |  | FRCC
|  |  | Level 3 — A contingency plan has been implemented, but does not include all of the elements contained in Requirements 1–4. |  | FRCC
|  |  | Level 3 — The Reliability Authority, Transmission Operator, or Balancing Authority has written documentation that includes two of the five items in M1. |  | FRCC
|  |  | Level 4 — A contingency plan has not been developed, implemented, and tested. |  | FRCC
|  |  | Level 4 — The Reliability Authority, Transmission Operator, or Balancing Authority has written documentation that includes none of the items in M1, or the interview verification items 1 and 2 do not support the authority of each operating position within the Reliability Authority, Transmission Operator, and Balancing Authority. |  | FRCC
|  |  | NERC Interconnections: Eastern, ERCOT, Western, and associated Regional Reliability Councils |  | FRCC
|  |  | No levels of Non Compliance were included. When this information is added, the Compliance Template P9T2 should be utilized for the translation. |  | FRCC
|  |  | R1 references the NERC OC (The reference should be to the Standards Developer not to NERC and not to a committee) |  | PSE&G | Standards Developer does not measure compliance.
|  |  | Recommend the following revision to properly reflect existing policy: |  | FRCC
|  |  | Reference is Performance Standard Reference Document C 1.1.1.1 |  | FRCC | Reference corrected.
|  |  | Reference Policy 1A Requirement 2.2.1 should be Performance Standard Reference Document, 1.2.1 o |  | FRCC | Reference corrected.
|  |  | Reference Policy 1A Requirement 2.2.2 should be Performance Standard Reference Document, 1.2.2 o |  | FRCC | Reference corrected.
|  |  | Reference Policy 1A Requirement 2.2.2.1 should be Performance Standard Reference Document, 1.2.2.1 o Suggest “A Balancing Authority providing or receiving SUPPLEMENTAL REGULATION SERVICE though DYNAMIC TRANSFER shall ……. be removed from M2 and included as a requirement (see suggestion to add R5 above). • |  | FRCC | Reference corrected.
|  |  | Review of this standard could not be competed because portions of this standard were not included in the Version 0 packet: Attachment 1, page 2 etc. |  | FRCC
|  |  | Self-certification: The Reliability Authority, Transmission Operator, and Balancing Authority shall annually complete a self-certification form developed by the RRC based on requirements 1–5 in the Measure M1. |  | FRCC
|  |  | Should "Contingency" be all upper case? |  | SRP | Yes.
|  |  | Suggest CPM1 be changed to CPS1. |  | FRCC | Corrected.
|  |  | Suggest CPM2 be changed to CPS2 to preserve the Policy 1 designations |  | FRCC | Corrected.
|  |  | The contingency plan must meet the following requirements with interim provisions included if it is expected to take in excess of one hour to implement the loss of Primary Control Facility contingency plan: 1. The contingency plan shall not rely on data or voice communication from the primary control facility to be viable. 2. The plan shall include procedures and responsibilities for providing basic tie line control and procedures and responsibilities for maintaining the status of all inter area schedules such that there is an hourly accounting of all schedules. 2. The plan shall include procedures and responsibilities for providing basic tie line control and procedures and responsibilities for maintaining the status of all inter area schedules such that there is an hourly accounting of all schedules. 3. The contingency plan must address monitoring and control of critical transmission facilities, generation control, voltage control, time and frequency control, control of critical substation devices, and logging of significant power system events. The plan shall list the critical facilities. 4. The plan shall include procedures and responsibilities for maintaining basic voice communication capabilities with other Reliability Authorities, Transmission Operators, and Balancing Authorities. 5. The plan shall include procedures and responsibilities for conducting periodic tests, at least annually, to ensure viability of the plan. 6. The plan shall include procedures and responsibilities for providing annual training to ensure that Shift Operating personnel are able to implement the contingency plans. 7. The plan shall be reviewed and updated annually. |  | FRCC
|  |  | The definition of “clock-minute average” needs to add the phrase “as well as for the control area’s frequency bias” A clock-minute average is the average of the reporting Balancing Authority’s valid measured variable (i.e. for ACE and for frequency error, as well as for the control area’s frequency bias) for each sampling cycle during a given clock-minute. o |  | FRCC
|  |  | The following is provided as a recommended revision for clarity: |  | FRCC
|  |  | The Reliability Authority shall ensure that all Balancing Authorities, and Transmission Operators operate to prevent the likelihood that a disturbance, action, or non-action in its Reliability Authority Area will result in a SOL or IROL violation in another area of the Interconnection. In instances where there is a difference in derived limits, the Reliability Authority and its Balancing Authorities, and Transmission Operators shall always operate the Bulk Electric System to the most limiting parameter. |  | FRCC
|  |  | The remainder of this section was the existing Compliance Template P9T2 Compliance Assessment notes. These should be added as additional requirements to this standard. With this addition, it is important to remove any references to existing NERC Policies and Appendices since these will be retired with the adoption of Version 0 Standards. |  | FRCC
|  |  | The Standard Drafting Team recommends the Compliance Monitoring section be removed from Version 0. If this section remains: Reference to NERC Standard Training Document be changed to NERC Performance Standard Reference Document |  | FRCC
|  |  | To achieve 100% Compliance the Reliability Authority implemented relief procedures in accordance with the requirements. |  | FRCC