2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | American Bituminous Power Partners, LP (ABPP) | NCR00680 | RFC2014014452 | PRC-005-1 | R2 | On October 31, 2014, ABPP submitted a Self-Report stating that, as a Generator Owner (GO), it had an issue of PRC-005-1 R2. ABPP determined that it did not keep complete evidence of maintenance and testing within defined intervals for its batteries and battery chargers. Specifically, ABPP did not keep complete evidence of maintenance and testing within defined intervals for its batteries and battery chargers at its Grant Town Power Plant. ABPP discovered this missing evidence during an internal assessment of compliance as part of ABPP’s ongoing operation of its internal compliance program. This internal assessment reviewed battery and battery charger maintenance documentation stored in ABPP’s facility maintenance management database. Testing evidence was either missing or incomplete for monthly, quarterly, and annual activities. ABPP’s discovery of the missing and incomplete evidence prompted it to further investigate the issue. As part of this investigation, ABPP conducted interviews with site personnel and hired a third party NERC consultant (ICF International) which led ABPP to the conclusion that its PRC-005 compliance program needed revision and improvement. ABPP determined that the root cause of the issue was that ABPP maintenance personnel did not fully understand the PRC-005 documentation requirements related to maintenance and testing and that site plant procedure, controls, and training related to PRC-005 compliance needed improvement. The duration of this noncompliance is from September 1, 2011, the date ABPP was required to comply with PRC-005-1 R2, to October 21, 2014, the date ABPP completed its Mitigation Plan. During mitigation, ABPP discovered another noncompliance with PRC-005-1 R2. On December 29, 2014, ABPP sent an email to ReliabilityFirst stating that, as a GO, it had found another issue with PRC-005-1 R2. Specifically, ABPP found that prior to ABPP’s November 8-9, 2014 testing of its current transformers (CTs) and potential transformers (PTs), ABPP had not been testing its CTs and PTs and therefore was not keeping evidence of that testing. ABPP, in its capacity as a GO is subject to compliance with PRC-005-1 R2 and ABPP registered as a GO on May 30, 2007. From May 30, 2007 through November 8, 2014, ABPP did not test, and therefore did not keep records of testing, its CTs and PTs. The root cause of this noncompliance was the same as the self-reported issue described above: ABPP maintenance personnel did not understand and were not properly trained on the documentation requirements related to maintenance and testing of CTs and PTs. The duration of this second noncompliance is from September 1, 2011, the date ABPP was required to comply with PRC-005-1 R2, to November 9, 2014, the date ABPP completed its testing of its CTs and PTs with proper documentation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. ABPP checks its battery systems, batteries, and chargers every day as part of daily inspections. There were no misoperations during the noncompliance period related to battery systems or CTs and PTs. All devices with missing or incomplete testing were subsequently tested and ABPP found no issues with any of the tested devices. Also, ABPP identified no issues with the supporting testing documentation of the battery systems, CTs, and PTs. Additionally, all other components of ABPP’s protection system maintenance and testing program were tested in accordance with defined intervals and with properly maintained evidence to support that testing. Finally, ABPP is an 80 megawatt waste coal power facility that has a minimal impact on the Bulk Electric System. ReliabilityFirst considered ABPP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, ABPP: 1) revised the site plant procedure to more clearly define inspection intervals and data recording requirements; 2) retrained applicable site personnel, including management and technicians, on Reliability Standard Requirements and documentation protocols to remind them of the importance of keeping accurate and timely records of testing; 3) installed additional site controls to ensure timely completion of testing through the use of the Microsoft Outlook program that allows the manager to record and assign tasks to subordinates; 4) revised its inspection data sheets to more clearly define inspection protocols to match the recommendations of the Original Equipment Manufacturer; and 5) implemented a six month period of additional data review and evidence sign off by the Plant Manager to ensure technicians are following the correct inspection recording protocol. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE East China, LLC (DTEEC) | NCR08048 | RFC2014014016 | PRC-005-1 | R1 | During a Compliance Audit conducted from May 8, 2014 through May 23, 2014, ReliabilityFirst determined that DTEEC, as a Generator Owner (GO), had an issue of PRC-005-1 R1. DTEEC’s Protection System maintenance and testing program did not include testing and maintenance intervals for DC battery chargers. Although DTEEC’s Protection System maintenance and testing program did not include battery chargers, DTEEC did provide evidence that it had actually been testing the devices. In addition, DTEEC’s DC control circuitry interval of seven years was based on the NERC Protection System Maintenance Technical Reference, which requires partial monitoring to qualify for the less frequent seven-year interval. DTEEC did not meet all the requirements for partial monitoring of DC control circuitry. Although DTEEC met the interval requirements for partially monitoring for notes 1a, 1d, 1e, and 1f, it failed to meet note 1b (monitoring of trip coil continuity and trip voltage by periodic checking of a monitoring light or by an automatic continuity monitoring means such as the trip coil monitor of the microprocessor relay). Because DTEEC did not satisfy all requirements of the NERC Protection System Maintenance Technical Reference, DTEEC did not qualify for the longer, seven-year interval and instead should have used a five-year interval. The duration of this noncompliance is from April 1, 2013, when battery chargers were added to the definition of Protection System and therefore were subject to the Requirements of PRC-005, to May 16, 2014, the date DTEEC remediated this issue. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Although DTEEC’s Protection System maintenance and testing program did not specify maintenance and testing intervals for one device type, DTEEC was actually performing testing on those devices, significantly reducing risk to the BES. In addition, although DTEEC failed to meet one requirement to qualify for the longer, seven-year interval for DC control circuitry testing, it did have monitoring lights of trip coil continuity and trip voltage, but lacked a formal procedure for personnel to monitor them. Furthermore, DTEEC was performing all necessary maintenance and testing on the incorrectly-determined seven-year maintenance and testing interval. ReliabilityFirst considered DTEEC's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DTEEC: 1) revised its Protection System maintenance and testing program to incorporate DC battery charger maintenance and testing requirements; and 2) changed the DC control circuitry testing intervals to every five years. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | DTE Electric Company (DTE Electric) | NCR00753 | RFC2014013448 | VAR-002-2b | R3 | On February 21, 2014, DTE Electric submitted a Self-Report to ReliabilityFirst stating that as a Generator Owner (GO) and Generator Operator (GOP), it had an issue with VAR-002-2b R3. The noncompliance occurred at the St. Clair Power Plant on Unit #1. At 1331 EST, the St. Clair Power Plant Unit #1 automatic voltage regulator (AVR) unexpectedly changed from automatic mode to manual mode. Although AVR status change alarming was installed and operational on the Energy Management System (EMS), there was no audible alarming in the control room itself. The alarming was designed to alert the Central System Supervisor and the Merchant Operation Controller in case the operator failed to make the required call after manually changing AVR status, which was the anticipated course of action. The EMS alarm was identified by DTE Electric Merchant Operation personnel at 1402 EST, who then called the St. Clair Power Plant operator to question this change in state. Once notified, the St. Clair Power Plant operator inspected the AVR status and returned the AVR to Auto at 1404 EST. The St. Clair Power Plant Unit #1 AVR was in manual mode for a total of 33 minutes. After the AVR was returned to automatic mode, the plant operator notified the TOP of the change in AVR from automatic mode to manual mode and the subsequent return to automatic voltage control mode. The duration of the issue with VAR-002-2b R3 is less than one day, January 27, 2014, the date DTE Electric failed to notify its Transmission Operator within thirty minutes of a change in status of an automatic voltage regulator. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. DTE Electric was cooperative throughout the enforcement process for this issue, DTE Electric’s mitigation was effective and comprehensive. ReliabilityFirst considered DTE Electric's compliance history and determined there were no relevant instances of noncompliance or ReliabiltyFirst considered DTE Electric's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because ReliabilityFirst determined that the conduct of DTE Electric’s personnel was ideal under circumstances that they could not control, the issue was promptly detected, the mitigation was robust and effective, and its reporting of the issue was timely. | To mitigate this issue, DTE Electric: 1) inspected the St. Clair Power Plant Unit #1 AVR relay contacts; 2) created a corrective action report on AVR signage and unit control room alarms; and 3) installed AVR control room alarming at the St. Clair Power Plant. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation and Marketing (FE Generation) | NCR11317 | RFC2013012499 | PRC-001-1 | R3 | On May 31, 2013, FE Generation submitted a Self-Certification to ReliabilityFirst stating that as a Generator Operator (GOP) it had an issue with PRC-001-1 R3. FE Generation reported that, during an internal review, it discovered that it failed to coordinate a change on a single protective relay with its Transmission Operator (TOP) and Host Balancing Authority. Specifically, FE Generation discovered that a generator protective relay upgrade conducted in 2011 was not on an internal PRC-001 relay project list. Upon discovery, FE Generation conducted an investigation to determine the level of coordination that occurred during the upgrade. FE Generation determined that it had no documentation available to support that coordination was conducted with the locally interconnected Transmission Owner. FE Generation determined that although it has a detailed procedure in place for coordinating changes to protective systems, the relay design engineer did not follow it. The duration of this noncompliance is from May 2, 2011, the date FE Generation failed to coordinate a change to a protective system, to October 31, 2013, the date FE Generation completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the noncompliance was not discovered for two years, the duration also supports the conclusion that the noncompliance was an isolated occurrence of a single employee not following the procedure. Second, FE Generation made only one functional change to the relay that required coordination. ReliabilityFirst considered FE Generation's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FE Generation: 1) removed the additional protective relay functionality that was not coordinated; and 2) developed and presented re-training on the requirements of coordination.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Generation and Marketing (FE Generation) | NCR11317 | RFC2013012757 | PRC-001-1 | R1 | During the FE Generation Compliance Audit conducted from June 17, 2013 through June 28, 2013, ReliabilityFirst determined that FE Generation, as a Generator Operator (GOP) had an issue of PRC-001-1 R1. ReliabilityFirst discovered that FE Generation did not designate operating personnel as the individuals who are familiar with the purpose and limitation of Protection System schemes. Furthermore, of those non-operating personnel, one of eight individuals was not familiar with certain Protection System schemes applied in FE Generation’s area, affecting two of the 18 generation facilities. The duration of this noncompliance is from June 18, 2007, the date FE Generation was required to comply with PRC-001, to December 31, 2014, the date FE Generation completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, the personnel identified by FE Generation who were familiar with Protection System schemes are technical personnel who support operations at the facilities. Second, FEGM personnel unfamiliarity was limited to stability limitations and Special Protection schemes, not owned by FE Generation, at two generating facilities. ReliabityFirst considered FE Generation's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue FE Generation: 1) developed standardized PRC-001 training to include the purpose and limitations of Protection System schemes in its area; 2) revised a procedure to designate operations personnel to have familiarity with the purpose and limitations of Protection System schemes; and 3) administered training to those designated operations personnel, with future training to occur on a three-year cycle.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Nuclear (FE Nuclear) | NCR11316 | RFC2013012170 | VAR-002-1.1b | R2 | On March 18, 2013, FE Nuclear submitted a Self-Report to ReliabilityFirst stating that as a Generator Owner (GO) and Generator Operator (GOP) it had and issue with VAR-002-1.1b R2. FE Nuclear reported that during a review of operating data at all nuclear sites, it discovered three voltage schedule excursions during off-peak hours at its Beaver Valley facility. In each case, there was no record of having contacted the local control center. The greatest excursion was 2.6 kV. FE Nuclear’s root cause analysis of the excursions revealed that a small difference in exciter voltage, such as the small difference present in the instant noncompliance, when displayed on an analog meter, did not appear different enough for an operator to identify that the voltage schedule was not being followed. The duration of this noncompliance is from March 18, 2011, the date of the first occurrence of the noncompliance, to September 12, 2013, the date FE Nuclear completed its remediation. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, although the noncompliance was not identified for a period of two years, the root cause was related to human error in reading imprecise instrumentation, which has a limited likelihood of recurrence even during the period in which the problem was unknown to FE Nuclear. Second, the Beaver Valley facility is located in a geographic area of significant generation such that other units could compensate for the error. Third, the failure to identify the small voltage excursions was not due to a failure to monitor voltage. ReliabilityFirst considered FE Nuclear's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FE Nuclear: 1) supplemented metering with a computer dedicated to monitoring station voltage with alarms for voltage excursions; 2) improved a procedure to require twice-daily review of automatic voltage regulator set-point adjustments to maintain voltage during the change from on-peak to off-peak voltage schedules; and 3) conducted training on the revised procedure. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | FirstEnergy Nuclear (FE Nuclear) | NCR11316 | RFC2013012759 | FAC-008-1 | R2 | During the FE Nuclear Compliance Audit conducted from June 17, 2013 through June 28, 2013, ReliabilityFirst determined that FE Nuclear, as Generator Owner (GO) had an issue of FAC-008-1 R2. FE Nuclear failed to provide a method of inspection and review of Facility Ratings Methodologies for three nuclear generating facilities. The duration of this noncompliance is from February 23, 2009, the start date of the Compliance Audit period, to June 28, 2013, the date FE Nuclear implemented its mitigating actions. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. First, FE Nuclear’s generating facilities have a normal band of operation between the normal operating point (applicable alarm or trip value) and the operating limit (maximum operating value) imposed on the system, so the inherent value in this Requirement is diminished for the operating conditions of these particular facilities. Second, FE Nuclear promptly resolved the noncompliance during the audit. ReliabityFirst considered FE Nuclear's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue FE Nuclear revised its Facility Ratings Methodology to apply to FE Generation and FE Nuclear, thus providing all Facility Ratings Methodologies in one document. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | Pleasants Energy, LLC (Pleasants Energy) | NCR00294 | RFC2014013916 | VAR-002-1.1b | R2 | ReliabilityFirst conducted a compliance audit of Pleasants Energy on August 14, 2013, during which ReliabilityFirst determined that Pleasants Energy, as a Generator Operator (GOP) had an issue of VAR-002-1.1b R2. Pleasants Energy did not maintain the generator voltage or Reactive Power output (within applicable Facility Ratings) as directed by the Transmission Operator (TOP). Specifically, Pleasants Energy did not maintain the generator voltage or Reactive Power output (within applicable Facility Ratings) as directed by the TOP at various times from April 12, 2012 to August 30, 2013. At various points during this time period, Pleasants Energy did not maintain voltage levels within the TOP’s default voltage schedule. Also, Pleasants Energy did not notify the TOP when it was not maintaining proper voltage levels and did not request any exemptions or modifications to its voltage schedule from the TOP. The operators on shift were unaware that they were required to notify the TOP if they were operating outside of the voltage schedule. The root cause of this noncompliance was that Pleasants Energy plant operators did not understand that VAR-002-1.1b requires notification to the TOP, and exemption or modification (where applicable), when Pleasants Energy is unable to maintain voltage levels within its schedule. This was the only audit finding at the Operations and Planning Compliance Audit of Pleasants Energy, and there was no indication that plant operators lacked an understanding of compliance responsibilities with respect to other Reliability Standards. The duration of this noncompliance is from August 3, 2012, the date by which Pleasants Energy was required to comply with VAR-002-1.1b, to May 30, 2013, the date Pleasants Energy completed its Mitigation Plan. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. At all relevant times, voltage was regulated by Pleasants Energy’s Automatic Voltage Regulator (AVR). From April 12, 2012 to August 30, 2013, the plant had a total operating time of 969 hours and 7 minutes. For 840 hours and 16 minutes, the plant operated within its voltage schedule. For 128 hours and 51 minutes, Pleasants Energy operated outside of its voltage schedule (138kv +/- 2kV). During those 128 hours and 51 minutes, Pleasants Energy was always within 1.98% of the TOP’s voltage schedule (138kv +/- 2kV). Throughout the entire period of the noncompliance, the AVR continued to maintain system voltage and Pleasants Energy was not contacted by the TOP about operating outside of the low end of the voltage schedule. The size, type, location, and electrical connections of the units at the plant made it impossible at times for the plant to meet its voltage schedule, even when the plant was providing maximum MVARs to the electrical system. During the entire period of noncompliance, Pleasants Energy did not notify or request an exemption from the TOP when it was outside of its voltage schedule. Although Pleasants Energy’s mitigation plan was completed on May 30, 2013, Pleasants Energy did not request a modified voltage schedule until July 1, 2013. As of July 1, 2013, Pleasants Energy had put in place a procedure to notify the TOP when it is unable to meet the voltage schedule and to obtain an exemption in such cases, thereby decreasing risk to the Bulk Electric System (BES). ReliabilityFirst considered Pleasants Energy's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Pleasants Energy: 1) developed and presented training to plant personnel on the TOP voltage schedule that Pleasants Energy must follow; 2) added a red flashing alert to the operator screen in the control room which alerts the operators if the TOP voltage level is not being met; and 3) revised its plant procedure to state that after synchronizing to the grid and reaching base/preselected load, the net system voltage must be monitored to ensure compliance with the TOP voltage schedule. If the net system voltage is outside of the TOP voltage schedule, the control room operator must raise or lower the voltage accordingly or notify the TOP requesting an exemption or modification to the voltage schedule. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | ReliabilityFirst Corporation (ReliabilityFirst) | U.S. Department of Energy (DOE) | NCR04167 | RFC2013013004 | PRC-005-1b | R2.1 | On September 20, 2013, DOE submitted a Self-Report stating that, as a Distribution Provider (DP) and Transmission Owner (TO), it had an issue of PRC-005-1b R2.1 During a review of Preventive Maintenance activity for Bulk Electric System (BES) related equipment, DOE discovered that two items associated with the BES had exceeded their Preventive Maintenance delinquent dates. Delinquent dates are maintenance due dates. Exceeding an item’s Preventive Maintenance delinquent date means the item is overdue for maintenance according to DOE’s Preventive Maintenance Program (Program). One of these two items, the Bus 22 Potential Transformer (PT), is part of the Protection System for the site and falls under the Transmission Owners requirement of PRC-005-R1b R2.1. The other item, Oil Circuit Breaker (OCB) 258, is part of the BES and is included in the Site’s Program but does not fall under the NERC definition of a Protection System. Procedure FBP-SM-PRO-00384 of the Program requires that when a Preventive Maintenance task cannot be completed by the delinquent date, then either (a) a Preventive Maintenance deferral must be processed or (b) the equipment must be taken out of service. DOE initially planned, scheduled, and attempted Preventive Maintenance testing for the Bus 22 PT at the X-530 Switchyard within its defined interval. During the first and subsequent maintenance attempts, DOE encountered recurring problems while switching the PT out of service, which caused a loss of metering to the plant side. While the DOE further evaluated these switching out of service issues, the maintenance task exceeded the May 30, 2013 delinquent date without the required Preventive Maintenance deferral. Additionally, power operations could not take the Bus 22 PT out of service prior to its delinquent date because it would have impacted revenue metering for the plant site. OCB 258 became delinquent on June 15, 2013 and a request was made to Ohio Valley Electric Corporation (OVEC) and the Midcontinent Independent System Operator, Inc. (MISO) to take the OCB out of service on June 18, 2013. MISO approved the removal of OCB on June 24, 2013 and it was taken out of service on that same day. The duration of this noncompliance is from May 30, 2013, the date by which DOE was required to comply with PRC-005, to October 31, 2013, the date DOE completed its Mitigation Plan to remediate its noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. The Bus 22 PTs remained in service and the protective relays were not impacted. If a fault were to occur on the Bus 22 PT, the system would switch to the Bus 21 PT and thus the relay potential would remain in service while metering for the site might be lost. Additionally, OCB 258 is only one of 20 OCBs in a seven bay breaker-and-a-half scheme (meaning the system has adequate alternate ties to the BES in case of the failure of OCB 258). ReliabiltyFirst considered DOE's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because although DOE had two prior violations of PRC-005, ReliabilityFirst did not consider DOE’s violation history as a factor warranting an alternative disposition method. The two prior violations are distinguishable as both prior violations involved a failure to provide evidence of any maintenance and testing for required Protection System devices. In contrast, the instant noncompliance stems from DOE attempting to implement its Program for the devices at issue, but encountering unexpected problems while implementing it, which caused DOE to violate the Reliability Standard at issue while addressing those problems. As a result, ReliabilityFirst did not consider the prior conduct of DOE an aggravating factor warranting a non-monetary sanction since ReliabilityFirst does not have the authority to assess a monetary sanction against the DOE. | To mitigate this issue, DOE: 1) generated and processed Preventive Maintenance deferrals to evaluate the impact of their continued operation and to allow time for proper planning and scheduling of the overdue maintenance; 2) expedited the maintenance on the overdue items within its work control process and either processed Preventive Maintenance deferrals or removed the equipment from service; 3) completed an extent of condition analysis to determine if any other maintenance tasks were overdue for other DOE items; 4) processed and completed tasks related to three additional items revealed as a result of the condition analysis; 5) made switchyard preventative maintenance a higher priority in its work control process; and 6) made the identification and processing of NERC related maintenance tasks a higher priority in its work control process. ReliabilityFirst has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014141 | PRC-005-1b | R2 | On July 17, 2014, DEP submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1b R2. DEP reported that it was missing a quarterly battery inspection report for the 4th quarter of 2013 at the Mayo Plant. As part of a self-assessment, DEP generation compliance requested a review of the quarterly and annual maintenance inspection records for each of the Fossil and Hydro plants for DEP. DEP discovered that a quarterly inspection report for the Mayo Plant was missing for the fourth quarter of 2013. DEP completed the preventative maintenance (PM) record on November 21, 2013 for this fourth quarter inspection. However, DEP could not locate the completed inspection report. This inspection report is required to demonstrate DEP’s compliance with its PRC-005 program. Two batteries were affected at the Mayo Plant. While SERC was performing its assessment and determining the scope of the issue, DEP found an additional issue. In 2012, DEP’s PRC-005 program for battery maintenance required it to perform maintenance quarterly and annually. The program defines quarterly as every three months and the system used to schedule maintenance establishes target dates based on the previous completion date. The program also allows a three week grace period before and after the target date. The system generates work orders 30 days prior to the target date to allow scheduling of the maintenance to occur within the grace period. DEP discovered a second issue with the Protection System maintenance program during an internal review of records in preparation for the upcoming DEP audit. On January 25, 2012, DEP performed fourth quarter battery maintenance at the Smith Energy Complex Combined Cycle Steam Unit. Based on that completion date, the maintenance management system generated a work order 30 days prior to the target date for the next quarter which was April 25, 2012. To comply with the maintenance program, the earliest the maintenance should have been performed was April 4, 2012. However, the maintenance was immediately scheduled and performed on March 27, 2012, one week earlier than allowed by the DEP program. DEP’s work management system did not have logic to prevent the early scheduling and completion of periodic maintenance and testing. This issue affected one battery at the Smith Energy Complex. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System. DEP’s failure to maintain adequate inspection records and to maintain its batteries within the intervals defined in its program could have resulted in inadequate maintenance of the batteries, which could result in unnecessary and unplanned plant outages or the inability to respond to disturbances or both. However, the batteries at both locations had low voltage alarms, allowing DEP to investigate if a battery had a problem. In addition, DEP’s other monthly and weekly preventative maintenance records show the batteries were in good operating condition. The quarterly maintenance records for subsequent quarters also indicate that the batteries were in good operating condition. No harm is known to have occurred. A Settlement Agreement covering violations of PRC-005 R2 for DEP was filed with FERC under NP12-12-000 on December 30, 2011. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. The prior violation involved a failure by DEP to conduct maintenance on Coupling Capacitive Voltage Transformers as called for in its Protection System maintenance and testing program. DEP determined that the root cause of the violation was database corruption and as part of its Mitigation Plan, DEP undertook an inventory of its substations and reconciled the remainder of the field inventory with its database. A Settlement Agreement covering violations of PRC-005 R2 for DEP was filed with FERC under NP13-476-000 on July 31 2013. On January 27, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. DEP missed or had incomplete maintenance or testing records for less than 5 percent of the Protection System devices. Mitigation included performing maintenance and testing on those devices and revising their record keeping methods for those, but not all, devices. A Find, Fix, Track and Report informational posting addressing remediated issues for certain registered entities including noncompliance with PRC-005 R2 for DEP was posted on the NERC website on January 30, 2014. The 60-day review period passed on March 31, 2014. SERC considered DEP's compliance history and determined that the instant issue was appropriate for compliance exception treatment because the causes of the extant issues were not addressed by the previous Mitigation Plan. For this prior issue DEP had inadvertently closed a work order before testing on a single line trap had been successfully completed. DEP identified the root cause was the failure to require evidence of work completion to be attached to the work order prior to closing the order. The requirement to do so was added to the work order process for all Protection System devices. | To mitigate this issue, DEP: 1) issued a plant standing order to properly document the reports per the Fossil/Hydro Organization procedure with the plant Instrument & Control personnel; 2) established a procedure to ensure that staff will verify once a quarter that the inspection reports are properly recorded in addition to the existing checks already in place; 3) documented lessons learned to ensure all parties involved with quarterly battery PM are aware of the requirement to complete the PM during the specified quarter, and not prior to the start date; 4) ensured that all applicable staff signed off that they had read the document containing the lessons learned; and 5) sent a memo to DEP plant managers and superintendents informing each plan of the quarterly PM review and expectations.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014176 | PRC-023-2 | R5 | On July 22, 2014, DEP submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R5. DEP failed to submit a list of circuits using PRC-023 Criterion 12 to the Regional Entity within 15 months. On June 5, 2014, during an internal periodic review of PRC-023-2 compliance, DEP determined that it had exceeded the 15 month period since it last reported on PRC-023-2 R5. DEP reported its updated list to SERC on June 17, 2014. Before that, DEP last reported its updated list to SERC on February 6, 2013. During the approximate 16.5 months between reports, on May 13, 2013, DEP replaced the relays on one 500kV terminal at its Wake substation with microprocessor relays with load encroachment capability. This left only one 230kV line on the DEP criterion 12 list. DEP stated that the apparent cause of this issue was that it had no mechanism in place to remind it to report criterion 12 data to SERC. This issue lasted from May 6, 2014, when DEP failed to submit its updated list within 15 months of its last report through June 17, 2014, when DEP submitted its updated list. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. DEP’s failure to provide an updated list of its criterion 12 circuits to SERC within 15 months left SERC and NERC unaware for approximately 1.5 months that DEP removed one circuit from its criterion 12 list and could have affected long term planning. However, the relaying change DEP made increased the loadability of the transmission line and DEP used the correct setpoints in its contingency planning models. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, DEP: 1) reported its Criterion 12 facility list to SERC via email on June 17, 2014; and 2) established a recurring internal reminder to the responsible DEP business units for completing a review and submitting the report. SERC has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014017 | INT-001-3 | R1 | On June 23, 2014, DEP submitted a Self-Report stating that, as a Purchasing-Selling Entity (PSE), it had an issue with INT-001-3 R1. DEP failed to ensure that Arranged Interchange was submitted to the Interchange Authority for all Dynamic Schedules at the expected average MW profile for each hour. The joint dispatch dynamic schedule is referenced as Dynamic Transfer East to Duke (DTRED). Duke Energy Power Trading is responsible for purchasing transmission service reservations (TSRs). On May 8, 2014, Duke Energy Power Trading reserved a TSR on the DEP system to flow power into the Duke Energy Carolinas (DEC) system, but because DTRED was not expected to flow in this direction, a TSR was not established on the DEC system. A tag was not needed because power was not flowing at the time. For Hour Ending (HE) 20:00, conditions changed anticipating DTRED would flow from DEC to DEP. Therefore, Duke Energy Power Trading established a TSR on the DEC system for flow into DEP. No actual flow was taking place and no tag was in place for this anticipated flow. However, TSRs were in place and ready if economics were satisfied for actual flow. Earlier that day, DEP system operators substituted 0 MW for the DEP TSR values to avoid an unexpected flow without the necessary tagging in place. However, this entry was made in the incorrect data field in the DEP system that provides data for the automation. Due to this incorrect entry, from 19:00 to 19:07 the dynamic schedule DTRED flowed eight MWh of energy without a tag in place because TSRs had been established and economic conditions had been satisfied. During the seven minutes, the DTRED schedule ramped up to reach a peak of 100 MW and integrated a total of eight MWh. At 19:28, the DEP system operator discovered the issue and terminated the DTRED schedule for the remainder of the hour. This issue occurred because the DEP system operators failed to adhere to DEP’s established procedures. This issue lasted from May 8, 2014 at 19:00, when the schedule began to flow without a tag, to May 8, 2014 at 19:07, when the DEP system operator terminated the schedule. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. For a period of 28 minutes, when the inputs in the automated system would have allowed flows if then economic conditions were met, DEP’s Interchange Authority and Reliability Coordinator would not have been aware of the DTRED transaction because DEP failed to properly tag this data. However, the transaction flowed for seven minutes with an integrated total of eight MWh. After the seven minutes, the transaction stopped flowing because economic conditions were no longer met and the system operator later terminated the flow for the remainder of the hour. At the time of the issue, the DEC Balancing Authoritie's (BA’s) instantaneous load was approximately 14,660 MW and the DEP East BA’s instantaneous load was approximately 8,922 MW for a total of 23,582 MW instantaneous load between the two BAs. The peak of 100 MW that flowed during these seven minutes represented approximately 0.4% of the combined BA load at that time. In addition, there were no Transmission Loading Reliefs for the flowgates that this transaction would impact. No harm is known to have occurred. A Notice of Confirmed Violation covering violations of INT-001 R1 for DEP was filed with FERC under NP11-266-000 on August 31, 2011. On September 30, 2011, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Find, Fix, Track and Report (FFT) informational filing addressing remediated issues for certain registered entities including noncompliance with INT-001 R1 for DEP was filed with FERC under RC14-14-000 on July 31, 2012. The 60-day review period passed on September 29, 2012. SERC considered DEP's compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, the underlying conduct of the instances was different. The prior violations were related to failure to create and submit tags while the instant issue was related to failure of DEP System Operators to adhere to established procedures. A System Operator had inadvertently replaced the DTRED schedule in the Energy Management System tabular incorrectly and this allowed the DTRED to flow without a tag on May 8, 2014 from 19:00 to 19:07 when other criteria were satisfied. System Operators had current approved procedures providing guidance on the correct process to substitute the DTRED schedule to a certain MW value, which, if adhered to, would have prevented the DTRED from flowing without a tag. | To mitigate this issue, DEP: 1) notified system operator supervisors that effective immediately, the Transmission Services Desk will generate a tag as soon as transmission for the DTRED is purchased with no delay; 2) sent an email to system operators advising them of the event and the correct and incorrect ways to substitute the DTRED schedule to a certain value; 3) deployed an “interlock” to the DEP energy management system such that the DTRED will not be allowed to flow energy without a Confirmed Interchange tag for DTRED; and 4) required system operators to read and sign off on their understanding of the existing procedure SORMC-GOP-150 "Joint Dispatch Dynamic Schedule" which contains guidance on how to manually substitute values for DTRED. SERC has verified the completion of all mitigation activity.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Carolinas (Duke) | NCR01219 | SERC2014014200 | PRC-023-2 | R5 | On August 6, 2014, Duke submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-023-2 R5. Duke reported that it had not submitted a list of facilities using PRC-023-1 R1 Criterion 12 to its Regional Entity. An affiliate’s discovery of an issue with PRC-023-2 R5 prompted Duke to review its records related to PRC-023. On July 7, 2014, that review led Duke to discover that it had not reported its one facility that had relay trip setpoints established in accordance with PRC-023-2 R1 Criterion 12. Duke should have submitted the initial list to SERC in 2013, the year that PRC-023-2 went into effect. In 2013, SERC conducted a survey to determine how many circuits in the SERC Region were set according to Criterion 12. SERC confirmed that Duke did not submit a list to SERC including the Asbury 500kV line in the 2013 calendar year. Duke stated that the primary cause of the issue was an administrative oversight. SERC determined that Duke had an issue with PRC-023-2 R5 because it failed to provide an updated list of the circuits associated with relays set in accordance with Requirement 1 Criterion 12 to its Regional Entity at least once each calendar year. This issue lasted from January 1, 2014, when Duke failed to submit its updated list within the 2013 calendar year through July 11, 2014, when Duke reported the facility to SERC. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Duke’s failure to provide a list of its criterion 12 circuits to SERC within the 2013 calendar year left SERC and NERC unaware that Duke had one facility with relay trip setpoints established in accordance with criterion 12. However, Duke used the correct Facility Ratings in its contingency planning models. No harm is known to have occurred. SERC considered Duke's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, Duke: 1) reported its Criteria 12 facilities to SERC via email on July 11, 2014; 2) implemented a new Standards implementation procedure to ensure the proper implementation of new NERC Standards prior to the Standards becoming effective; and 3) setup automated reminders in CATSWeb to assist with meeting compliance submittal deadlines.
2015-03-31 | SERC Reliability Corporation (SERC) | Duke Energy Progress, Inc. (DEP) | NCR01298 | SERC2014014385 | EOP-005-2 | R5 | On August 5, 2014, SERC sent DEP a notice of a Compliance Audit scheduled for November 3, 2014 through November 21, 2014. On October 7, 2014, DEP submitted a Self-Report stating that, as a Transmission Operator, it had an issue with EOP-005-2 R5. DEP did not provide the latest Reliability Coordinator (RC) approved restoration plan to all of its system operators prior to its effective date. DEP’s restoration plans are made available to system operators as hard copies and are also uploaded electronically to its energy control center SharePoint site. DEP utilizes its SharePoint site as evidence of the date it made restoration plan available to system operators in the primary control room. On July 9, 2014, during a review of the EOP-005-2 R5 compliance evidence, DEP discovered that the May 27, 2014 RC-approved restoration plan was posted to the SharePoint site on May 30, 2014, which was three days after the effective date. DEP determined that the issue was caused by process flaws associated with the revision and posting process of the RC-approved versions of the restoration plan. This issue lasted from May 26, 2014, the last day that DEP could have made its restoration plan available to all of its system operators prior to its effective date, through May 30, 2014, when DEP made its restoration plan available to all of its system operators. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk-Power System. DEP’s failure to post the approved version of the restoration plan prior to its effective date could have led system operators to use restoration plans that do not correctly reflect current system configurations, appropriate blackstart units and cranking paths, and other vital information. However, the previous version of the restoration plan was available in the control room and the five changes to the restoration plan would not have affected the essential steps of a system restoration event if one had occurred prior to posting the revised version of the restoration plan on the SharePoint site. DEP posted the revised restoration plan within three days of its approval. No harm is known to have occurred. SERC considered DEP's compliance history and determined there were no relevant instances of non-compliance. | To mitigate this issue, DEP: 1) posted the current version of the RC-approved DEP restoration plan to the DEP energy control center SharePoint site for availability to system operators; 2) held a meeting in which relevant staff discussed the issue and possible solutions; 3) modified the SharePoint Library to include effective dates for all system operator reference manuals; 4) revised the “Administration of the System Operations Reference Manual Carolinas" to incorporate the effective date into the procedure process and to modify the procedure process so that the procedure is available in the SharePoint Library before the effective date; and 5) created an extra step in the approval process to address the use of effective dates.
2015-03-31 | SERC Reliability Corporation (SERC) | Fayetteville Public Works Commission (FPWC) | NCR01240 | SERC2014014194 | PRC-005-1.1b | R2 | On July 31, 2014, FPWC submitted a Self-Report stating that, as a Transmission Owner and a Distribution Provider that owns a transmission Protection System, it had an issue with PRC-005-1.1b R2. FPWC reported that it could not produce evidence of annual testing of station batteries during calendar year 2013. FPWC could not provide data to demonstrate that it performed impedance testing on station batteries at its Points of Delivery (POD) during calendar year 2013, as required by its program. FPWC downloads test data reports from the battery testing device into a database for permanent retention. The last recorded test date for annual impedance testing of the POD batteries in the database was July 25, 2012. Sometime around August 2013, during FPWC’s performance of its yearly battery testing program, the battery tester failed. FPWC did not download the data from testing completed prior to the tester failure into the database. Therefore, FPWC does not have documentation that it completed the required POD testing prior to the failure. FPWC personnel verified that yearly battery testing was being done when the tester failed, but cannot confirm whether all POD battery testing was completed prior to the failure. The cause of the issue was FPWC staff’s failure to promptly download data from the testing device to verify that the required testing had been satisfactorily completed. Timely verification of the satisfactory testing would have provided the opportunity to expedite repair of the tester or to acquire another tester to complete the testing, prior to the end of calendar year 2013. SERC reviewed FPWC’s Protection System program documents and an inventory spreadsheet compiled by FPWC, which included a complete listing of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. SERC determined that FPWC had an issue with PRC-005-1.1b R2 because it could not provide documentation that seven out of seven batteries (100%) were maintained and tested within the defined annual interval. In total, FPWC could not provide documentation that seven out of 87 Protection System devices (8%) were maintained and tested within the defined intervals. This issue lasted from January 1, 2014, when FPWC could not provide evidence of annual impedance testing for 2013 through July 31, 2014, when FPWC completed and documented battery testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. A station battery failure could trip a FPWC unit offline or prevent a trip when necessary. However, FPWC physically inspected the batteries twice each month for parameters such as voltage, physical appearance, charger output voltage and current, and electrolyte levels. The results of these other tests did not indicate any issues with the batteries. In addition, FPWC displays the battery voltage at its dispatch operations center, and receives an alarm there if voltage drops below a prescribed value. FPWC had directed its dispatchers to send out FPWC personnel to respond in the event of battery voltage alarms and received no battery alarms during the period. FPWC had redundant battery banks in order to provide battery capacity to cycle the breaker. No harm is known to have occurred. SERC considered FPWC compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, FPWC: 1) obtained a replacement impedence tester, completed the required impedance testing on the POD batteries, and found all battery tests satisfactory; 2) downloaded test data into the database; 3) revised procedure to require data to be downloaded into permanent repository within 30 days of completing testing; 4) trained personnel on procedure changes and required status reports; 5) established a designated storage area in a well-traveled location for equipment that needs to be tested or repaired; and 6) began monthly reporting of compliance status of protection system testing.
2015-03-31 | SERC Reliability Corporation (SERC) | Grand Tower Energy Center, LLC (GTEC) | NCR11435 | SERC2014014384 | PRC-005-1.1b | R2 | On October 7, 2014, GTEC submitted a Self-Report stating that, as a Generation Owner, it had an issue with PRC-005-1.1b R2. GTEC cannot provide evidence that the voltage and current sensing devices were maintained or tested. On January 31, 2014, GTEC purchased a generating plant from another utility. Following the purchase of the plant, GTEC conducted a review of maintenance and testing records provided by the utility. GTEC could not find maintenance or testing records associated with voltage and current sensing devices in the documentation provided. SERC reviewed the Protection System program document and an inventory spreadsheet compiled by GTEC which included a complete listing of Protection System devices, the defined intervals, and most recent and prior maintenance and testing dates. Based on this review, SERC determined that GTEC had an issue with PRC-005-1.1b R2 for failing to have documentation that its Protection System devices were maintained and tested for all 141 of its voltage and current sensing devices. In total, GTEC lacked documentation showing maintenance or testing of 141 out of 302 (47%) total Protection System devices. The root cause of the issue was that GTEC could not locate maintenance and testing records for the voltage and current sensing devices in the documentation that the selling utility provided to GTEC. This issue lasted from January 31, 2014, GTEC’s registration date, through May 16, 2014, when GTEC completed maintenance and testing of the voltage and current sensing devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. GTEC’s lack of maintenance and testing records could have led to inadequate or late maintenance or testing, which could result in the loss of a generating unit or reliance on the Transmission Owner’s Protection System devices to respond to a fault if GTEC’s Protection System devices failed to operate as designed. However, GTEC’s plant is manned by a control operator and monitored by an outside operator twenty-four hours a day, seven days a week. The readings from the voltage and current sensing devices lead to a microprocessor relay that would show a failure reading from the voltage and current sensing devices and personnel would be dispatched to determine the cause of the signal. GTEC is a combined cycle power plant with a total summer output of 478 MW interconnected by a single 138 KV interconnection in the MISO footprint, which has 137,232 MW of summer generation capacity. Therefore, GTEC represents less than 0.3% of the generation in the MISO footprint. GTEC is an independent power producer and is bid into MISO for the day-ahead market. Therefore, the generation is not used for generation planning purposes. GTEC completed all testing by May 16, 2014 and did not identify any issues with the voltage and current sensing devices. No harm is known to have occurred. | To mitigate this issue, GTEC: 1) updated the maintenance and testing program per PRC-005-2 requirements; and 2) completed the first round of potential and current transformer testing per the PRC-005-2 requirements.
2015-03-31 | SERC Reliability Corporation (SERC) | South Carolina Electric & Gas Company (SCEG) | NCR00915 | SERC2014014125 | PRC-005-1b | R2 | On June 10, 2014, SERC sent SCEG a notice of a compliance audit scheduled to begin on September 8, 2014. On July 10, 2014, SCEG submitted a Self-Report stating that, as a Transmission Owner, it had an issue with PRC-005-1b R2. SCEG could not provide evidence that all Protection System devices were maintained within the defined intervals. On March 27, 2014, as part of a normal self-audit, SCEG compared a list of known PRC-005 applicable substations to the list used in SCEG’s substation inspection management software (SIMS) program. SCEG identified two substation batteries and two battery chargers that were not listed in SIMS. Although SCEG management met with and confirmed that the responsible technician performed the required maintenance, SIMS did not contain evidence that SCEG performed maintenance on the two batteries and two battery chargers. SCEG installed the batteries and chargers on March 1, 2013, and performed acceptance testing on the devices prior to installation. As such, SCEG should have conducted maintenance on these devices once in each remaining quarter in 2013 and once in the first quarter of 2014. SCEG could not produce a record of the two batteries and two chargers being maintained in the last two quarters of 2013 and in the first quarter of 2014. SCEG submitted evidence that it conducted maintenance on these devices on May 29, 2014. After the July 10, 2014 Self-Report, SCEG conducted a thorough review of all other substation inspection and maintenance documentation and discovered one additional issue. SCEG built a new substation in 2012 and placed it into service on May 23, 2012. The substation had one battery and one battery charger but these Protection System devices were not added to SIMS. SCEG has documentation that the inspector was in the substation doing inspections from June 2012 through February 2013, but SCEG did not document any maintenance of the battery or battery charger during this period. SCEG first recorded battery maintenance for this new substation on April 5, 2013. According to SCEG, its current Protection System consists of the following: 2,707 relays, 156 associated communication systems, 2,519 PT/CTs (V/I Verifications), 103 station batteries, 103 station battery chargers, and 2,707 DC control circuitry devices. Therefore, SCEG’s current Protection System consists of 8,295 total devices. SCEG could not provide evidence that 3 of 103 station batteries (2.9%) and 3 of 103 station battery chargers (2.9%) were maintained within the defined intervals. In total, SCEG could not provide evidence that 6 of 8,295 Protection System devices (0.072%) were maintained within the defined intervals. This issue lasted from October 1, 2012, when SCEG could not provide evidence of maintenance within the defined interval, through May 29, 2014, when SCEG conducted and documented maintenance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. SCEG’s failure to record the maintenance of batteries and battery chargers created a risk that SCEG might not discover problems with those devices, which could lead to Protection System devices not operating as expected, thus affecting neighboring Transmission Operators. However, SCEG conducted acceptance testing prior to installation. The batteries also had low voltage alarms that were monitored 24 hours a day, 7 days a week, which would have alerted SCEG personnel to problems with those devices. Even though SCEG could not produce evidence of the maintenance, SCEG provided an attestation that it maintained the three batteries and three chargers as required by its PRC-005 maintenance and testing program. No harm is known to have occurred. A Find, Fix, Track and Report informational filing addressing remediated issues for certain registered entities including noncompliance with PRC-005-1 R2 for SCEG was filed with FERC under RC13-7-000 on March 27, 2013. The 60-day review period passed on May 26, 2013. SERC considered SCEG’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment. The prior issue involved a failure to provide maintenance and testing dates for relays, associated communication devices, voltage and current sensing devices, and DC control circuitry. The current issue involves a small number of batteries and battery chargers that were not added to the software program for maintenance and testing after the Protection System devices were installed, resulting in inadequate documentation of maintenance activities. As a result, the mitigating actions from the prior issue did not address the root cause of the instant issue. | To mitigate this issue, SCEG: 1) performed and documented maintenance activities on the batteries, as described in SCEG’s PRC-005 maintenance and testing program; 2) developed and conducted training to remind technicians of proper testing, maintenance, and documentation processes and to help ensure that similar future issues are quickly identified and corrected; 3) conducted periodic management reviews of PRC-005 applicable substations. This periodic review compares two different data sets to ensure SCEG accounts for all batteries; 4) enhanced automated quarterly battery reports to identify documentation errors; 5) focused training on reinforcing documentation processes such that inspectors have a clearly defined path for reporting erroneous or missing data discovered in the field; and 6) developed a workflow process to ensure uniformity across both regions, define roles and responsibilities, and to serve as a permanent reference document.
2015-03-31 | SERC Reliability Corporation (SERC) | Tennessee Valley Authority (TVA) | NCR01151 | SERC2014014106 | PRC-005-1.1b | R2 | On July 7, 2014, TVA submitted a Self-Report stating that, as a Generator Owner, it had an issue with PRC-005-1.1b R2. TVA could not provide evidence that all Protection System devices were maintained and tested within the defined intervals. On April 15, 2014, during a review of performance dates for preventive maintenance activities, TVA Browns Ferry Nuclear (BFN) personnel identified a missed maintenance interval of 26 weeks plus a 45 day grace period for a battery and charger. The scheduler mishandled a change in the scheduled maintenance, which resulted in TVA performing its maintenance and testing late. The scheduler set the date without regard to the previous preventative maintenance performance date, and therefore, had no logical basis for the date set. TVA performed the preventative maintenance nine days after required by the defined interval. TVA performed the preventative maintenance activities on April 15, 2014, immediately upon discovering the missed interval. Before that, TVA last performed the activities on August 21, 2013. TVA reported owning the following Protective System devices: 20,906 protective relays, 1,374 associated communication systems, 28,259 voltage and current sensing devices, 446 station batteries, 541 station battery chargers, and 20,906 DC control circuits. Of these devices, TVA maintained or tested one out of 446 station batteries (0.22%) and one out of 541 station battery chargers (0.18%) outside of the defined intervals. In total, TVA maintained or tested two out of 72,432 Protection System devices (0.0028%) outside of the defined intervals. This issue lasted from April 6, 2014, when TVA failed to maintain Protection System devices within the defined interval through April 15, 2014, when TVA completed preventative maintenance on the missed Protection System devices. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). TVA’s failure to maintain the station battery and battery charger within the defined intervals could lead to the equipment malfunctioning. However, the 24VDC bus is equipped with a low-voltage alarm in a control room that TVA manned on a 24-hour basis. The appropriate procedural response to this alarm would have been to dispatch personnel to the communications battery room to investigate the cause. No voltage alarms associated with the missed battery went off for the duration of the issue. TVA completed the annual preventative maintenance on November 8, 2013, which was in the interim between its quarterly preventative maintenance. On April 15, 2014, TVA completed the quarterly preventative maintenance. On both occasions TVA did not discover any maintenance or operability issues with the station battery or charger. The involved devices did not experience any failures during the issue period, which lasted a total of nine days. No harm is known to have occurred. A Notice of Confirmed Violation covering violations of PRC-005-1 R2 for TVA was filed with FERC under NP09-36-000 on September 25, 2009. On October 23, 2009, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering two violations of PRC-005-1 R2.1 for TVA was filed with FERC under NP10-180-000 on September 30, 2010. On October 29, 2010, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1 R2; R2.1 for TVA was filed with FERC under NP13-5-000 on October 31, 2012. On November 29, 2012, FERC issued an order stating it would not engage in further review of the Notice of Penalty. A Settlement Agreement covering violations of PRC-005-1b R2 for TVA was filed with FERC under NP14-4-000 on October 30, 2013. On November 29, 2013, FERC issued an order stating it would not engage in further review of the Notice of Penalty. SERC considered TVA’s compliance history and determined that the instant issue was appropriate for Compliance Exception treatment because while the instances were of the same Standard and Requirement, TVA’s internal controls limited the scope of and duration of the issue. TVA had implemented a regular review of performance dates for preventive maintenance activities, which allowed TVA to detect the issue within nine days of missing the interval, and immediately implemented corrective actions by performing the required maintenance activities on the two devices. TVA had a low voltage alarm for the battery at issue, which would have alerted it to any problems with the battery. TVA's prior violations involved significantly more Protection System devices and the duration of those violations were significantly longer. | To mitigate this issue, TVA: 1) removed the individual who processed the subject preventative maintenance change request (PMCR) from PMCR duties; 2) performed an extent of condition review of PMCRs performed by the same individual, and identified no additional occurrences; 3) briefed all BFN work management personnel responsible for scheduling preventative maintenance and implementing PMCRs; 4) revised descriptions for all applicable BFN NERC preventative maintenances to start with "FERC" to ensure personnel are aware when they are dealing with a NERC regulated preventative maintenance; 5) regularly completed compliance verifications since they were resumed for March 2014; 6) shared lessons learned with Nuclear Power Group peers and made lessons learned available to all TVA NERC compliance program managers; 7) revised PRC-005 preventative maintenance compliance verification process to require: (a) initiation of corrective actions when issues are identified; and (b) that dated documentation of each completed verification is provided; 8) revised its compliance program document to include performance of compliance verifications of PRC-005; and 9) performed communication and training required by an approved change management plan.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Arkansas Electric Cooperative Corporation (AECC) | NCR01060 | SPP2013012620 | PRC-008-0 | R2 | On July 11, 2013, AECC submitted a Self-Report stating that, as a Distribution Provider and Transmission Owner, it had an issue of noncompliance with PRC-008-0 R2 because it did not test two of its 64 (3.1%) UFLS relays within the five year interval defined in its Protection System Maintenance and Testing Program (Program). The root cause of the issue of noncompliance was AECC‘s lack of employee oversight of the UFLS equipment testing schedule reviews. The issue of noncompliance began July 31, 2009, when the first UFLS relay should have been tested to fall within the defined interval and ended October 8, 2012, the date of the last UFLS relay test. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Only two of AECC’s 64 (3.1%) UFLS relays, at two substations, were not tested within the five year interval. Subsequent testing of the two UFLS relays found the relays to be fully operational and would have functioned as expected if a load shedding event had occurred. The load under UFLS control at the two substations is approximately 16.5 MW on peak and represents only 2.0% of the designated load shed of AECC’s UFLS program. No actual harm occurred. AECC does not have prior violation history. | To mitigate this issue of noncompliance, AECC: 1. revised the Program to improve the process of reviewing the UFLS test schedule; and, 2. confirmed both relays had been properly tested. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Grand River Dam Authority (GRDA) | NCR01101 | SPP2014013865 | TOP-002-2.1b | R11 | During a Compliance Audit conducted from May 12, 2014, through May 15, 2014, SPP RE determined that GRDA, as a Generator Operator, Load-Serving Entity, and Transmission Operator, had an issue of noncompliance with TOP-002-2.1b R11 because it did not use identical seasonal System Operating Limits (SOLs) for common facilities with neighboring Transmission Operators. GRDA determined its seasonal SOLs based on its Facility Ratings, which are based upon the most limiting element of the facility. GRDA kept the most limiting elements of its facilities on a spreadsheet. GRDA provided its neighboring Transmission Operators with its SOLs on a different spreadsheet. During the audit, SPP RE noticed discrepancies between the two spreadsheets (8 out of 17 sampled facilities had mismatched SOLs). Therefore, GRDA could not demonstrate that it was using identical SOLs with its neighboring Transmission Operators. The root cause of the issue of noncompliance was a lack of documentation consistency. The issue began on March 11, 2014, and ended on December 22, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Although wrongly reported SOLs can lead to facilities being operated above their actual ratings, most of the SOLs GRDA provided its neighboring TOPs were below the facilities’ actual ratings. Only two of the wrongly reported SOLs exceeded the actual rating. Furthermore, of the SOLs that exceeded the actual facility rating, the largest discrepancy was 15 MVA. Upon a subsequent inquiry by SPP RE, GRDA attested that historical SCADA data showed that none of its facilities experienced operations that exceeded their actual ratings. No actual harm occurred as a result of this issue of non-compliance. No violation history. | To mitigate this issue, GRDA: 1. Verified current GRDA SOLs on common facilities with SPP, as its Balancing Authority and Reliability Coordinator, and affected neighboring TOPs; 2. Updated the GRDA’s document # 6200Facility Ratings Process document to clarify steps for the coordination with neighboring TOPs of identical SOLs for common facilities; and 3. Documented that the responsible engineering staff have read and understand the updated GRDA’s document # 6200 Facility Ratings Process procedural steps. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | Grand River Dam Authority (GRDA) | NCR01101 | SPP2014013874 | TOP-008-1 | R2 | During a Compliance Audit conducted from May 12, 2014, through May 15, 2014, SPP RE determined that GRDA, as a Transmission Operator, had an issue of noncompliance with TOP-008-1 R2 because it did not operate to prevent the likelihood that a disturbance, i.e., loss of a Catoosa autotransformer would result in a System Operating Limit (SOL) violation. On December 3, 2013, GRDA became aware that the autotransformers at its Catoosa substation would exceed their emergency ratings (188 MVA) should loss of the other autotransformer occur (only two of the three autotransformers were in service). GRDA’s Reliability Coordinator (RC) contacted GRDA regarding the potential SOL violation and suggested that GRDA place a third autotransformer at the Catoosa substation in service. GRDA notified the RC that it had an operating directive in place to open a power circuit breaker at the Claremore substation to prevent the SOL violation, should it lose one of the autotransformers. The December 3, 2013 RTCA provided by GRDA showed that the post contingency loading on the autotransformers (207.9 MVA) was in excess of the emergency rating of the autotransformers (188 MVA) for loss of one of the two autotransformers in service. GRDA’s operating directive did not indicate that it was safe to exceed the autotransformer emergency rating for any length of time. The root cause of the issue of noncompliance was a lack of a fully vetted procedure. The issue began on December 3, 2013, and ended on September 15, 2014. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). GRDA did have an operating directive in place to prevent the likelihood of an SOL violation caused by loss of a Catoosa autotransformer. However, the operating directive was ineffective in preventing an immediate SOL violation, i.e., the remaining Catoosa autotransformer exceeding its emergency rating by 10%. GRDA has since indicated that the autotransformers at Catoosa can exceed their Emergency rating by 111% for two (2) hours before being damaged. Additionally, SCADA alarms (Level 1 = 135 MVA, Level 2 = 150 MVA, Level 3 = 165 MVA, Level 4 = 188 MVA) are in place that would provide notification to system operators in the event of an impending transformer overload. GRDA system operators would under most overload conditions have sufficient time to implement mitigating measures. No Violation History. | To mitigate this minimal risk instance of noncompliance, GRDA: 1. Updated its SOL Process to address how System Operators are to handle N-1 SOL violations in real-time; 2. Updated its Operations Planning Process to include Next-day system studies performed by System Operators and procedural steps associated with the study. 3. Updated its GRDA Facility Rating Methodology to include time limit for exceeding emergency limits. 4. Trained responsible system operation staff on updated processes. 5. Trained responsible engineering staff on updated processes. 6. Updated Transmission Operating Directive TOD or operating guide for exceeding the Catoosa Autotransformers emergency rating that includes three limits, (Normal, emergency and short term emergency) and time limits for exceeding emergency limits. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-Tulsa) | NCR06038 | SPP201000204 | FAC-001-0 | R1; R1.1, R1.2, R1.3 | On January 13, 2010, United States Corps of Engineers-Tulsa District (COE-Tulsa) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R1, R1.1, R1.2, R1.3, (SPP201000204). Specifically, the COE-Tulsa does not document, maintain, and publish facility connection requirements (FAC-001-0 R1). The root cause of the issue of noncompliance is because COE-Tulsa has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE- Tulsa does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-Tulsa does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-Tulsa’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities, an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred since the issue of noncompliance start date. The COE-Tulsa has no relevant compliance history. | To mitigate this issue, COE-Tulsa will complete the following mitigation activities by October 30, 2015: 1) develop facility connection requirements addressing all requirements and subrequirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-Tulsa) | NCR06038 | SPP201000205 | FAC-001-0 | R2; R2.1, R2.1.1, R2.1.2, R2.1.3, R2.1.4, R2.1.5, R2.1.6, R2.1.7, R2.1.8, R2.1.9, R2.1.10, R2.1.11, R2.1.12, R2.1.13, R2.1.14, R2.1.15, R2.1.16 | On January 13, 2010, United States Corps of Engineers-Tulsa District (COE-Tulsa) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R2, et seq. (SPP201000205). Specifically, the COE-Tulsa does not document, maintain, and publish facility connection requirements (FAC-001-0 R2, et. seq). The root cause of the issue of noncompliance is that COE-Tulsa has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE- Tulsa does not believe it is a Transmission Owner and it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-Tulsa does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-Tulsa’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation, and approval would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-Tulsa has no relevant compliance history. | To mitigate this issue, COE-Tulsa will complete the following mitigation activities by October 30, 2015: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Little Rock District (COE-LR) | NCR06037 | SPP201000202 | FAC-001-0 | R1; R1.1, R1.2, R1.3 | On January 18, 2010, United States Corps of Engineers-Little Rock District (COE-LR) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R1, R1.1, R1.2, R1.3, (SPP201000202). Specifically, the COE-LR does not document, maintain, and publish facility connection requirements (FAC-001-0 R1). The root cause of the issue of noncompliance is because COE-LR has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-LR does not believe it is a Transmission Owner, it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-LR does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-LR’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities, an extensive evaluation and approval process would be necessary for any interconnection requests from outside entities. No actual harm has occurred since the issue of noncompliance start date. The COE-LR has no relevant compliance history. | To mitigate this issue, COE-LR will complete the following mitigation activities by October 7, 2015: 1) develop facility connection requirements addressing all requirements and subrequirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | United States Corps of Engineers-Tulsa District (COE-LR) | NCR06037 | SPP201000203 | FAC-001-0 | R2; R2.1, R2.1.1, R2.1.2, R2.1.3, R2.1.4, R2.1.5, R2.1.6, R2.1.7, R2.1.8, R2.1.9, R2.1.10, R2.1.11, R2.1.12, R2.1.13, R2.1.14, R2.1.15, R2.1.16 | On January 18, 2010, United States Corps of Engineers-Little Rock District (COE-LR) submitted a Self-Certification as a Transmission Owner because it had an issue of noncompliance with FAC-001-0 R2, et seq. (SPP201000203). Specifically, the COE-LR does not document, maintain, and publish facility connection requirements (FAC-001-0 R2, et. seq). The root cause of the issue of noncompliance is that COE-LR has never needed such interconnection requirements in the past and does not believe it needs such documentation going forward. Additionally, because COE-LR does not believe it is a Transmission Owner and it believes it does not need to comply with FAC-001. | This issue of noncompliance posed a minimal risk and did not pose a serious or substantial risk to the reliability of the Bulk Power System (BPS). Although the COE-LR does not document, maintain, and publish facility connection requirements, it is unlikely that its transmission facilities would be expanded to provide additional connections to the BPS. COE-LR’s transmission facilities are limited to the substations providing interconnection for its hydro-electric facilities. These facilities are located adjacent to its hydroelectric facilities and offer limited access for expansion. Because Congress must approve any expansion of the Corps facilities an extensive evaluation, and approval would be necessary for any interconnection requests from outside entities. No actual harm has occurred due to this issue of noncompliance. The COE-LR has no relevant compliance history. | To mitigate this issue, COE-LR will complete the following mitigation activities by October 7, 2015: 1) develop facility connection requirements addressing all subrequirements and requirements of the standard; and, 2) publish these requirements.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE-Kansas City District | NCR01357 | SPP201100459 | PRC-005-1 | R2; R2.1 | On January 18, 2011, USACE-Kansas City submitted a Self-Report stating that, as a Generator Owner and Transmission Owner, it had an issue of noncompliance with PRC-005-1 R2, inclusive of R2.1 because it did not have evidence that some Protection System devices were maintained and tested within the intervals defined in its Protection System Maintenance and Testing program (Program) (Version 2, dated 08/04/10). Specifically, USACE-Kansas City did not have evidence of performing its yearly microprocessor based relays tests on 27 of its 93 relays for the year of 2010. USACE-Kansas City’s Program requires USACE-Kansas City to perform yearly 1) microprocessor relay self-tests; 2) meter accuracy verification; and 3) output trip circuit verifications to ensure D.C. circuitry connectivity with its breakers. USACE-Kansas was not able to provide evidence that it had performed these tests on 27 of its 93 relays for the year 2010. The root cause of the issue of noncompliance was USACE-Kansas City’s employees’ inattention to ensure the microprocessor based relays were tested according to USACE-Kansas City’s Program. The issue of noncompliance began on January 1, 2010, and lasted until July 18, 2011 (the date of completion of testing and verification of the microprocessor based relays). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. Of the 93 total relays located at USACE Kansas City’s two substations, only 27 were implicated in the self-report. When USACE-Kansas City tested the microprocessor relays to mitigate the issue of noncompliance, it verified that all 27 relays were in proper working order. Additionally, these microprocessor relays were commissioned in 2007 and installed with back-up relays. These microprocessor relays are monitored by a USACE-Kansas City operator in the operations center 24x7 and there are alarms if the relays become inoperable. Although USACE-Kansas City’s testing interval for its microprocessor relays is yearly, Table 1 of the NERC Technical Reference, applicable at the time of the issue of non-compliance, proposed a maximum verification interval of ten (10) years for thoroughly monitored relays. No actual harm is known to have occurred. No Violation History. | To mitigate this issue and prevent recurrence, USACE-Kansas City: 1) Completed relay self-tests and output trip circuit verification on all the relays; 2) Performed relay meter accuracy verification tests (04/18/2011); 3) Evaluated its Program and revised the intervals; 4) Developed a revised testing schedule for the two facilities in accordance with its revised Program; and, 5) Completed relay tests within the frequency required by the new Program. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Southwest Power Pool Regional Entity (SPP RE) | USACE-Kansas City District | NCR01357 | SPP2011008131 | VAR-002-1.1b | R3; R3.1 | On September 19, 2011, USACE-Kansas City submitted a Self-Report stating that, as a Generator Owner and Generator Operator, it had an issue of noncompliance with VAR-002-1.1b R3, inclusive of R3.1 because it did not notify its Transmission Operator (TOP) within 30 minutes of the status change of a power system stabilizer (PSS) at the Stockton hydro facility. On February 10, 2011, USACE-Kansas City staff reported to its TOP that the status of the PSS at Stockton was “off.” During an August 3, 2011, Power Operations and Maintenance review at Stockton, USACE-Kansas City staff noticed that the Stockton PSS was in the “on” position. USACE-Kansas City staff could not establish when the PSS was switched on and could not confirm that its TOP had been notified of the change in status. On August 3, 2011, at 15:15, USACE-Kansas City changed the status of the Stockton PSS to “off,” and notified its TOP. The root cause of this issue of noncompliance was the failure of the Stockton operators to verify the status of the PSS during plant operations, and notify the TOP of a status change. This issue of noncompliance began sometime after February 10, 2011, when USACE-Kansas City failed to report to its TOP that the Stockton PSS was on and ended August 3, 2011, when USACE-Kansas City switched the Stockton PSS to the off position and informed its TOP of the status change. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. USACE-Kansas City’s TOP had previously provided the USACE-Kansas City’s Stockton facility with an exemption from its PSS requirements; was not relying on the Stockton PSS for voltage support; and was not expecting any notifications regarding the status of the Stockton PSS. Furthermore, USACE-Kansas City’s Stockton facility is a small hydroelectric power plant (50 MW) capable of providing minimal reactive support to the BES. No actual harm is occurred while the PSS was switch in the “on” position. No Violation History. | To mitigate this issue, USACE-Kansas City: 1) determined required PSS settings and applied the correct setting; 2) informed the TOP of the PSS status change; 3) provided information tags on the PSS to indicate the required position; and, 4) informed plant staff of the appropriate PSS status and reporting requirements. SPP RE has verified the completion of all mitigation activity.
2015-03-31 | Texas Reliability Entity (Texas RE) | South Houston Green Power, LLC (SHGP) | NCR11310 | TRE2014014440 | PRC-005-1b | R1; R1.1 | During a Compliance Audit conducted from October 28, 2014 through November 5, 2014, Texas RE determined that SHGP, as a Generator Owner (GO), had an issue with PRC-005-1b R1 and R1.1. Specifically, SHGP’s Maintenance and Testing Program did not have a defined interval or basis for testing Instrument Transformers from February 1, 2013 to April 29, 2014. Following the Compliance Audit, Texas RE also determined that while SHGP did define test intervals for its Instrument Transformers on April 29, 2014, SHGP did not define a basis for these test intervals until December 1, 2014. After the plant was acquired under new ownership in February 2013, SHGP revised the Protection System Maintenance Program; however, it did not make any adjustments to the interval and basis for testing instrument transformers in the revision. The root cause was determined to be a failure to make these adjustments. Texas RE determined the duration of the issue to be from February 1, 2013, when SHGP registered as a GO, through December 1, 2014, when SHGP defined an interval and basis for its test intervals. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). This issue is documentation-based, and did not pose any Operational risk to the BPS. During the Audit, Texas RE found that the Instrument Transformers had been tested in 2008. According to SHGP’s current testing intervals, these Instrument Transformers were not due for testing again until 2020. Additionally, while SHGP’s generation totals at approximately 1100 MW, throughout the issue period, SHGP only exported a maximum of 485 MW from its Private Use Network. No actual harm is known to have occurred. SHGP asserts that it has not experienced any trips or mis-operations due to the Instrument Transformers over the duration period. Texas RE considered SHGP’s compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SHGP has taken the following actions: 1) updated its Maintenance and Testing Program to include defined testing intervals for its Instrument Transformers; and 2) updated its Maintenance and Testing Program to include a defined basis for the testing intervals of its Instrument Transformers. SHGP will complete the following mitigating activity by April 1, 2015: 3) develop and implement a new Maintenance and Testing Program, designed to address the requirements set forth in the upcoming NERC Reliability Standard, PRC-005-2. The new Standard defines set intervals for Protection System equipment and serves as an industry basis.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Arizona Public Service Company (AZPS) | NCR05016 | WECC2014014406 | INT-004-2 | R2 | On October 24, 2014, AZPS submitted a Self-Report stating that, as a Balancing Authority (BA), Transmission Operator (TOP), and Purchase-Selling Entity (PSE) it had an issue of INT-004-2 R2.. During an internal compliance review, AZPS found that it had an inconsistent interpretation of the requirements of INT-004-2. Operators would make adjustments to dynamic interchange schedules for the next available scheduling hour and future hours when a generator would trip and the energy profile would go to zero. Similarly, when the generator would return to service, the next available scheduling hour and the future hours would be adjusted to reflect the schedule returning to full. However, when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%, the required adjustments were not always performed. Similarly, when the average energy profile in an hour was less than or equal to 250 MW and in that hour the actual hourly integrated energy deviates from the hourly average energy profile indicated on the tag by more than +/- 25 megawatt-hours, the required adjustments were not always performed. A WECC Subject Matter Expert (SME) review the information provided by AZPS and found that AZPS provided updates for electronic tags for Dynamic Interchange Scheduling (tags) for instances of generator loss or reductions, it failed to update the tags when certain outside Load Serving Entity’s (LSEs) executed energy purchases and/or sales when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%. Likewise, when the average energy profile in an hour was less than 250 MW and in that hour the actual hourly average profile indicated on the tag deviated by more than +/- 25%, the entity did not update the tag. Therefore the SME determined AZPS had a possible issue with INT-004 R2. The SME forwarded this information to Enforcement. Enforcement reviewed the information provided by AZPS and the SME. Enforcement determined that AZPS failed to ensure that the tag for the Dynamic Interchange Schedule was updated for the next available scheduling hour and future hours when the average energy profile in an hour was greater than 250 MW and in that hour the actual hourly integrated energy deviated from the hourly average energy profile indicated on the tag by more than +/- 10%. Likewise, when the average energy profile in an hour was less than 250 MW and in that hour the actual hourly average profile indicated on the tag deviated by more than +/- 25%, the entity did not update the tag. As a result, AZPS has an issue with INT-004-2 R2. AZPS has had multiple instances of noncompliance of this standard beginning August 27, 2008, the effective date of this standard and is ongoing . AZPS does not have a history of violations for INT-004-2. The root cause of this issue was lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. AZPS failed to ensure that the tag for a Dynamic Interchange Schedule was updated for the next available scheduling hour and future hours which could potentially result in transmission congestion within the BA area and/or across interconnections with neighboring entities. The amount of congestion that could occur is not possible to calculate given the lack of data and the limitless scenarios that could be played out. Additionally, AZPS has had numerous instances in which the tags were not updated when required and is not able to catalog all of the events or their severity. For these reasons, the impact severity is based upon a cascading loss of more than three BES elements of >200kV. The root cause of this issue was lack of compliance understanding. AZPS implemented strong preventative and detective controls to prevent a cascading loss of more than three BES elements of >200kV. Specifically, AZPS implemented real time monitoring of its transmission system via an energy management system (EMS) by NERC certified system operators on a continuous basis. Should transmission congestion begin to occur, the EMS will provide indication by real time quantities and, potentially, alarms for the operators. The operators will then act to mitigate congestion by reducing generation. This is further bolstered by the entity’s training programs and procedures for mitigating transmission congestion. Further, AZPS implemented strong detective controls to detect if a cascading loss of more than three BES elements of >200kV occured. Specifically, it implemented real time monitoring of its transmission system via an energy management system (EMS) by NERC certified system operators on a continuous basis. Additionally, its operators are positioned and trained to immediately respond to any directive issued by the Reliability Coordinator (RC) upon notification of a potential contingency scenario. Furthermore, AZPS implemented procedures for its operators to mitigate any transmission congestion issues by reducing generation and provided training to its NERC certified system operators on the procedures as well as monitoring and alarming tools. As generation is reduced, AZPS’ operators are trained to update the electronic tags relative to the generation reduction amount. For these reasons, and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the reliability of the BPS. | To mitigate this issue, AZPS completed the follow mitigation activities: 1) developed an automated process that accesses future hour forecasted schedule values and automatically updates the dynamic tags every hour. This automation is monitored and alarmed if it should fail; and 2) Developed a training module to instruct the staff on these requirements; the automated process and the manual process to follow should the automation fail. This training module was delivered to all Real-time Traders.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Public Utility District No.1 of Clark County (CKPD) | NCR05334 | WECC2014014463 | PER 005-1 | R1 | During a Compliance Audit conducted from November 3, 2014 through November 14, 2014, WECC determined that CKPD, as a Transmission Operator (TOP) , had an issue of PER-005-1 R1. The audit period for this audit was October 28, 2011 to August 1, 2014. During the onsite audit, the WECC Auditors found a possible issue of PER-005-1 R1. Specifically, PER-005-1 R1 requires CKPD to use a “Systematic Approach to Training (SAT) to establish a training program for the BES company-specific reliability-related tasks performed by its system operators and to implement the program” and R1.1 requires CKPD to “create a list of BES company-specific reliability related tasks performed by its System Operators.” After several data requests and interviews, the WECC Auditors determined that the documentation of CKPD’s SAT is insufficient to meet the intended requirements of PER-005 R1. Firstly, because it does not include documentation of CKPD’s analysis of its training needs, which pursuant to FERC Order 742 is considered the foundational element of a SAT. Secondly, the SAT does not include a documented method for evaluating the program and making improvements as a result of this evaluation. Other than a single sentence at the end of the program document, there was no evidence that this evaluation was performed. The lack of these two things led the audit team to conclude that CKPD did not use a SAT to establish its training program during the audit period. Furthermore, the audit team found that CKPD’s list of 21 Reliability Related Tasks (RRTs) was insufficient as a list of RRTs as required by the PER-005-1 R1. This is because many of the elements in the RRT list are not tasks at all, but internal procedures. Such procedure-based tasks could possibly be viewed as RRTs if they were broken down into constituent tasks, but CKPD provided no evidence of such an approach. Also, 17 of the 21 RRTs are solely related to emergency response. Limiting the tasks to emergency actions excludes a significant number of key tasks that CKPD should consider as reliability related item to be performed during normal operations. As a result, the audit team found that CKPD did not use a SAT to establish its training program and did not create an adequate list of BES company-specific reliability related tasks performed by its System Operators. This information was forwarded to Enforcement for review. Enforcement reviewed the information provided by CKPD and the audit team. Per PER-005 R1 CKPD is required to use a “Systematic Approach to training to establish a training program for the BES Company-specific reliability related tasks performed by its System Operators”. Although CKPD has a documented Training Program, the program’s design and implementation do not rise to the level of a SAT. Specifically, CKPD could not produce documentation to demonstrate how the process was designed and developed. Further. CKPD’s RRTs cannot be described as “tasks”, but consist of general procedures. Therefore, CKPD failed to use a Systematic Approach to Training to establish its training program and has an issue with PER-005-1 R1. This issue began April1, 2013, the date PER-005-1 R1 became enforceable and is ongoing. The root cause is lack of compliance understanding. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, CKPD failed to use a Systematic Approach to Training to establish its training program and failed to create a list of BES company-specific reliability related tasks performed by its System Operators. The lack of sufficiently documented process for establishing, implementing, and evaluating its program indicates that its training program is not based on an organized and methodical system. As a result, it seems probable that CKPD’s System Operators do not have the level of training required to maintain BES reliability under all conditions. If the lack of a Systematic Approach to Training persists, the risk to the BES is that human error performed by CKPD’s System Operators will cause, contribute to, or exacerbate a system event. Further, failing to create an adequate list of BES company specific reliability related tasks for its System Operators could lead to the System Operators not receiving regular training on tasks necessary for the reliable operation of the BES. The root cause of this issue was lack of compliance understanding. Although CKPD’s documentation of its SAT is insufficient to meet the intended requirements of PER-005-1 R1, CKPD does employ outside vendors for the provision of the bulk of their System Operator training in addition to participation in annual RC restoration drills and some in-house training. Further, CKPD is relatively small in size. Its service territory covers a single county. CKPD owns 120 miles of 115kV transmission lines and less than ten miles at 69kV with an all-time system peak of 1000 MW. A system failure brought on by a lack of sufficient training would be contained within CKPD’s immediate service area and would be unlikely to have cascading effects that would impact the large interconnecting entities. For these reasons and the fact that no harm was caused, WECC determined that this issue poses a minimal risk to the BES. WECC considered CKPD's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, CKPD will complete the following mitigation activities by May 15, 2015: 1) amend its Operating Personnel Training Program to ensure that the program's design and implementation rise to the level of a Systematic Approach to Training. Specifically, CKPD will produce documentation that demonstrates how the process was designed and developed (based on a SAT); 2) CKPD will produce a list of its utility specific BES Real-Time Reliability Related Tasks that provide detail regarding activities that its System Operators would be expected to complete (instead of a list of general procedures); and 3) activities will include both emergency activities as well as normal activities expected to be performed regularly as part of the BES operations.
2015-03-31 | Western Electricity Coordinating Council (WECC) | Seattle City Light (SCL) | NCR05382 | WECC2014014497 | INT-009-2 | R1 | On December 11, 2014, SCL submitted a Self-Report stating that, as a balancing authority (BA), it had an issue of INT-009-2 R1. On November 2, 2014, SCL experienced an internet outage. During this internet outage, SCL failed to implement a 1 MW reliability curtailment for eTag SCL PWX01Z507113 CISO. The curtailment was to begin on November 2, 2014 at 1900 and was requested at 1841. The internet provider continued to accept outbound internet traffic from SCL but SCL was not able to receive inbound data. Because of the internet outage, SCL had no visibility of the eTag adjustment at the time, but was automatically approved at 1849 by an Open Access Technology International, Inc., (OATI) “Backstop” service but not actually implemented by SCL until 1940. As a result, SCL did not comply with INT-009-2 R1 for 40 minutes. The WECC Subject Matter Expert (SME) reviewed the information provided by SCL. SCL, as the sending BA, did not agree as to the magnitude of Interchange with the receiving BA for 40 minutes. The actual curtailment of energy (from 150MW to 149MW) was not implemented until internet connectivity was restored around 1940. The SME found that due to the interruption of internet service and the loss of the computer applications that depended on it, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority. The SME forwarded this information to Enforcement for review. Enforcement reviewed the information provided by the WECC SME and SCL. Enforcement determined that per INT-009 R1, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority. SCL did not agree to the magnitude of interchange with the receiving BA from 1900 to 1940, 40 minutes on November 2, 2014. The root cause of this issue was lack of technology management. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system. In this instance, SCL failed to have its Composite Confirmed Interchange identical in magnitude to that of the Adjacent Balancing Authority due to a loss of internet communications. SCL, as the sending BA, did not agree to the magnitude of interchange with the receiving BA for 40 minutes. Disagreement in the magnitude of Interchange between adjacent BAs causes the accumulation of inadvertent interchange and incorrect calculation of Net Scheduled Interchange for use in the Area Control Error (ACE) equation or in the worst cause the interconnection facilities could become overloaded. However, the amount of any overload that could occur is not possible to calculate. For these reasons, the impact severity is based upon a loss of a single BES element of >200kV. SCL implemented detective controls. Specifically, SCL implemented 24/7 hour staffing of its System Operations Control Center and Power Marketing operation, which allowed it to quickly notice degradation of certain computer applications and commence alternative actions. It leveraged its Energy Management System (EMS), which is independent of the Internet and provides SCL System Operators full situational awareness of real-time transmission limits, loadings, and alarming during this type of event. Further, SCL implemented strong compensating controls. Specifically, it implemented a redundant Internet Service Provider; however, some manual intervention was required to switch applications between internet systems. SCL had a documented emergency backup procedure, which addressed this type of event. As part of this procedure, SCL sent a WECCNet message informing the region and other BAs of SCL's internet failure requiring manual exchange of information. The backup procedure was implemented, allowing SCL's System Operators to control interchange quantities to the last known good WIT number, then manually exchange and confirm changes with neighboring BAs and PEAK RC. Additionally SCL's NERC certified System Operators are fully-trained to implement the emergency procedure. These measures and the functioning EMS allowed SCL to be aware of any significant curtailments, equipment outages, or large power flow changes occurring during an internet incident so that it could respond timely and accordingly. Based on this information and the fact that no harm was caused, this issue poses a minimal risk to the reliability of the BES. WECC considered SCL's compliance history and determined there were no relevant instances of noncompliance. | To mitigate this issue, SCL will complete the following mitigation activities by May 15, 2015: 1) Install additional workstation at System Operations Center connected to alternate ISP (Comcast guest network) as backup internet access point to log into OATI and WIT in the event of a primary or secondary ISP internet outage; System Operators review process for loss of internet and use of alternate connection, and individually log in using backup workstation to test functionality; 2) Install additional workstation at the Power Operations & Marketing (Power Marketing) floor connected to alternate ISP (Comcast guest network) as backup internet access point to log into OATI and WIT in the event of a primary or secondary ISP internet outage; Power Marketing revises its Emergency Preparedness Standard Operating Procedure (Procedure) for loss of internet and use of alternate connection; Real-Time Power Marketers review Procedure, and individually log in using backup workstation to test functionality; and 3) Implement monitoring of OATI on direct T-1 line by Uniform Resource Locator (URL) rather by Internet Protocol (IP) address to allow better monitoring of internet-based connectivity to OATI.
2015-02-26 | Florida Reliability Coordinating Council (FRCC) | Gainesville Regional Utilities (GRU) | NCR00032 | FRCC2014014491 | EOP-004-2 | R2 | During a Compliance Audit conducted from December 1, 2014 through December 3, 2014, FRCC determined that GRU, as a BA, DP, GO, GOP, TO and TOP, had a non-compliance of EOP-004-2, R2. GRU experienced an event which required its primary control center to evacuate and resume operations at its backup facility. However, GRU did not report the event (per their Operating Plan) within 24 hours of recognition of meeting an event type threshold for reporting required per Standard EOP-004-2, R2. GRU's evacuation occured on February 25, 2014, however GRU did not report that the evacuation had occurred until March 12, 2014. The root cause is that GRU failed to recognize that the evacuation of its primary control center required reporting in 24 hours The violation severity level for this noncompliance was determined to be Severe because GRU submitted the event report more than 60 hours after meeting an event threshold for reporting. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the BPS. GRU notified the Reliability Coordinator upon evacuating, and arrived at its back up control center within 19 minutes, and were operational at the backup control center within 23 minutes. Additionally, GRU's system only comprises approximately one percent of FRCC Regional transmission, and approximately one percent of the Regional load. No harm is known to have occurred. This is a case by case Compliance Exception and is not related to the Self Logging process. | To mitigate this issue, GRU: 1) GRU reported the event, although the timing was beyond the standard's requirements. 2) GRU provided additional training to its operating personnel on the recognition of reportable events and the timing requirements for reporting such events.
2015-02-26 | Midwest Reliability Organization (MRO) | City of Ames Electric Services (AMES) | NCR00972 | MRO2015014558 | EOP-004-2 | R1 | On November 25, 2014, City of Ames Electric Services (AMES), submitted a Self-Report stating that as a DP and TO, it had an issue of EOP-004-2 R1. AMES failed to update its Event Reporting procedures to include changes made to the new version of the EOP-004 Standard when it became effective on January 1, 2014. The issue began on January 1, 2014 and ended on November 25, 2014 | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The potential risk to the BPS of this finding is reduced as a result of: AMES was registered only for the DP and LSE functions until April 1, 2014 when it added the TO function for two 161kV substations. AMES has a peak load of 130MW and less than 35MW of UFLS, which means the only EOP-004-2 “Event Types” that are applicable are Damage or Destruction of a Facility and Physical Threats to a Facility, both of which were covered by AMES’s “Sabotage Reporting Procedure” and included contact information for the entity’s RC and TOP, local police, and the FBI. They were just missing updated contact information for NERC and MRO. AMES had no reportable events, and based upon its size and location, it is very unlikely that AMES could contribute to an event that would have an impact on BES reliability. There is no relevant compliance/violation history for this entity. | To mitigate this issue, AMES developed a new “Event Reporting Plan” which complies with EOP-004-2 R1 on November 25, 2014.
2015-02-26 | Midwest Reliability Organization (MRO) | ITC Midwest (ITCM) | NCR10192 | MRO2013013184 | FAC-008-3 | R6 | On August 28, 2013, ITC Midwest (ITCM) submitted a Self-Certification stating that, as a TO, it had an issue of FAC-008-3 R6. ITCM identified two equipment ratings that were incorrectly documented in its facility rating database. No incorrect facility ratings were identified. The issue began on January 1, 2013 (effective date of standard) and ended on January 15, 2014 (date facility rating database was revised). | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system (BPS). The facts and circumstances of this case are consistent with the use of good engineering judgment on behalf of ITCM to focus on the types of equipment, which are predominately the most limiting when calculating facility ratings. This is demonstrated by the fact that the pieces of equipment with rating documentation errors were not the most limiting elements in their facilities. It is also a reasonable assumption that relays and bus conductor would not be the most limiting equipment associated with a facility. ITCM has had no relevant prior violations. | To mitigate this issue, ITCM: 1) updated its facility ratings database to represent existing equipment; and 2) confirmed no facility ratings were impacted. To complete mitigation of this issue, ITCM will perform a comprehensive review of its equipment ratings by December 11, 2015.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | City of Lansing By Its Board of Water and Light (LBWL) | NCR00718 | RFC2014013622 | PRC-005-1 | R2 | On March 4, 2014, LBWL submitted a Self-Report stating that as a Distribution Provider (DP), Generator Owner (GO), and Transmission Owner (TO), it had an issue of PRC-005-1a R2. While gathering evidence for an upcoming NERC audit, LBWL discovered gaps in evidence associated with the implementation of its Protection System Maintenance and Testing Program (Program). These gaps included the completion of only some inconsistent testing of the Instrument Transformers and DC Control Circuity. Out of 735 total tests required by PRC-005-1a R2, 356 were either late or missed. Many of these tests lacked proper documentation and methodology, contained inadequately documented results, and revealed a lack of consistency in interpretation of the testing procedures. In 2011, LBWL revised its Maintenance Practices to require testing of its protective relay systems, communication systems, battery systems, and associated DC circuity and instrument transformers. Following these revisions, LBWL experienced several changes in leadership and key technical positions. This high turnover among the individuals responsible for implementing the revised Maintenance Practices led to inconsistent implementation of the Maintenance Practices and the required testing and documentation. The duration of this noncompliance is from June 9, 2011, the date by which LBWL should have performed its testing, to July 3, 2015, the date LBWL will complete its mitigating activities to remediate this noncompliance by performing the required testing. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. LBWL employs a comprehensive backup program. This backup program includes primary and back-up phase distance relaying. The primary relays are on one set of current transformers (CTs) and the backup relays are on a different set of CTs. The 138 kV circuit breakers are equipped with dual trip coils. Both the primary and secondary relays initiate the tripping of both breaker trip coils. Having the primary and backup relays on a different set of CTs reduces the likelihood of a Misoperation because if one set of CTs goes down, the relays can still get through on the other set of CTs. In addition, LBWL employs breaker-and-a-half and ring-bus configurations for its 138 kV system, which provides additional reliability and security as those reduce the likelihood of tripping and a Misoperation. LBWL also has a SCADA/EMS system with EMS alarming which monitors station DC battery potential as well as currents and voltages at all 138 kV busses and transmission lines. This monitoring system allows for quick detection and remediation of a potential Misoperation. Finally, LBWL’s entire Bulk Electric System (BES) only consists of a 138 kV loop feeding approximately 300 MW of load that has a minimal impact on the BES. Although LBWL has a prior violation of PRC-005-1 R2, that violation is distinguishable from the instant noncompliance. LBWL’s prior violation occurred in 2008 and arose from an inadvertent scheduling error in testing its relays. The scheduling was in error by a calendar quarter and put the testing out of sync such that 15% of LBWL’s relays were not tested on time. In contrast, this noncompliance stemmed from improper implementation of LBWL’s revised Maintenance Practices and resulted from a combination of leadership changes, changes in testing methodology, and the unavailability of key employees. As a result of the differences in facts and circumstances, ReliabilityFirst did not consider LBWL’s violation history as a factor warranting an alternative disposition method or a monetary penalty. | To mitigate this issue, LBWL will complete the following mitigation activities by July 3, 2015: 1) hired a maintenance engineer with responsibility for reliability compliance to work with LBWL’s Electrical Test Group (ETG); 2) the maintenance engineer worked with the ETG to set up a schedule of tests to bring each facility in violation back into compliance; 3) committed to test any Relays, Communications Systems, Voltage and Current Sensing Devices, Batteries and Chargers, and DC Control Circuitry in violation; 4) the maintenance engineer is responsible for confirmation and review of all tests and filing of all test results; and 5) the maintenance engineer is also responsible for overseeing all LBWL BES facilities’ maintenance responsibilities and ensuring that ETG staff comply with all testing requirements. Mitigation will take until July 2015 because of the number of tests LBWL must conduct and because LBWL is avoiding testing during periods of peak demand.
2015-02-26 | ReliabilityFirst Corporation (ReliabilityFirst) | Ebensburg Power Company (Ebensburg) | NCR08051 | RFC2014014206 | PRC-005-1b | R2 R2.1 | During the Compliance Audit conducted July 16, 2014 through July 24, 2014, ReliabilityFirst determined that Ebensburg, as a Generator Owner (GO) had an issue of PRC-005-1b R2 and R2.1. Ebensburg could not provide evidence that it completed maintenance and testing for its current transformers (CTs) and potential transformers (PTs) from 1990 until 2013. Specifically, Ebensburg had tested its plant’s CTs and PTs during the commissioning of the plant in 1990. After those tests in 1990, Ebensburg did not test its CTs and PTs again until 2013. From 1990 to 2012, Ebensburg’s Maintenance and Testing Program only required testing of CTs and PTs during installation of equipment and when problems were identified with the equipment. Ebensburg’s CTs and PTs did not experience any problems from 1990 to 2012 and therefore were not tested. On April 18, 2012, Ebensburg revised its Program, implemented the Revised Program and changed the testing frequency of the plant’s CTs and PTs to a ten year interval in accordance with NERC requirements. Ebensburg performed the required testing of all CTs and PTs during Ebensburg’s scheduled spring outage from April 21 to April 27, 2013. The duration of this noncompliance is from April 18, 2012, the date Ebensburg revised its Program to change the testing procedures and frequency of the plant’s CTs and PTs, to May 30, 2013, the date Ebensburg completed the testing of all CTs and PTs with supporting documentation to remediate this noncompliance. | This issue posed a minimal risk and did not pose a serious or substantial risk to the reliability of the bulk power system based on the following factors. Throughout the duration of the noncompliance, Ebensburg maintained and tested various components of CTs and PTs as part of the routine maintenance and testing of the plant’s electrical systems, particularly the generation protective systems. Although Ebensburg did not conduct the specific CTs and PTs testing on time, the routine maintenance tests and checks Ebensburg conducted decreased the risk posed by the instant noncompliance. Also, the failure rate of CTs and PTs is generally very low. Moreover, the tests, when performed, demonstrated that the CTs and PTs were operating properly. Finally, Ebensburg is a 50 MW generating unit that has a minimal impact on the Bulk Electric System (BES). Although Ebensburg has a prior violation of PRC-005 R2 (See Violation ID No. RFC200800094), that violation is distinguishable from the instant noncompliance. Ebensburg’s prior violation of PRC-005 R2 occurred in 2008, involved Ebensburg missing six months of battery tests, and occurred because of a breakdown in the facility’s preventative maintenance system process which is used to issue work orders for the monthly tests. In contrast, this noncompliance arose because Ebensburg’s Preventative Maintenance and Testing Program in place from 1990 to 2012 did not require interval testing of Ebensburg’s CTs and PTs. As a result of the differences in facts and circumstances, ReliabilityFirst did not consider Ebensburg’s violation history as a factor warranting an alternative disposition method or a monetary penalty. | To mitigate this issue, Ebensburg: 1) performed the required testing of all CTs and PTs, with supporting documentation, during Ebensburg’s scheduled spring outage from April 21 to April 27, 2013; 2) started work on establishing a monthly system to review the latest versions of NERC Standards that apply to Ebensburg as a GO and a Generator Operator. These monthly reviews will identify any changes that may need to be made to keep Ebensburg in compliance with the updated procedures and requirements; and 3) implemented this new monthly check system in October 2014. This system will ensure that Ebensburg continues to test in accordance with testing intervals listed in Ebensburg’s Revised Program and in accordance with the relevant Reliability Standards.
2015-02-26 | Western Electricity Coordinating Council (WECC) | Wheat Field Wind Power Project, LLC (WFWP) | NCR10318 | WECC2014014376 | PRC-005-1.1b | R2 | On October 6, 2014, WFWP submitted a Self-Report stating that as a, Generator Operator and Generator Owner, it had an issue with PRC-005-1.1b R2. In the Self-Report, WFWP reported that it failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1.1b R2. Specifically, WFWP’s Protection System maintenance and testing program in effect during June 2014 required that visual substation inspections were to be conducted monthly. WFWP conducted the monthly inspection for June 2014 nine days outside of the interval described in its maintenance and testing program. As a result, WFWP reported that it had a possible issue with PRC-005-1.1b R2. An audit was conducted WFWP concluding on November 19, 2014. This issue was reviewed by the auditors and was initially dismissed due to WFWP's adoption of PRC-005 version 2 on July 7, 2014, which allows up to four months for battery inspections. As part of NERC’s review of the dismissal, NERC officially rejected the dismissal on December 29, 2014. NERC’s rejection of the dismissal is based on the timeline of the issue. WFWP failed to perform the monthly inspection in June and did not adopt version two until July 7, 2014 or perform the inspection until July 9, 2014. In January 2015, a WECC Subject Matter Expert (SME) began a review of WFWP’s Self-Report. As a result of the examination, the SME determined that WFWP had a possible issue with PRC-005-1.1b R2. Specifically, the SME determined that WFWP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program. WFWP identified that the root cause of the issue was human error in that the maintenance was simply performed late. The SME forwarded the findings and Self-Report to Enforcement for review. Enforcement reviewed the Self-Report and SME findings. Based on this review, Enforcement determined that WFWP had an issue with PRC-005-1.1b R2. Specifically, Enforcement determined that WFWP failed to provide evidence that it maintained and/or tested a battery system in accordance with its maintenance and testing program as required by PRC-005-1.1b R2. Enforcement determined that the issue began on July 1, 2014, the day that the monthly requirement to perform the visual substation inspection for June expired. Enforcement also notes that the issue ended on July 7, 2014, the date that the entity adopted version 2 of the standard and that WFWP performed the inspection on July 9, 2014. | WFWP failed to provide evidence that Protection System devices were maintained and tested within the defined intervals of its Protection System maintenance and testing program. Specifically, the monthly visual substation inspection for June 2014 was conducted nine days late. If devices are not tested per the program defined by the entity, the devices cannot be certified to operate as planned to interrupt disturbances that may damage the transmission system or generating units. However, WFWP is only a 96.6 MW wind power facility, limiting the effect that it has on the BPS. Additionally, in this instance, WFWP conducted the testing only nine days after the interval described in its maintenance and testing program and this was a single occurrence of missed maintenance. All other required monthly substation inspections were conducted and documented at the correct intervals, limiting the probability of any potential harm to the BPS. WFWP also developed and implemented a plan to transition to PRC-005 version 2 on July 7, 2014, only seven days after the missed maintenance occurred. The intervals of the maintenance performed by WFWP would have been compliant under the new PRC-005 version 2 maintenance and testing plan. For these reasons, WECC determined this issue posed minimal risk to the reliability of the BPS. | To mitigate this issue, WFWP: 1) adopted version 2 of PRC-005 for the battery permitting up to four months for the battery inspection to be completed.
2015-02-26 | Western Electricity Coordinating Council (WECC) | California Independent System Operator (CISO) | NCR05048 | WECC2014014368 | EOP-001-2.1b | R5 | On September 25, 2014, CISO submitted a Self-Report citing possible noncompliance with EOP-001-2.1b R5. Specifically, CISO reported that when it performed its annual review and update of emergency plan, two of CISO’s twenty-two neighboring entities were inadvertently omitted from the distribution list, resulting in those entities not receiving updated copies of CISO’s emergency plans. On November 6, 2014, a WECC SME reviewed the Self-Report and discussed the possible noncompliance with CISO. The SME determined that CISO updated its emergency plans in January, February and December of 2013. After the December update, CISO failed to distribute its new plan to Hetch Hetchy Water and Power (“HHWP”) and Western Area Power Administration–Desert Southwest Region (“WALC”), two neighboring entities that CISO was required to distribute the updated plan to. The SME further determined that the changes made in the December revision were minor. The SME found that CISO had a possible noncompliance with EOP-001-2.1b R5, and forwarded the findings to Enforcement for review. Enforcement reviewed the Self-Report and the SME’s findings and determined that CISO failed to provide a copy of its updated emergency plans to its neighboring Transmission Operators (“TOPs”) and Balancing Authorities (“BAs”). Such failure is a noncompliance with EOP-001-2.1b R5. Enforcement further determined that this issue began on December 23, 2013, the date CISO should have provided its emergency plans to HHWP and WALC, and continued through September 4, 2014, the date that CISO did provide the update to these neighboring entities. | CISO failed to provide a copy of its updated emergency plans to its neighboring BAs/TOPs which could potentially result in a miscommunication between the entities with regard to emergencies. Given that the types of emergencies addressed by the plans are numerous and vary in scope and magnitude, it is impossible to assess the exact impact to the BES. However, given that all neighboring BAs and TOPs did receive previous copies of the emergency plans, and due to the nature of the minor changes in the December revision, the impact to the BES would be limited to misunderstandings of small details associated with emergency response. The root cause of this issue was a failure of controls management. Specifically, as a preventive control, CISO implemented a list of entity names required to receive a copy of the plans within the header of the document. However, the person sending the document did not use the proper email information. As a compensating measure, CISO distributed earlier revisions of its emergency plans to all of the required entities as part of its January and February 2013 revisions. Also, the revisions made in the December 2013 version were minor and non-substantive. For these reasons, and because this issue caused no actual harm, WECC determined this issue posed minimal risk to the reliability of the BES. | To mitigate this issue, CISO: a. created a check sheet that ensures a correlation between email addresses and entity names that will be used to verify each entity is included in the distribution prior to the plan being distributed; b. added a second review, prior to publishing, to ensure that the Reliability Coordinator (“RC”) and all adjacent BAs/TOPs are included on Operating Procedure update email notifications; and c. provided training to the Procedure Control team regarding sharing and coordination practices with the RC and adjacent BAs/TOPs. WECC accepted CISO’s Mitigation Plan on January 29, 2015. CISO completed its Mitigation Plan on October 22, 2014. WECC verified completion of the Mitigation Plan on February 2, 2015.